05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-099 trips on frequency protection settings. LANO GSU trips on voltage protection settings. | Disabling frequency protection settings for GEN-2018-099 and voltage protection settings for LANO GSU prevents trips. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Antelope units trip on power unbalance. | Reducing fault clearing time to 5 cycles prevents trip. There are no stability constraints when these generators trip offline or when the fault clearing times are reduced to 5 cycles to prevent them from tripping.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17_151_TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17_151_TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO BORDER7 345.0 KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO BORDER7 345.0 KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16_003_TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16_003_TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_89_P2_2_PLANT_X6 | Apply single-phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 525481 b.2.GENERATOR 1 525494 b.3. LOAD S1 525494 b.4. DISCONNECT 525479 b.5. DISCONNECT 525494 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_90_P2_2_GRASSLAND6 | Apply single-phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 526677 b.2. GENERATOR 1 526678 b.3. LOAD A1 599125 b.4. DISCONNECT 526674 b.5. DISCONNECT 526678 b.6. DISCONNECT 526679 b.7. DISCONNECT 599125 b.8. DISCONNECT 599126 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_91_P2_2_CUNNIGHM_N6 | Apply single-phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. DISCONNECT 527865 b.2. GENERATOR 1 527883 b.3. LOAD S1 527883 b.4. DISCONNECT 527883 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_163_P5_5_CUNNINGHAM | Single phase fault with stuck relay near CUNNIGHM_N 6 (527865) 230 kV bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV bus b. Run fault for 19.32 cycles and trip the faulted elements b.1. LINE 527867 TO 527894 CKT 1 c. Run fault for 6.06 cycles and trip the faulted elements c.1. LINE 527865 TO 527963 CKT 1 d. Run fault for 17.1 cycles and trip the faulted elements d.1. GENERATOR 1 527883 d.2. DISCONNECT 527883 d.3. LINE 527865 TO 527883 CKT 1 e. Run fault for 13.2 cycles and trip the faulted elements e.1. LINE 527865 TO 527799 CKT 1 f. Run fault for 2.22 cycles and trip the faulted elements f.1. GENERATOR 1 527882 f.2. DISCONNECT 527882 f.3. LINE 527867 TO 527882 CKT 1 g. Run fault for 66.12 cycles and trip the faulted elements g.1. DISCONNECT 527863 g.2. DISCONNECT 527865 g.3. DISCONNECT 527867 h. Clear fault at CUNNIGHM_N 6 (527865) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_164_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 524623 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4 GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 523959 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_165_P5_5_BUSHLAND | Single phase fault with stuck relay near BUSHLAND 6 (524267) 230 kV bus a. Apply fault at the BUSHLAND 6 (524267) 230 kV bus b. Run fault for 5 cycles and trip the faulted elements b.1. DISCONNECT 524263 b.2. LINE 524267 TO 523959 CKT 1 b.3. LINE 524267 TO 524290 CKT 1 b.4. GENERATOR 1 524285 b.5. GENERATOR 1 524287 c. Run fault for 32 cycles and trip the faulted elements c.1. LINE 524267 TO 524623 CKT 1 d. Clear fault at the BUSHLAND 6 (524267) 230 kV bus and trip the faulted elements d.1. LOAD A1 524285 d.2. DISCONNECT 524267 d.3. DISCONNECT 524275 d.4. DISCONNECT 524276 d.5. DISCONNECT 524285 d.6. DISCONNECT 524287 d.7. DISCONNECT 524289 d.8. DISCONNECT 524290 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_166_P5_5_GRASSLAND | Single phase fault with stuck relay near GRASSLAND 6 (526677) 230 kV bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV bus b. Run fault for 34.38 cycles and trip the faulted elements b.1. LINE 526677 TO 526337 CKT 1 c. Run fault for 54.9 cycles and trip the faulted elements c.1. LINE 526676 TO 526656 CKT 1 d. Clear fault at the GRASSLAND 6 (526677) 230 kV bus and trip the faulted elements d.1. GENERATOR 1 526678 d.2. LOAD 1 526513 d.3. LOAD 1 526569 d.4. LOAD 1 526576 d.5. LOAD 1 526583 d.6. LOAD 1 526592 d.7. LOAD 1 526622 d.8. LOAD 2 526622 d.9. LOAD 3 526622 d.10. LOAD 1 526814 d.11. LOAD A1 599125 d.12 DISCONNECT 526513 d.13. DISCONNECT 526569 d.14. DISCONNECT 526576 d.15. DISCONNECT 526583 d.16. DISCONNECT 526592 d.17. DISCONNECT 526622 d.18.DISCONNECT 526674 d.19. DISCONNECT 526676 d.20. DISCONNECT 526677 d.21. DISCONNECT 526678 d.22. DISCONNECT 526679 d.23. DISCONNECT 526691 d.24. DISCONNECT 526692 d.25. DISCONNECT 526693 d.26. DISCONNECT 526694 d.27. DISCONNECT 526799 d.28. DISCONNECT 526814 d.29. DISCONNECT 526821 d.30. DISCONNECT 599125 d.31. DISCONNECT 599126 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_167_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525480 TO 525636 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 d. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements d.1. LOAD 1 525592 d.2. LOAD 1 525599 d.3. LOAD 2 525599 d.4. LOAD 1 525606 d.5. LOAD 1 525613 d.6. LOAD 1 525620 d.7. LOAD 2 525620 d.8. LOAD 1 525650 d.9. LOAD 1 525664 d.10. LOAD 2 525664 d.11. LOAD 1 525671 d.12. LOAD 1 525678 d.13. LOAD 1 525687 d.14. LOAD 1 525694 d.15. LOAD 1 525701 d.16. LOAD 2 525701 d.17. LOAD 1 525703 d.18. LOAD 1 525708 d.19. LOAD 1 525717 d.20. DISCONNECT 525592 d.21. DISCONNECT 525599 d.22. DISCONNECT 525606 d.23. DISCONNECT 525613 d.24. DISCONNECT 525620 d.25. DISCONNECT 525631 d.26. DISCONNECT 525632 d.27. DISCONNECT 525633 d.28. DISCONNECT 525635 d.29. DISCONNECT 525636 d.30. DISCONNECT 525637 d.31. DISCONNECT 525650 d.32. DISCONNECT 525657 d.32. DISCONNECT 525664 d.33. DISCONNECT 525671 d.34. DISCONNECT 525678 d.35. DISCONNECT 525687 d.36. DISCONNECT 525694 d.37. DISCONNECT 525697 d.38. DISCONNECT 525701 d.39. DISCONNECT 525703 d.40. DISCONNECT 525708 d.41. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_168_P5_5_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 14.88 cycles and trip the faulted elements c.1. DISCONNECT 525633 d. Run fault for 0.6 cycles and trip the faulted elements d.1. LINE 525636 TO 525480 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525635 e.28. DISCONNECT 525636 e.29. DISCONNECT 525650 e.30. DISCONNECT 525657 e.31. DISCONNECT 525664 e.32. DISCONNECT 525671 e.33. DISCONNECT 525678 e.34. DISCONNECT 525687 e.35. DISCONNECT 525694 e.36. DISCONNECT 525697 e.37. DISCONNECT 525701 e.38. DISCONNECT 525703 e.39. DISCONNECT 525708 e.40. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_169_P5_2_LUBBOCK_STH | Single phase fault with stuck relay near LUBBCK_STH 6 (526269) 230 kV bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV bus b. Run fault for 4.38 cycles and trip the faulted elements b.1. LINE 526269 TO 526525 CKT 1 c. Run fault for 40.2 cycles and trip the faulted elements c.1. LINE 526268 TO 526213 CKT 1 d. Run fault for 130.44 cycles and trip the faulted elements d.1. LINE 526268 TO 526298 CKT 1 e. Run fault for 60.3 cycles and trip the faulted elements e.1. LINE 526269 TO 526337 CKT 1 e.2. LINE 526269 TO 526337 CKT 2 f. Run fault for 63.6 cycles and trip the faulted elements f.1. DISCONNECT 526264 g. Run fault for 0.78 cycles and trip the faulted elements g.1. LINE 526602 TO 526656 CKT 1 h. Clear fault at the LUBBCK_STH 6 (526269) 230 kV bus and trip the faulted elements h.1. LOAD 1 526205 h.2. LOAD 1 526228 h.3. LOAD 1 526249 h.4. LOAD 1 526602 h.5. DISCONNECT 526205 h.6. DISCONNECT 526228 h.7. DISCONNECT 526249 h.8. DISCONNECT 526256 h.9. DISCONNECT 526265 h.10. DISCONNECT 526266 h.11. DISCONNECT 526267 h.12. DISCONNECT 526268 h.13. DISCONNECT 526269 h.14. DISCONNECT 526602 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_170_P5_2_MOORE | Single phase fault with stuck relay near RB-S&S 3 (523315) 115 kV bus a. Apply fault at the RB-S&S 3 (523315) 115 kV bus b. Run fault for 4.02 cycles and trip the faulted elements b.1. LINE 523315 TO 523318 CKT 1 c. Run fault for 8.28 cycles and trip the faulted elements c.1. LINE 523216 TO 523246 CKT 1 d. Run fault for 48.9 cycles and trip the faulted elements d.1. DISCONNECT 523302 e. Run fault for 10.62 cycles and trip the faulted elements e.1. LINE 523235 TO 523228 CKT 1 f. Run fault for 3.18 cycles and trip the faulted elements f.1. LINE 523176 TO 523175 CKT 1 g. Run fault for 35.1 cycles and trip the faulted elements g.1. LINE 523352 TO 523377 CKT 1 h. Clear fault at the RB-S&S 3 (523315) 115 kV bus and trip the faulted elements h.1. GENERATOR 1 523252 h.2. GENERATOR 1 523254 h.3. GENERATOR 1 523277 h.4. GENERATOR 1 523297 h.5. GENERATOR 3 523301 h.6. LOAD 1 523176 h.7. LOAD 1 523177 h.8. LOAD 1 523216 h.9. LOAD 1 523217 h.10. LOAD 1 523237 h.11. LOAD 1 523240 h.12. LOAD F1 523252 h.13. LOAD F1 523254 h.14. LOAD 1 523255 h.15. LOAD 2 523255 h.16. LOAD D1 523255 h.17. LOAD D2 523255 h.18. LOAD 1 523277 h.19. LOAD A1 523277 h.20. LOAD F1 523297 h.21. LOAD 1 523301 h.22. LOAD A3 523301 h.23. LOAD 1 523315 h.24. LOAD 1 523359 h.25. LOAD D1 523359 h.26. LOAD 1 523366 h.27. DISCONNECT 523176 h.28. DISCONNECT 523177 h.29. DISCONNECT 523216 h.30. DISCONNECT 523217 h.31. DISCONNECT 523235 h.32. DISCONNECT 523237 h.33. DISCONNECT 523240 h.34. DISCONNECT 523251 h.35. DISCONNECT 523252 h.36. DISCONNECT 523253 h.37. DISCONNECT 523254 h.38. DISCONNECT 523255 h.39. DISCONNECT 523256 h.40. DISCONNECT 523277 h.41. DISCONNECT 523294 h.42. DISCONNECT 523295 h.43. DISCONNECT 523296 h.44. DISCONNECT 523297 h.45. DISCONNECT 523301 h.46. DISCONNECT 523304 h.47. DISCONNECT 523308 h.47. DISCONNECT 523315 h.48. DISCONNECT 523352 h.49. DISCONNECT 523359 h.50. DISCONNECT 523366 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_171_P5_5_OASIS | Single phase fault with stuck relay near OASIS 3 (524874) 115 kV bus a. Apply fault at the OASIS 3 (524874) 115 kV bus b. Run fault for 19.2 cycles and trip the faulted elements b.1. LINE 524874 TO 524924 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 524764 TO 524822 CKT 1 d. Run fault for 10.8 cycles and trip the faulted elements d.1. LINE 524784 TO 524808 CKT 1 e. Run fault for 14.04 cycles and trip the faulted elements e.1. LINE 524875 TO 524909 CKT 1 f. Run fault for 49.08 cycles and trip the faulted elements f.1. DISCONNECT 524872 g. Clear fault at the OASIS 3 (524874) 115 kV bus and trip the faulted elements g.1. LOAD 1 524784 g.2. LOAD 1 524794 g.3. LOAD 1 524797 g.4. LOAD 1 524801 g.5. LOAD 1 524863 g.6. DISCONNECT 524764 g.7. DISCONNECT 524784 g.8. DISCONNECT 524790 g.9. DISCONNECT 524794 g.10. DISCONNECT 524797 g.11. DISCONNECT 524801 g.12. DISCONNECT 524863 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_172_P5_5_POTASH | Single phase fault with stuck relay near POTASH_JCT 3 (527962) 115 kV bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV bus b. Run fault for 19.02 cycles and trip the faulted elements b.1. LINE 527962 TO 527930 CKT 1 c. Run fault for 0.18 cycles and trip the faulted elements c.1. LINE 528064 TO 527953 CKT 1 d. Run fault for 15.3 cycles and trip the faulted elements d.1. LINE 527962 TO 528160 CKT 1 e. Run fault for 4.08 cycles and trip the faulted elements e.1. DISCONNECT 527958 f. Run fault for 14.94 cycles and trip the faulted elements f.1. LINE 528145 TO 527929 CKT 1 g. Clear fault at POTASH_JCT 3 (527962) 115 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_173_P5_5_7_RIVERS | Single phase fault with stuck relay near 7-RIVERS 3 (528094) 115 kV bus a. Apply fault at the 7-RIVERS 3 (528094) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 528094 TO 527711 CKT 1 b.2. LINE 528070 TO 528178 CKT 1 b.3. LINE 527786 TO 528116 CKT 1 c. Run fault for 20.4 cycles and trip the faulted elements c.1. LINE 528095 TO 528179 CKT 1 d. Run fault for 136.92 cycles and trip the faulted elements d.1. LINE 528095 TO 527799 CKT 1 e. Clear fault at the 7-RIVERS 3 (528094) 115 kV bus and trip the faulted elements e.1. LOAD 1 528003 e.2. LOAD 1 528076 e.3. LOAD 1 528079 e.4. LOAD 1 528109 e.5. LOAD 1 528116 e.6. DISCONNECT 528003 e.7. DISCONNECT 528070 e.7. DISCONNECT 528076 e.8. DISCONNECT 528079 e.9. DISCONNECT 528090 e.10. DISCONNECT 528091 e.11. DISCONNECT 528093 e.12. DISCONNECT 528094 e.13. DISCONNECT 528095 e.14. DISCONNECT 528109 e.15. DISCONNECT 528116 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_174_P5_5_YOAKUM | Single phase fault with stuck relay near YOAKUM 3 (526934) 115 kV bus a. Apply fault at the YOAKUM 3 (526934) 115 kV bus b. Run fault for 19.5 cycles and trip the faulted elements b.1. LINE 526934 TO 527194 CKT 1 c. Run fault for 1.5 cycles and trip the faulted elements c.1. LINE 526934 TO 526928 CKT 1 d. Run fault for 8.4 cycles and trip the faulted elements d.1. LINE 526792 TO 526736 CKT 1 e. Run fault for 24.6 cycles and trip the faulted elements e.1. DISCONNECT 527122 e.2. LINE 527130 TO 527136 CKT @1 f. Run fault for 3.72 cycles and trip the faulted elements f.1. GENERATOR 1 527162 f.2. DISCONNECT 527162 g. Run fault for 0.18 cycles and trip the faulted elements g.1. LINE 527051 TO 527062 CKT 1 h. Run fault for 0.12 cycles and trip the faulted elements h.1. GENERATOR 1 527161 h.2. DISCONNECT 527161 h.3. GENERATOR 1 527163 i. Run fault for 0.96 cycles and trip the faulted elements i.1. DISCONNECT 526932 i.2. DISCONNECT 526931 j. Clear fault at the YOAKUM 3 (526934) 115 kV bus and trip the faulted elements j.1. LOAD 1 526792 j.2. LOAD D1 526792 j.3. LOAD 1 527018 j.4. LOAD 1 527047 j.5. LOAD 1 527056 j.6. DISCONNECT 526792 j.7. DISCONNECT 526934 j.8. DISCONNECT 527018 j.9. DISCONNECT 527041 j.10. DISCONNECT 527047 j.11. DISCONNECT 527051 j.12.DISCONNECT 527056 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_175_P5_5_CARLISLE | Single phase fault with stuck relay near CARLISLE 3 (526160) 115 kV bus a. Apply fault at the CARLISLE 3 (526160) 115 kV bus b. Run fault for 19.38 cycles and trip the faulted elements b.1. LINE 526109 TO 526146 CKT 1 c. Run fault for 14.64 cycles and trip the faulted elements c.1. LINE 526475 TO 526481 CKT 1 d. Run fault for 13.08 cycles and trip the faulted elements d.1. DISCONNECT 526157 e. Run fault for 12.78 cycles and trip the faulted elements e.1. LINE 526160 TO 526192 CKT 1 f. Clear fault at the CARLISLE 3 (526160) 115 kV bus and trip the faulted elements f.1. LOAD 1 526109 f.2. LOAD 1 526160 f.3. LOAD D2 526160 f.4. LOAD 1 526176 f.5. LOAD 1 526221 f.6. LOAD 1 526483 f.7. DISCONNECT 526109 f.8. DISCONNECT 526130 f.9. DISCONNECT 526158 f.10. DISCONNECT 526159 f.11. DISCONNECT 526160 f.12. DISCONNECT 526162 f.13. DISCONNECT 526176 f.14. DISCONNECT 526184 f.15. DISCONNECT 526221 f.16. DISCONNECT 526481 f.17. DISCONNECT 526483 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_176_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 3.42 cycles and trip the faulted elements b.1. LINE 526243 TO 526199 CKT 1 c. Run fault for 53.4 cycles and trip the faulted elements c.1. LINE 526213 TO 526268 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_177_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 5.52 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 55.68 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_178_P5_2_ALLEN | Single phase fault with stuck relay near ALLEN 3 (526213) 115 kV bus a. Apply fault at the ALLEN 3 (526213) 115 kV bus b. Run fault for 48.3 cycles and trip the faulted elements b.1. LINE 526213 TO 526268 CKT 1 c. Run fault for 6.72 cycles and trip the faulted elements c.1. LINE 526243 TO 526199 CKT 1 d. Clear fault at the ALLEN 3 (526213) 115 kV bus and trip the faulted elements d.1. LOAD 1 526213 d.2. LOAD 2 526213 d.3. LOAD 1 526236 d.4. LOAD 1 526243 d.5. DISCONNECT 526213 d.6. DISCONNECT 526236 d.7. DISCONNECT 526243 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_179_P5_2_HARRNG_EST | Single phase fault with stuck relay near HARRNG_EST 6 (523979) 230 kV bus a. Apply fault at the HARRNG_EST 6 (523979) 230 kV bus b. Run fault for 20 cycles and trip the faulted elements b.1. DISCONNECT 523979 b.2. GENERATOR 1 523973 b.3. DISCONNECT 523973 c. Clear fault at HARRNG_EST 6 (523979) 230 kV bus | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_180_P5_2_WOLFFORTH | Single phase fault with stuck relay near WOLFFORTH 3 (526524) 115 kV bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV bus b. Run fault for 10 cycles and trip the faulted elements b.1. LINE 526162 TO 526160 CKT 1 b.2. DISCONNECT 526522 c. Run fault for 22 cycles and trip the faulted elements c.1. LINE 526524 TO 526736 CKT 1 d. Clear fault at the WOLFFORTH 3 (526524) 115 kV bus and trip the faulted elements d.1. LOAD 1 526176 d.2. LOAD 1 526475 d.3. LOAD 1 526483 d.4. DISCONNECT 526162 d.5. DISCONNECT 526176 d.6. DISCONNECT 526475 d.7. DISCONNECT 526481 d.8. DISCONNECT 526483 d.9. DISCONNECT 526524 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | LT__SPS_All_181_P5_3_LAMB | Single phase fault with stuck relay near LAMB_CNTY 3 (525636) 115 kV bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV bus b. Run fault for 39 cycles and trip the faulted elements b.1. LINE 525636 TO 526020 CKT 1 c. Run fault for 15.48 cycles and trip the faulted elements c.1. LINE 525636 TO 525480 CKT 1 d. Run fault for 46.32 cycles and trip the faulted elements d.1. LINE 525637 TO 525531 CKT 1 e. Clear fault at the LAMB_CNTY 3 (525636) 115 kV bus and trip the faulted elements e.1. LOAD 1 525592 e.2. LOAD 1 525599 e.3. LOAD 2 525599 e.4. LOAD 1 525606 e.5. LOAD 1 525613 e.6. LOAD 1 525620 e.7. LOAD 2 525620 e.8. LOAD 1 525650 e.9. LOAD 1 525664 e.10. LOAD 2 525664 e.11. LOAD 1 525671 e.12. LOAD 1 525678 e.13. LOAD 1 525687 e.14. LOAD 1 525694 e.15. LOAD 1 525701 e.16. LOAD 2 525701 e.17. LOAD 1 525703 e.18. LOAD 1 525708 e.19. LOAD 1 525717 e.20. DISCONNECT 525592 e.21. DISCONNECT 525599 e.22. DISCONNECT 525606 e.23. DISCONNECT 525613 e.24. DISCONNECT 525620 e.25. DISCONNECT 525631 e.26. DISCONNECT 525632 e.27. DISCONNECT 525633 e.28. DISCONNECT 525635 e.29. DISCONNECT 525636 e.30. DISCONNECT 525637 e.31. DISCONNECT 525650 e.32. DISCONNECT 525657 e.33. DISCONNECT 525664 e.34. DISCONNECT 525671 e.35. DISCONNECT 525678 e.36. DISCONNECT 525687 e.37. DISCONNECT 525694 e.38. DISCONNECT 525697 e.39. DISCONNECT 525701 e.40. DISCONNECT 525703 e.41. DISCONNECT 525708 e.42. DISCONNECT 525717 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2020-014 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.9298 | 6.9786 | 0.0488
GEN-2020-014 | 01 NORTH | 652400 | WILISTN4 | 230 | 12.2324 | 12.2492 | 0.0168
GEN-2020-014 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.7411 | 8.8706 | 0.1295
GEN-2020-014 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 3.5811 | 3.5815 | 0.0004
GEN-2020-014 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 6.3052 | 6.3066 | 0.0014
GEN-2020-014 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.2648 | 3.2652 | 0.0004
GEN-2020-014 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 3.982 | 3.9824 | 0.0004
GEN-2020-014 | 01 NORTH | 655839 | SATHERDM-MK7 | 115 | 2.2594 | 2.2595 | 0.0001
GEN-2020-014 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.7411 | 8.8706 | 0.1295
GEN-2020-014 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.7445 | 6.9614 | 0.2169
GEN-2020-014 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2139 | 3.2142 | 0.0003
GEN-2020-014 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6349 | 1.6349 | 0
GEN-2020-014 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.1039 | 5.1046 | 0.0007
GEN-2020-014 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6661 | 4.7025 | 0.0364
GEN-2020-014 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.08 | 4.0804 | 0.0004
GEN-2020-014 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 3.7806 | 3.7811 | 0.0005
GEN-2020-014 | 01 NORTH | 655848 | BERG -MK7 | 115 | 4.8206 | 4.8214 | 0.0008
GEN-2020-014 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 7.3981 | 7.3999 | 0.0018
GEN-2020-014 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4088 | 3.4092 | 0.0004
GEN-2020-014 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.1591 | 3.1594 | 0.0003
GEN-2020-014 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.8082 | 4.8469 | 0.0387
GEN-2020-014 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.2877 | 6.2888 | 0.0011
GEN-2020-014 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.3874 | 2.3876 | 0.0002
GEN-2020-014 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 3.8035 | 3.804 | 0.0005
GEN-2020-014 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.3269 | 3.3273 | 0.0004
GEN-2020-014 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.2919 | 2.2921 | 0.0002
GEN-2020-014 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.0803 | 3.0806 | 0.0003
GEN-2020-014 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 4.8297 | 4.8305 | 0.0008
GEN-2020-014 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 4.933 | 4.9338 | 0.0008
GEN-2020-014 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 3.5867 | 3.5871 | 0.0004
GEN-2020-014 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.944 | 2.9442 | 0.0002
GEN-2020-014 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7174 | 2.7176 | 0.0002
GEN-2020-014 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6198 | 2.62 | 0.0002
GEN-2020-014 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.8412 | 3.8417 | 0.0005
GEN-2020-014 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 5.652 | 5.653 | 0.001
GEN-2020-014 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 5.2483 | 5.2492 | 0.0009
GEN-2020-014 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.6456 | 7.7441 | 0.0985
GEN-2020-014 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.4044 | 8.5239 | 0.1195
GEN-2020-014 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.2717 | 5.3182 | 0.0465
GEN-2020-014 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9266 | 3.9524 | 0.0258
GEN-2020-014 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.702 | 4.739 | 0.037
GEN-2020-014 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 4.8444 | 4.8452 | 0.0008
GEN-2020-014 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 9.1057 | 9.1085 | 0.0028
GEN-2020-014 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 7.4261 | 7.4279 | 0.0018
GEN-2020-014 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 6.1773 | 6.1786 | 0.0013
GEN-2020-014 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 4.6028 | 4.6035 | 0.0007
GEN-2020-014 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 3.7207 | 3.7211 | 0.0004
GEN-2020-014 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 4.3304 | 4.331 | 0.0006
GEN-2020-014 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.3876 | 3.3879 | 0.0003
GEN-2020-014 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.0432 | 6.0442 | 0.001
GEN-2020-014 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9308 | 3.9312 | 0.0004
GEN-2020-014 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.3031 | 4.334 | 0.0309
GEN-2020-014 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.1019 | 3.1022 | 0.0003
GEN-2020-014 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 4.5093 | 4.5099 | 0.0006
GEN-2020-014 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1152 | 3.1314 | 0.0162
GEN-2020-014 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 5.2785 | 5.2795 | 0.001
GEN-2020-014 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.5332 | 6.8579 | 0.3247
GEN-2020-014 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.0153 | 11.0292 | 0.0139
GEN-2020-014 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.8496 | 11.8695 | 0.0199
GEN-2020-014 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 7.899 | 7.9064 | 0.0074
GEN-2020-014 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.5285 | 6.8585 | 0.33
GEN-2020-014 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 11.756 | 11.7588 | 0.0028
GEN-2020-014 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 11.7561 | 11.7588 | 0.0027
GEN-2020-014 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 4.2991 | 4.301 | 0.0019
GEN-2020-014 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 9.7751 | 9.7783 | 0.0032
GEN-2020-014 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 7.7274 | 7.7334 | 0.006
GEN-2020-014 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 16.5543 | 16.5622 | 0.0079
GEN-2020-014 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 16.4641 | 16.472 | 0.0079
GEN-2020-014 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 16.4748 | 16.4826 | 0.0078
GEN-2020-014 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.8562 | 6.904 | 0.0478
GEN-2020-014 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 6.5285 | 6.8585 | 0.33
GEN-2020-014 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 7.6206 | 7.6265 | 0.0059
GEN-2020-021 | 01 NORTH | 67030 | MPC04000MPT | 230 | 11.2022 | 11.2026 | 0.0004
GEN-2020-021 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.4779 | 7.4842 | 0.0063
GEN-2020-021 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 11.6482 | 11.688 | 0.0398
GEN-2020-021 | 01 NORTH | 608597 | SQBP1DC4 | 230 | 24.0487 | 24.0506 | 0.0019
GEN-2020-021 | 01 NORTH | 608599 | SQBP2DC4 | 230 | 24.0487 | 24.0506 | 0.0019
GEN-2020-021 | 01 NORTH | 608600 | BISONMP4 | 230 | 8.1738 | 8.1739 | 0.0001
GEN-2020-021 | 01 NORTH | 608602 | SQBEAST4 | 230 | 24.0487 | 24.0506 | 0.0019
GEN-2020-021 | 01 NORTH | 608603 | TRICNTY4 | 230 | 5.9049 | 5.905 | 0.0001
GEN-2020-021 | 01 NORTH | 615600 | GRE-COAL CR4 | 230 | 19.2523 | 19.2537 | 0.0014
GEN-2020-021 | 01 NORTH | 615601 | GRE-COAL FM8 | 69 | 9.0459 | 9.046 | 0.0001
GEN-2020-021 | 01 NORTH | 615604 | GRE-COALFB14 | 230 | 19.2523 | 19.2537 | 0.0014
GEN-2020-021 | 01 NORTH | 615605 | GRE-COALFB24 | 230 | 19.2523 | 19.2537 | 0.0014
GEN-2020-021 | 01 NORTH | 615606 | GRE-COALFB34 | 230 | 19.2523 | 19.2537 | 0.0014
GEN-2020-021 | 01 NORTH | 615900 | GRE-COAL TP4 | 230 | 16.1947 | 16.196 | 0.0013
GEN-2020-021 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.1325 | 18.1349 | 0.0024
GEN-2020-021 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1029 | 1.1029 | 0
GEN-2020-021 | 01 NORTH | 652276 | FTTHOMP8 | 69 | 3.7633 | 3.7646 | 0.0013
GEN-2020-021 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.831 | 7.8332 | 0.0022
GEN-2020-021 | 01 NORTH | 652426 | BISMARK4 | 230 | 14.8772 | 14.8815 | 0.0043
GEN-2020-021 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.0412 | 12.0455 | 0.0043
GEN-2020-021 | 01 NORTH | 652442 | GARRISN7 | 115 | 15.5563 | 15.5584 | 0.0021
GEN-2020-021 | 01 NORTH | 652444 | JAMESTN4 | 230 | 8.4682 | 8.4687 | 0.0005
GEN-2020-021 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.4975 | 10.5073 | 0.0098
GEN-2020-021 | 01 NORTH | 652466 | HILKEN 4 | 230 | 8.2423 | 8.2437 | 0.0014
GEN-2020-021 | 01 NORTH | 652506 | FTTHOMP3 | 345 | 8.9067 | 9.034 | 0.1273
GEN-2020-021 | 01 NORTH | 652507 | FTTHOMP4 | 230 | 18.3306 | 18.456 | 0.1254
GEN-2020-021 | 01 NORTH | 652540 | BIGBND14 | 230 | 11.5027 | 11.546 | 0.0433
GEN-2020-021 | 01 NORTH | 652541 | BIGBND24 | 230 | 11.4297 | 11.4723 | 0.0426
GEN-2020-021 | 01 NORTH | 652806 | FTTHOM1-LNX3 | 345 | 8.8446 | 8.9723 | 0.1277
GEN-2020-021 | 01 NORTH | 652807 | FTTHOM2-LNX3 | 345 | 8.9067 | 9.034 | 0.1273
GEN-2020-021 | 01 NORTH | 655153 | MOS-AMES-ER8 | 69 | 3.6909 | 3.6922 | 0.0013
GEN-2020-021 | 01 NORTH | 655158 | MOS-HYDE-ER8 | 69 | 2.2087 | 2.2091 | 0.0004
GEN-2020-021 | 01 NORTH | 655240 | HGHMORE-ER8 | 69 | 1.6045 | 1.6046 | 0.0001
GEN-2020-021 | 01 NORTH | 655328 | BIGBEND-ER8 | 69 | 2.897 | 2.8977 | 0.0007
GEN-2020-021 | 01 NORTH | 655329 | GANNVALL-ER8 | 69 | 0.8715 | 0.8716 | 0.0001
GEN-2020-021 | 01 NORTH | 655352 | AMES-ER8 | 69 | 1.3195 | 1.3197 | 0.0002
GEN-2020-021 | 01 NORTH | 655384 | NWPS8645-ER8 | 69 | 1.6247 | 1.6249 | 0.0002
GEN-2020-021 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9748 | 0.9748 | 0
GEN-2020-021 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.902 | 0.902 | 0
GEN-2020-021 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9088 | 0.9088 | 0
GEN-2020-021 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.689 | 0.689 | 0
GEN-2020-021 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6173 | 0.6173 | 0
GEN-2020-021 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1091 | 1.1092 | 0.0001
GEN-2020-021 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.115 | 1.115 | 0
GEN-2020-021 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1053 | 1.1053 | 0
GEN-2020-021 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5099 | 1.5101 | 0.0002
GEN-2020-021 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0215 | 1.0215 | 0
GEN-2020-021 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.989 | 0.9891 | 0.0001
GEN-2020-021 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9894 | 0.9895 | 0.0001
GEN-2020-021 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5474 | 1.5476 | 0.0002
GEN-2020-021 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.0991 | 4.0995 | 0.0004
GEN-2020-021 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 3.5814 | 3.5815 | 0.0001
GEN-2020-021 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 6.3062 | 6.3066 | 0.0004
GEN-2020-021 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.1305 | 14.1338 | 0.0033
GEN-2020-021 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9479 | 6.9487 | 0.0008
GEN-2020-021 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.0768 | 3.0771 | 0.0003
GEN-2020-021 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.3955 | 5.3962 | 0.0007
GEN-2020-021 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.2651 | 3.2652 | 0.0001
GEN-2020-021 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 3.9823 | 3.9824 | 0.0001
GEN-2020-021 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2141 | 3.2142 | 0.0001
GEN-2020-021 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.1044 | 5.1046 | 0.0002
GEN-2020-021 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.0803 | 4.0804 | 0.0001
GEN-2020-021 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 3.7809 | 3.7811 | 0.0002
GEN-2020-021 | 01 NORTH | 655848 | BERG -MK7 | 115 | 4.8212 | 4.8214 | 0.0002
GEN-2020-021 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 7.3995 | 7.3999 | 0.0004
GEN-2020-021 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4091 | 3.4092 | 0.0001
GEN-2020-021 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.8739 | 2.8742 | 0.0003
GEN-2020-021 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5056 | 3.5059 | 0.0003
GEN-2020-021 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.0356 | 8.0374 | 0.0018
GEN-2020-021 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.1593 | 3.1594 | 0.0001
GEN-2020-021 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.2886 | 6.2888 | 0.0002
GEN-2020-021 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.3875 | 2.3876 | 0.0001
GEN-2020-021 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 3.8039 | 3.804 | 0.0001
GEN-2020-021 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.3272 | 3.3273 | 0.0001
GEN-2020-021 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.292 | 2.2921 | 0.0001
GEN-2020-021 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.0805 | 3.0806 | 0.0001
GEN-2020-021 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 4.8303 | 4.8305 | 0.0002
GEN-2020-021 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 4.9336 | 4.9338 | 0.0002
GEN-2020-021 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 3.587 | 3.5871 | 0.0001
GEN-2020-021 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.9442 | 2.9442 | 0
GEN-2020-021 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7175 | 2.7176 | 0.0001
GEN-2020-021 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.62 | 2.62 | 0
GEN-2020-021 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.8415 | 3.8417 | 0.0002
GEN-2020-021 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 5.6528 | 5.653 | 0.0002
GEN-2020-021 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 5.249 | 5.2492 | 0.0002
GEN-2020-021 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 4.845 | 4.8452 | 0.0002
GEN-2020-021 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 9.1078 | 9.1085 | 0.0007
GEN-2020-021 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 7.4275 | 7.4279 | 0.0004
GEN-2020-021 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 6.1783 | 6.1786 | 0.0003
GEN-2020-021 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 4.6034 | 4.6035 | 0.0001
GEN-2020-021 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 3.721 | 3.7211 | 0.0001
GEN-2020-021 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 4.3308 | 4.331 | 0.0002
GEN-2020-021 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.3878 | 3.3879 | 0.0001
GEN-2020-021 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.0439 | 6.0442 | 0.0003
GEN-2020-021 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9311 | 3.9312 | 0.0001
GEN-2020-021 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.0708 | 6.0718 | 0.001
GEN-2020-021 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.487 | 3.4873 | 0.0003
GEN-2020-021 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.1021 | 3.1022 | 0.0001
GEN-2020-021 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 4.5098 | 4.5099 | 0.0001
GEN-2020-021 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 5.2792 | 5.2795 | 0.0003
GEN-2020-021 | 01 NORTH | 655905 | RBNSNLAK-MW7 | 115 | 4.5933 | 4.5934 | 0.0001
GEN-2020-021 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 4.4726 | 4.4727 | 0.0001
GEN-2020-021 | 01 NORTH | 655919 | OSBORN -MW7 | 115 | 4.8458 | 4.8459 | 0.0001
GEN-2020-021 | 01 NORTH | 655920 | VANHOOK -MW7 | 115 | 4.5225 | 4.5226 | 0.0001
GEN-2020-021 | 01 NORTH | 657756 | SQBUTTE4 | 230 | 24.0487 | 24.0506 | 0.0019
GEN-2020-021 | 01 NORTH | 657848 | YNG2 4 | 230 | 19.46 | 19.461 | 0.001
GEN-2020-021 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 15.9178 | 15.9549 | 0.0371
GEN-2020-021 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 16.9687 | 17.0552 | 0.0865
GEN-2020-021 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 23.5635 | 23.6344 | 0.0709
GEN-2020-021 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.3576 | 6.3589 | 0.0013
GEN-2020-021 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3752 | 5.377 | 0.0018
GEN-2020-021 | 01 NORTH | 659130 | CHAPELLE-BE3 | 345 | 6.3355 | 6.4982 | 0.1627
GEN-2020-021 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 5.7275 | 5.728 | 0.0005
GEN-2020-021 | 01 NORTH | 659155 | LOGAN___-BE7 | 115 | 10.9106 | 10.9117 | 0.0011
GEN-2020-021 | 01 NORTH | 659160 | GROTON__-BE3 | 345 | 6.2922 | 6.2935 | 0.0013
GEN-2020-021 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.2535 | 14.2568 | 0.0033
GEN-2020-021 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.0223 | 11.0292 | 0.0069
GEN-2020-021 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7427 | 3.743 | 0.0003
GEN-2020-021 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.5194 | 21.5781 | 0.0587
GEN-2020-021 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.226 | 15.26 | 0.034
GEN-2020-021 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 15.9178 | 15.9549 | 0.0371
GEN-2020-021 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.6149 | 9.6176 | 0.0027
GEN-2020-021 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.1902 | 7.1953 | 0.0051
GEN-2020-021 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2573 | 7.2589 | 0.0016
GEN-2020-021 | 01 NORTH | 659284 | ECKLUND_-PP4 | 230 | 7.0576 | 7.0586 | 0.001
GEN-2020-021 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.8647 | 11.8695 | 0.0048
GEN-2020-021 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 6.5013 | 6.5017 | 0.0004
GEN-2020-021 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 10.5196 | 10.5205 | 0.0009
GEN-2020-021 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 11.7581 | 11.7588 | 0.0007
GEN-2020-021 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 11.7581 | 11.7588 | 0.0007
GEN-2020-021 | 01 NORTH | 659365 | BALDWIN_-PP4 | 230 | 7.0576 | 7.0586 | 0.001
GEN-2020-021 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 8.6128 | 8.6187 | 0.0059
GEN-2020-021 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.3325 | 11.336 | 0.0035
GEN-2020-021 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 4.3005 | 4.301 | 0.0005
GEN-2020-021 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 9.7775 | 9.7783 | 0.0008
GEN-2020-021 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 7.7319 | 7.7334 | 0.0015
GEN-2020-021 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 16.5601 | 16.5622 | 0.0021
GEN-2020-021 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.0769 | 4.0771 | 0.0002
GEN-2020-021 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 15.9178 | 15.9549 | 0.0371
GEN-2020-021 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1938 | 4.1965 | 0.0027
GEN-2020-021 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 16.9687 | 17.0552 | 0.0865
GEN-2020-021 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2922 | 6.2935 | 0.0013
GEN-2020-021 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 16.9687 | 17.0552 | 0.0865
GEN-2020-021 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 6.5013 | 6.5017 | 0.0004
GEN-2020-021 | 01 NORTH | 659428 | CC.LS-LO-BE3 | 345 | 6.3059 | 6.469 | 0.1631
GEN-2020-021 | 01 NORTH | 659433 | TRIPLEH__UA3 | 345 | 6.2757 | 6.435 | 0.1593
GEN-2020-021 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 16.4699 | 16.472 | 0.0021
GEN-2020-021 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 16.4806 | 16.4826 | 0.002
GEN-2020-021 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 5.1146 | 5.1149 | 0.0003
GEN-2020-021 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.2016 | 3.2019 | 0.0003
GEN-2020-021 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 10.9684 | 11.0036 | 0.0352
GEN-2020-021 | 01 NORTH | 764210 | GEN-2020-021 | 345 | 3.2313 | 3.6154 | 0.3841
GEN-2020-021 | 01 NORTH | 764220 | G20-021-TAP | 345 | 3.853 | 4.2303 | 0.3773
GEN-2020-021 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 7.6249 | 7.6265 | 0.0016
GEN-2020-083 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 8.5816 | 8.5908 | 0.0092
GEN-2020-083 | 01 NORTH | 652200 | GLENDIVE7 | 115 | 8.6505 | 8.6718 | 0.0213
GEN-2020-083 | 01 NORTH | 652212 | GLENDIVEP2T7 | 115 | 4.8986 | 4.9053 | 0.0067
GEN-2020-083 | 01 NORTH | 652213 | FALLON 8 | 69 | 1.1023 | 1.1024 | 0.0001
GEN-2020-083 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.9707 | 6.9786 | 0.0079
GEN-2020-083 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.1605 | 18.3229 | 0.1624
GEN-2020-083 | 01 NORTH | 652400 | WILISTN4 | 230 | 12.1972 | 12.2492 | 0.052
GEN-2020-083 | 01 NORTH | 652401 | CIRCLE 7 | 115 | 2.2832 | 2.2843 | 0.0011
GEN-2020-083 | 01 NORTH | 652403 | DAWSONC4 | 230 | 7.0625 | 7.0808 | 0.0183
GEN-2020-083 | 01 NORTH | 652404 | DAWSONC7 | 115 | 10.0803 | 10.1131 | 0.0328
GEN-2020-083 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.3552 | 2.3564 | 0.0012
GEN-2020-083 | 01 NORTH | 652406 | FTPECK 7 | 115 | 3.1183 | 3.1195 | 0.0012
GEN-2020-083 | 01 NORTH | 652407 | FALLON 7 | 115 | 3.4807 | 3.4836 | 0.0029
GEN-2020-083 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.8658 | 8.8706 | 0.0048
GEN-2020-083 | 01 NORTH | 652409 | WOLFPT 7 | 115 | 3.0751 | 3.0765 | 0.0014
GEN-2020-083 | 01 NORTH | 652411 | MI CTYE4 | 230 | 3.2553 | 3.258 | 0.0027
GEN-2020-083 | 01 NORTH | 652412 | MI CTYE7 | 115 | 4.2144 | 4.2167 | 0.0023
GEN-2020-083 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.1605 | 18.3241 | 0.1636
GEN-2020-083 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 5.4646 | 5.4708 | 0.0062
GEN-2020-083 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.03 | 5.5405 | 0.5105
GEN-2020-083 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 5.3322 | 5.3376 | 0.0054
GEN-2020-083 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 3.6618 | 3.6644 | 0.0026
GEN-2020-083 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.756 | 6.0347 | 0.2787
GEN-2020-083 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9842 | 2.0589 | 0.0747
GEN-2020-083 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.567 | 3.8144 | 0.2474
GEN-2020-083 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 5.9573 | 5.9745 | 0.0172
GEN-2020-083 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 3.5806 | 3.5815 | 0.0009
GEN-2020-083 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 6.3037 | 6.3066 | 0.0029
GEN-2020-083 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.2644 | 3.2652 | 0.0008
GEN-2020-083 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 3.9815 | 3.9824 | 0.0009
GEN-2020-083 | 01 NORTH | 655839 | SATHERDM-MK7 | 115 | 2.2396 | 2.2595 | 0.0199
GEN-2020-083 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.8658 | 8.8706 | 0.0048
GEN-2020-083 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.9597 | 6.9614 | 0.0017
GEN-2020-083 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.2136 | 3.2142 | 0.0006
GEN-2020-083 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6245 | 1.6349 | 0.0104
GEN-2020-083 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.103 | 5.1046 | 0.0016
GEN-2020-083 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.7012 | 4.7025 | 0.0013
GEN-2020-083 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.0794 | 4.0804 | 0.001
GEN-2020-083 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 3.78 | 3.7811 | 0.0011
GEN-2020-083 | 01 NORTH | 655848 | BERG -MK7 | 115 | 4.8197 | 4.8214 | 0.0017
GEN-2020-083 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 7.396 | 7.3999 | 0.0039
GEN-2020-083 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.4084 | 3.4092 | 0.0008
GEN-2020-083 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.1587 | 3.1594 | 0.0007
GEN-2020-083 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.8455 | 4.8469 | 0.0014
GEN-2020-083 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.2864 | 6.2888 | 0.0024
GEN-2020-083 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.3871 | 2.3876 | 0.0005
GEN-2020-083 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 3.8029 | 3.804 | 0.0011
GEN-2020-083 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.3265 | 3.3273 | 0.0008
GEN-2020-083 | 01 NORTH | 655860 | SKAAR___-MK7 | 115 | 3.4299 | 3.4766 | 0.0467
GEN-2020-083 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.2918 | 2.2921 | 0.0003
GEN-2020-083 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.08 | 3.0806 | 0.0006
GEN-2020-083 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 4.8288 | 4.8305 | 0.0017
GEN-2020-083 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 4.9321 | 4.9338 | 0.0017
GEN-2020-083 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 3.5862 | 3.5871 | 0.0009
GEN-2020-083 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.9437 | 2.9442 | 0.0005
GEN-2020-083 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7171 | 2.7176 | 0.0005
GEN-2020-083 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6196 | 2.62 | 0.0004
GEN-2020-083 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.8407 | 3.8417 | 0.001
GEN-2020-083 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 5.6507 | 5.653 | 0.0023
GEN-2020-083 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 5.2472 | 5.2492 | 0.002
GEN-2020-083 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.7405 | 7.7441 | 0.0036
GEN-2020-083 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.5195 | 8.5239 | 0.0044
GEN-2020-083 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.3165 | 5.3182 | 0.0017
GEN-2020-083 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9514 | 3.9524 | 0.001
GEN-2020-083 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.7376 | 4.739 | 0.0014
GEN-2020-083 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 4.8435 | 4.8452 | 0.0017
GEN-2020-083 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 9.1025 | 9.1085 | 0.006
GEN-2020-083 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 7.4239 | 7.4279 | 0.004
GEN-2020-083 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 6.1758 | 6.1786 | 0.0028
GEN-2020-083 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 4.602 | 4.6035 | 0.0015
GEN-2020-083 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 3.7201 | 3.7211 | 0.001
GEN-2020-083 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 4.3296 | 4.331 | 0.0014
GEN-2020-083 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.3872 | 3.3879 | 0.0007
GEN-2020-083 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.0419 | 6.0442 | 0.0023
GEN-2020-083 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.9303 | 3.9312 | 0.0009
GEN-2020-083 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.3328 | 4.334 | 0.0012
GEN-2020-083 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.1015 | 3.1022 | 0.0007
GEN-2020-083 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 4.5085 | 4.5099 | 0.0014
GEN-2020-083 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1308 | 3.1314 | 0.0006
GEN-2020-083 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 5.2774 | 5.2795 | 0.0021
GEN-2020-083 | 01 NORTH | 655915 | BARRBUTE-MW7 | 115 | 4.6978 | 4.7022 | 0.0044
GEN-2020-083 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 14.0562 | 14.0942 | 0.038
GEN-2020-083 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 14.425 | 14.5175 | 0.0925
GEN-2020-083 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.396 | 8.4272 | 0.0312
GEN-2020-083 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 5.6564 | 5.6647 | 0.0083
GEN-2020-083 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 10.2894 | 10.3217 | 0.0323
GEN-2020-083 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 10.1521 | 10.186 | 0.0339
GEN-2020-083 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 10.0848 | 10.1223 | 0.0375
GEN-2020-083 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 9.8523 | 9.8841 | 0.0318
GEN-2020-083 | 01 NORTH | 655940 | MONT -MW7 | 115 | 13.3062 | 13.3576 | 0.0514
GEN-2020-083 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 7.3796 | 7.3907 | 0.0111
GEN-2020-083 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 8.3309 | 8.3426 | 0.0117
GEN-2020-083 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 7.7251 | 7.7424 | 0.0173
GEN-2020-083 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 6.5809 | 6.5935 | 0.0126
GEN-2020-083 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.1234 | 6.1304 | 0.007
GEN-2020-083 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 4.4512 | 4.454 | 0.0028
GEN-2020-083 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 10.7142 | 10.7294 | 0.0152
GEN-2020-083 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 5.7256 | 5.728 | 0.0024
GEN-2020-083 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.797 | 6.0798 | 0.2828
GEN-2020-083 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.8569 | 6.8579 | 0.001
GEN-2020-083 | 01 NORTH | 659180 | KOCH_OIL-BE7 | 115 | 3.7035 | 3.7752 | 0.0717
GEN-2020-083 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.434 | 3.4637 | 0.0297
GEN-2020-083 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.0111 | 11.0292 | 0.0181
GEN-2020-083 | 01 NORTH | 659186 | E.SIDNEY-LY7 | 115 | 4.3022 | 4.4248 | 0.1226
GEN-2020-083 | 01 NORTH | 659191 | SQUAWGAP-BE7 | 115 | 3.4325 | 3.4792 | 0.0467
GEN-2020-083 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.8759 | 5.8797 | 0.0038
GEN-2020-083 | 01 NORTH | 659259 | HEADRESS-CM7 | 115 | 3.0678 | 3.0692 | 0.0014
GEN-2020-083 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.7724 | 5.777 | 0.0046
GEN-2020-083 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.6621 | 5.6658 | 0.0037
GEN-2020-083 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.8545 | 11.8695 | 0.015
GEN-2020-083 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 7.8856 | 7.9064 | 0.0208
GEN-2020-083 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.7945 | 11.8393 | 0.0448
GEN-2020-083 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.8574 | 6.8585 | 0.0011
GEN-2020-083 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 14.0562 | 14.0942 | 0.038
GEN-2020-083 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 11.7529 | 11.7588 | 0.0059
GEN-2020-083 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 11.7529 | 11.7588 | 0.0059
GEN-2020-083 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.4596 | 7.473 | 0.0134
GEN-2020-083 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 8.5505 | 8.5627 | 0.0122
GEN-2020-083 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 4.2969 | 4.301 | 0.0041
GEN-2020-083 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 9.7714 | 9.7783 | 0.0069
GEN-2020-083 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 7.7204 | 7.7334 | 0.013
GEN-2020-083 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 16.5452 | 16.5622 | 0.017
GEN-2020-083 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 6.493 | 6.5017 | 0.0087
GEN-2020-083 | 01 NORTH | 659430 | PIONEER2-BE7 | 115 | 13.4047 | 13.4382 | 0.0335
GEN-2020-083 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 16.455 | 16.472 | 0.017
GEN-2020-083 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 16.4657 | 16.4826 | 0.0169
GEN-2020-083 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 5.4646 | 5.4708 | 0.0062
GEN-2020-083 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.9434 | 3.945 | 0.0016
GEN-2020-083 | 01 NORTH | 659542 | REDWATER-MC7 | 115 | 2.2832 | 2.2843 | 0.0011
GEN-2020-083 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.8963 | 6.904 | 0.0077
GEN-2020-083 | 01 NORTH | 661004 | BAKER 4 | 230 | 3.5509 | 3.5526 | 0.0017
GEN-2020-083 | 01 NORTH | 661010 | MILESCITYSW7 | 115 | 1.0398 | 1.0399 | 0.0001
GEN-2020-083 | 01 NORTH | 661032 | GLENDCT7 | 115 | 7.4777 | 7.4907 | 0.013
GEN-2020-083 | 01 NORTH | 661056 | LEWIS 7 | 115 | 5.8736 | 6.1097 | 0.2361
GEN-2020-083 | 01 NORTH | 661075 | POPLAR 7 | 115 | 2.8068 | 2.8079 | 0.0011
GEN-2020-083 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 10.7142 | 10.7294 | 0.0152
GEN-2020-083 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 11.8694 | 11.8823 | 0.0129
GEN-2020-083 | 01 NORTH | 661086 | TIOGA7 7 | 115 | 9.4159 | 9.4251 | 0.0092
GEN-2020-083 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.6562 | 5.6622 | 0.006
GEN-2020-083 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 6.9002 | 6.9173 | 0.0171
GEN-2020-083 | 01 NORTH | 672603 | BDV 4 | 230 | 4.9056 | 4.9066 | 0.001
GEN-2020-083 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 7.3796 | 7.3907 | 0.0111
GEN-2020-083 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 5.3506 | 5.3564 | 0.0058
GEN-2020-083 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 6.8574 | 6.8585 | 0.0011
GEN-2020-083 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 7.6138 | 7.6265 | 0.0127
GEN-2020-083 | 01 NORTH | 765070 | GEN-2020-083 | 115 | 5.03 | 5.5405 | 0.5105
GEN-2020-091 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.4826 | 7.4842 | 0.0016
GEN-2020-091 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 11.6794 | 11.688 | 0.0086
GEN-2020-091 | 01 NORTH | 588550 | GEN-2017-010 | 230 | 4.7263 | 4.7291 | 0.0028
GEN-2020-091 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 8.566 | 8.5908 | 0.0248
GEN-2020-091 | 01 NORTH | 615901 | GRE-STANTON4 | 230 | 18.1338 | 18.1349 | 0.0011
GEN-2020-091 | 01 NORTH | 652216 | WATFORD4 | 230 | 6.9536 | 6.9786 | 0.025
GEN-2020-091 | 01 NORTH | 652248 | MAURINE8 | 69 | 2.9946 | 2.9948 | 0.0002
GEN-2020-091 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1029 | 1.1029 | 0
GEN-2020-091 | 01 NORTH | 652391 | WILLISTON27 | 115 | 18.2632 | 18.3229 | 0.0597
GEN-2020-091 | 01 NORTH | 652400 | WILISTN4 | 230 | 12.1409 | 12.2492 | 0.1083
GEN-2020-091 | 01 NORTH | 652403 | DAWSONC4 | 230 | 7.0669 | 7.0808 | 0.0139
GEN-2020-091 | 01 NORTH | 652404 | DAWSONC7 | 115 | 10.1026 | 10.1131 | 0.0105
GEN-2020-091 | 01 NORTH | 652405 | FTPECK 4 | 230 | 2.3557 | 2.3564 | 0.0007
GEN-2020-091 | 01 NORTH | 652408 | WATFORD7 | 115 | 8.8555 | 8.8706 | 0.0151
GEN-2020-091 | 01 NORTH | 652411 | MI CTYE4 | 230 | 3.2559 | 3.258 | 0.0021
GEN-2020-091 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0653 | 5.0691 | 0.0038
GEN-2020-091 | 01 NORTH | 652421 | WILISTN7 | 115 | 18.2643 | 18.3241 | 0.0598
GEN-2020-091 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.8045 | 7.8332 | 0.0287
GEN-2020-091 | 01 NORTH | 652425 | BELFELD4 | 230 | 10.4852 | 10.5109 | 0.0257
GEN-2020-091 | 01 NORTH | 652441 | GARRISN4 | 230 | 12.0436 | 12.0455 | 0.0019
GEN-2020-091 | 01 NORTH | 652456 | WASHBRN4 | 230 | 10.5046 | 10.5073 | 0.0027
GEN-2020-091 | 01 NORTH | 652468 | HEBRON 4 | 230 | 5.8662 | 5.8687 | 0.0025
GEN-2020-091 | 01 NORTH | 652480 | MAURINE7 | 115 | 5.2938 | 5.2946 | 0.0008
GEN-2020-091 | 01 NORTH | 652484 | NUNDRWD4 | 230 | 6.2092 | 6.2106 | 0.0014
GEN-2020-091 | 01 NORTH | 652497 | MAURINE4 | 230 | 5.4617 | 5.464 | 0.0023
GEN-2020-091 | 01 NORTH | 652616 | MINGUSVILLE4 | 230 | 5.4643 | 5.4708 | 0.0065
GEN-2020-091 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.5377 | 5.5405 | 0.0028
GEN-2020-091 | 01 NORTH | 652884 | NUNDRWD-LNX3 | 230 | 6.1882 | 6.1896 | 0.0014
GEN-2020-091 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9748 | 0.9748 | 0
GEN-2020-091 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.902 | 0.902 | 0
GEN-2020-091 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9088 | 0.9088 | 0
GEN-2020-091 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.689 | 0.689 | 0
GEN-2020-091 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6173 | 0.6173 | 0
GEN-2020-091 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1091 | 1.1092 | 0.0001
GEN-2020-091 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.115 | 1.115 | 0
GEN-2020-091 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1053 | 1.1053 | 0
GEN-2020-091 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.51 | 1.5101 | 0.0001
GEN-2020-091 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0215 | 1.0215 | 0
GEN-2020-091 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9891 | 0.9891 | 0
GEN-2020-091 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9895 | 0.9895 | 0
GEN-2020-091 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5475 | 1.5476 | 0.0001
GEN-2020-091 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 2.0585 | 2.0589 | 0.0004
GEN-2020-091 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.813 | 3.8144 | 0.0014
GEN-2020-091 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 5.9681 | 5.9745 | 0.0064
GEN-2020-091 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.0964 | 4.0995 | 0.0031
GEN-2020-091 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 3.5638 | 3.5815 | 0.0177
GEN-2020-091 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 6.2516 | 6.3066 | 0.055
GEN-2020-091 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.0852 | 14.1338 | 0.0486
GEN-2020-091 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9369 | 6.9487 | 0.0118
GEN-2020-091 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.0753 | 3.0771 | 0.0018
GEN-2020-091 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.3908 | 5.3962 | 0.0054
GEN-2020-091 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.2504 | 3.2652 | 0.0148
GEN-2020-091 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 3.9637 | 3.9824 | 0.0187
GEN-2020-091 | 01 NORTH | 655839 | SATHERDM-MK7 | 115 | 2.2588 | 2.2595 | 0.0007
GEN-2020-091 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 8.8555 | 8.8706 | 0.0151
GEN-2020-091 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 6.956 | 6.9614 | 0.0054
GEN-2020-091 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.202 | 3.2142 | 0.0122
GEN-2020-091 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6346 | 1.6349 | 0.0003
GEN-2020-091 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.0738 | 5.1046 | 0.0308
GEN-2020-091 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.6983 | 4.7025 | 0.0042
GEN-2020-091 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.0608 | 4.0804 | 0.0196
GEN-2020-091 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 3.7613 | 3.7811 | 0.0198
GEN-2020-091 | 01 NORTH | 655848 | BERG -MK7 | 115 | 4.7893 | 4.8214 | 0.0321
GEN-2020-091 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 7.3244 | 7.3999 | 0.0755
GEN-2020-091 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.3954 | 3.4092 | 0.0138
GEN-2020-091 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.8726 | 2.8742 | 0.0016
GEN-2020-091 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5036 | 3.5059 | 0.0023
GEN-2020-091 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.0254 | 8.0374 | 0.012
GEN-2020-091 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.1456 | 3.1594 | 0.0138
GEN-2020-091 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.8424 | 4.8469 | 0.0045
GEN-2020-091 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.2422 | 6.2888 | 0.0466
GEN-2020-091 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.3797 | 2.3876 | 0.0079
GEN-2020-091 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 3.784 | 3.804 | 0.02
GEN-2020-091 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.312 | 3.3273 | 0.0153
GEN-2020-091 | 01 NORTH | 655860 | SKAAR___-MK7 | 115 | 3.4751 | 3.4766 | 0.0015
GEN-2020-091 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.2859 | 2.2921 | 0.0062
GEN-2020-091 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.0693 | 3.0806 | 0.0113
GEN-2020-091 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 4.7982 | 4.8305 | 0.0323
GEN-2020-091 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 4.9002 | 4.9338 | 0.0336
GEN-2020-091 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 3.5693 | 3.5871 | 0.0178
GEN-2020-091 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 2.934 | 2.9442 | 0.0102
GEN-2020-091 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7089 | 2.7176 | 0.0087
GEN-2020-091 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6119 | 2.62 | 0.0081
GEN-2020-091 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.8242 | 3.8417 | 0.0175
GEN-2020-091 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.4065 | 4.4297 | 0.0232
GEN-2020-091 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 5.6089 | 5.653 | 0.0441
GEN-2020-091 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 5.2111 | 5.2492 | 0.0381
GEN-2020-091 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 7.7326 | 7.7441 | 0.0115
GEN-2020-091 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.51 | 8.5239 | 0.0139
GEN-2020-091 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.3128 | 5.3182 | 0.0054
GEN-2020-091 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 3.9494 | 3.9524 | 0.003
GEN-2020-091 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.7347 | 4.739 | 0.0043
GEN-2020-091 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 4.8127 | 4.8452 | 0.0325
GEN-2020-091 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 8.9944 | 9.1085 | 0.1141
GEN-2020-091 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 7.3518 | 7.4279 | 0.0761
GEN-2020-091 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 6.1258 | 6.1786 | 0.0528
GEN-2020-091 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 4.5742 | 4.6035 | 0.0293
GEN-2020-091 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 3.702 | 3.7211 | 0.0191
GEN-2020-091 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 4.3051 | 4.331 | 0.0259
GEN-2020-091 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.3743 | 3.3879 | 0.0136
GEN-2020-091 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.0011 | 6.0442 | 0.0431
GEN-2020-091 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.8934 | 4.897 | 0.0036
GEN-2020-091 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 3.913 | 3.9312 | 0.0182
GEN-2020-091 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.0649 | 6.0718 | 0.0069
GEN-2020-091 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.485 | 3.4873 | 0.0023
GEN-2020-091 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.3304 | 4.334 | 0.0036
GEN-2020-091 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.0889 | 3.1022 | 0.0133
GEN-2020-091 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 4.4818 | 4.5099 | 0.0281
GEN-2020-091 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1295 | 3.1314 | 0.0019
GEN-2020-091 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 5.241 | 5.2795 | 0.0385
GEN-2020-091 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 4.4705 | 4.4727 | 0.0022
GEN-2020-091 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 14.4834 | 14.5175 | 0.0341
GEN-2020-091 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.4157 | 8.4272 | 0.0115
GEN-2020-091 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 5.6597 | 5.6647 | 0.005
GEN-2020-091 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 10.3064 | 10.3217 | 0.0153
GEN-2020-091 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 10.17 | 10.186 | 0.016
GEN-2020-091 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 10.1058 | 10.1223 | 0.0165
GEN-2020-091 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 8.4552 | 8.4665 | 0.0113
GEN-2020-091 | 01 NORTH | 655940 | MONT -MW7 | 115 | 13.3364 | 13.3576 | 0.0212
GEN-2020-091 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 6.4398 | 6.4461 | 0.0063
GEN-2020-091 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 7.7336 | 7.7424 | 0.0088
GEN-2020-091 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 6.5871 | 6.5935 | 0.0064
GEN-2020-091 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 15.9191 | 15.9549 | 0.0358
GEN-2020-091 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.0365 | 17.0552 | 0.0187
GEN-2020-091 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 23.6164 | 23.6344 | 0.018
GEN-2020-091 | 01 NORTH | 659108 | LOGAN___-BE4 | 230 | 6.3559 | 6.3589 | 0.003
GEN-2020-091 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3766 | 5.377 | 0.0004
GEN-2020-091 | 01 NORTH | 659120 | BROADLND-BE3 | 345 | 4.1962 | 4.1965 | 0.0003
GEN-2020-091 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.4644 | 7.4733 | 0.0089
GEN-2020-091 | 01 NORTH | 659125 | DICKINSN-BE7 | 115 | 8.3566 | 8.3613 | 0.0047
GEN-2020-091 | 01 NORTH | 659131 | LARAMIE_-MB3 | 345 | 7.8459 | 7.8461 | 0.0002
GEN-2020-091 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 10.6884 | 10.7294 | 0.041
GEN-2020-091 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 6.8546 | 6.8579 | 0.0033
GEN-2020-091 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.4619 | 3.4637 | 0.0018
GEN-2020-091 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.2074 | 14.2568 | 0.0494
GEN-2020-091 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 10.9272 | 11.0292 | 0.102
GEN-2020-091 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4314 | 4.4352 | 0.0038
GEN-2020-091 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7396 | 3.743 | 0.0034
GEN-2020-091 | 01 NORTH | 659191 | SQUAWGAP-BE7 | 115 | 3.4777 | 3.4792 | 0.0015
GEN-2020-091 | 01 NORTH | 659195 | DICKINS2-BE7 | 115 | 8.3554 | 8.3601 | 0.0047
GEN-2020-091 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.5633 | 21.5781 | 0.0148
GEN-2020-091 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 15.2272 | 15.26 | 0.0328
GEN-2020-091 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 15.9191 | 15.9549 | 0.0358
GEN-2020-091 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.615 | 9.6176 | 0.0026
GEN-2020-091 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.1904 | 7.1953 | 0.0049
GEN-2020-091 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2574 | 7.2589 | 0.0015
GEN-2020-091 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.8719 | 5.8797 | 0.0078
GEN-2020-091 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.1571 | 4.1585 | 0.0014
GEN-2020-091 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.7752 | 5.777 | 0.0018
GEN-2020-091 | 01 NORTH | 659266 | RHAME___-BE4 | 230 | 4.8149 | 4.8178 | 0.0029
GEN-2020-091 | 01 NORTH | 659267 | RHAME___-BE7 | 115 | 2.0619 | 2.0622 | 0.0003
GEN-2020-091 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.6643 | 5.6658 | 0.0015
GEN-2020-091 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.7916 | 11.8695 | 0.0779
GEN-2020-091 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3308 | 2.3314 | 0.0006
GEN-2020-091 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 10.4852 | 10.5109 | 0.0257
GEN-2020-091 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 7.7866 | 7.9064 | 0.1198
GEN-2020-091 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 11.7242 | 11.8393 | 0.1151
GEN-2020-091 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 6.4708 | 6.5017 | 0.0309
GEN-2020-091 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 10.4796 | 10.5205 | 0.0409
GEN-2020-091 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 6.8551 | 6.8585 | 0.0034
GEN-2020-091 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 11.6464 | 11.7588 | 0.1124
GEN-2020-091 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 11.6465 | 11.7588 | 0.1123
GEN-2020-091 | 01 NORTH | 659350 | BISON___-GE7 | 115 | 1.5589 | 1.559 | 0.0001
GEN-2020-091 | 01 NORTH | 659351 | BISON___-GE4 | 230 | 3.7082 | 3.7094 | 0.0012
GEN-2020-091 | 01 NORTH | 659352 | BISON___-GE8 | 69 | 2.2866 | 2.2867 | 0.0001
GEN-2020-091 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 7.4461 | 7.473 | 0.0269
GEN-2020-091 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 8.5488 | 8.5627 | 0.0139
GEN-2020-091 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 8.5775 | 8.6187 | 0.0412
GEN-2020-091 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.3121 | 11.336 | 0.0239
GEN-2020-091 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 4.225 | 4.301 | 0.076
GEN-2020-091 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 9.647 | 9.7783 | 0.1313
GEN-2020-091 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 7.4913 | 7.7334 | 0.2421
GEN-2020-091 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 16.2432 | 16.5622 | 0.319
GEN-2020-091 | 01 NORTH | 659400 | ND.SUN._-PP4 | 230 | 5.3051 | 5.3071 | 0.002
GEN-2020-091 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.0658 | 4.0771 | 0.0113
GEN-2020-091 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 15.9191 | 15.9549 | 0.0358
GEN-2020-091 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1962 | 4.1965 | 0.0003
GEN-2020-091 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.0365 | 17.0552 | 0.0187
GEN-2020-091 | 01 NORTH | 659423 | GR.LS-LO-BE3 | 345 | 6.2933 | 6.2935 | 0.0002
GEN-2020-091 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.0365 | 17.0552 | 0.0187
GEN-2020-091 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 6.4708 | 6.5017 | 0.0309
GEN-2020-091 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9506 | 1.951 | 0.0004
GEN-2020-091 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7538 | 1.7541 | 0.0003
GEN-2020-091 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.9074 | 6.9164 | 0.009
GEN-2020-091 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6899 | 3.6917 | 0.0018
GEN-2020-091 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 16.1546 | 16.472 | 0.3174
GEN-2020-091 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 16.165 | 16.4826 | 0.3176
GEN-2020-091 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 5.097 | 5.1149 | 0.0179
GEN-2020-091 | 01 NORTH | 659535 | BEAVRHIL-GW4 | 230 | 5.4643 | 5.4708 | 0.0065
GEN-2020-091 | 01 NORTH | 659536 | BEAVRHIL-GW7 | 115 | 3.9433 | 3.945 | 0.0017
GEN-2020-091 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9506 | 1.951 | 0.0004
GEN-2020-091 | 01 NORTH | 659550 | LNGBUTTE-RR4 | 230 | 5.7219 | 5.7243 | 0.0024
GEN-2020-091 | 01 NORTH | 659551 | LNGBUTTE-RR7 | 115 | 3.5508 | 3.5512 | 0.0004
GEN-2020-091 | 01 NORTH | 659553 | RAIDER__-RR7 | 115 | 2.3969 | 2.3971 | 0.0002
GEN-2020-091 | 01 NORTH | 659554 | REDTRAIL-RR7 | 115 | 2.3733 | 2.3735 | 0.0002
GEN-2020-091 | 01 NORTH | 659555 | RICHRDTN-RR7 | 115 | 2.1958 | 2.196 | 0.0002
GEN-2020-091 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 6.8795 | 6.904 | 0.0245
GEN-2020-091 | 01 NORTH | 661011 | BEULAH27 | 115 | 9.4737 | 9.4751 | 0.0014
GEN-2020-091 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 10.6884 | 10.7294 | 0.041
GEN-2020-091 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 6.9091 | 6.9173 | 0.0082
GEN-2020-091 | 01 NORTH | 760998 | GEN-2017-214 | 230 | 3.2013 | 3.2019 | 0.0006
GEN-2020-091 | 01 NORTH | 763043 | GEN-2018-069 | 230 | 5.3503 | 5.3564 | 0.0061
GEN-2020-091 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 10.9961 | 11.0036 | 0.0075
GEN-2020-091 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 6.8551 | 6.8585 | 0.0034
GEN-2020-091 | 01 NORTH | 764210 | GEN-2020-021 | 345 | 3.6152 | 3.6154 | 0.0002
GEN-2020-091 | 01 NORTH | 764220 | G20-021-TAP | 345 | 4.2301 | 4.2303 | 0.0002
GEN-2020-091 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 7.3843 | 7.6265 | 0.2422
GEN-2020-091 | 01 NORTH | 765070 | GEN-2020-083 | 115 | 5.5377 | 5.5405 | 0.0028
GEN-2020-091 | 01 NORTH | 800120 | UNDERWOOD 2 | 345 | 4.3079 | 4.3092 | 0.0013
GEN-2020-091 | 01 NORTH | 800121 | MAURINE 2 | 345 | 4.3015 | 4.3041 | 0.0026
GEN-2020-002 | 02 NEBRASKA | 640155 | DAVEY 7 | 115 | 11.4174 | 11.4197 | 0.0023
GEN-2020-002 | 02 NEBRASKA | 640320 | PLTSMTH8 | 69 | 5.473 | 5.4754 | 0.0024
GEN-2020-002 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 48.0473 | 48.0983 | 0.051
GEN-2020-002 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.8384 | 12.9175 | 0.0791
GEN-2020-002 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4581 | 34.4987 | 0.0406
GEN-2020-002 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 42.3602 | 42.4281 | 0.0679
GEN-2020-002 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 40.2762 | 40.3571 | 0.0809
GEN-2020-002 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.4577 | 23.5233 | 0.0656
GEN-2020-002 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.7716 | 43.8416 | 0.07
GEN-2020-002 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 37.2251 | 37.2765 | 0.0514
GEN-2020-002 | 02 NEBRASKA | 647014 | S914A 8 | 69 | 11.393 | 11.736 | 0.343
GEN-2020-002 | 02 NEBRASKA | 647079 | 979TP 8 | 69 | 7.0268 | 7.0384 | 0.0116
GEN-2020-002 | 02 NEBRASKA | 647091 | 991TP 8 | 69 | 11.7678 | 11.8035 | 0.0357
GEN-2020-002 | 02 NEBRASKA | 647100 | ASH GRV8 | 69 | 6.9341 | 6.9533 | 0.0192
GEN-2020-002 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6808 | 14.6931 | 0.0123
GEN-2020-002 | 02 NEBRASKA | 647427 | FREM G 8 | 69 | 14.3924 | 14.4251 | 0.0327
GEN-2020-002 | 02 NEBRASKA | 647846 | S6846 8 | 69 | 7.376 | 8.0559 | 0.6799
GEN-2020-002 | 02 NEBRASKA | 647900 | S900 8 | 69 | 8.0792 | 8.1053 | 0.0261
GEN-2020-002 | 02 NEBRASKA | 647902 | S902 8 | 69 | 8.9862 | 9.2048 | 0.2186
GEN-2020-002 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.7445 | 8.7497 | 0.0052
GEN-2020-002 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1139 | 27.1676 | 0.0537
GEN-2020-002 | 02 NEBRASKA | 647914 | S914 8 | 69 | 7.7989 | 7.9119 | 0.113
GEN-2020-002 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.9731 | 22.9958 | 0.0227
GEN-2020-002 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5044 | 26.5228 | 0.0184
GEN-2020-002 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.0365 | 9.1477 | 0.1112
GEN-2020-002 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1593 | 20.1826 | 0.0233
GEN-2020-002 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4767 | 7.4855 | 0.0088
GEN-2020-002 | 02 NEBRASKA | 647972 | S972 8 | 69 | 4.284 | 4.2888 | 0.0048
GEN-2020-002 | 02 NEBRASKA | 647979 | S979 8 | 69 | 6.8775 | 6.8885 | 0.011
GEN-2020-002 | 02 NEBRASKA | 647982 | S982 8 | 69 | 3.8349 | 3.8372 | 0.0023
GEN-2020-002 | 02 NEBRASKA | 647983 | S983 8 | 69 | 7.178 | 7.6266 | 0.4486
GEN-2020-002 | 02 NEBRASKA | 647984 | S984 8 | 69 | 7.8793 | 7.9968 | 0.1175
GEN-2020-002 | 02 NEBRASKA | 647985 | S985 8 | 69 | 8.1538 | 8.1595 | 0.0057
GEN-2020-002 | 02 NEBRASKA | 647988 | S988 8 | 69 | 2.8883 | 2.91 | 0.0217
GEN-2020-002 | 02 NEBRASKA | 647991 | S991 8 | 69 | 9.8836 | 9.9087 | 0.0251
GEN-2020-002 | 02 NEBRASKA | 650169 | 70&BLUFF 5 | 161 | 8.9202 | 8.935 | 0.0148
GEN-2020-002 | 02 NEBRASKA | 650261 | 56&I80 7 | 115 | 23.0239 | 23.033 | 0.0091
GEN-2020-002 | 02 NEBRASKA | 650269 | 70&BLUFF 7 | 115 | 25.7003 | 25.7129 | 0.0126
GEN-2020-002 | 02 NEBRASKA | 650275 | 84&BLUFF 7 | 115 | 27.0499 | 27.0615 | 0.0116
GEN-2020-002 | 02 NEBRASKA | 650277 | TBGS_A 7 | 115 | 25.7367 | 25.7471 | 0.0104
GEN-2020-002 | 02 NEBRASKA | 650278 | TBGS_B 7 | 115 | 25.918 | 25.9285 | 0.0105
GEN-2020-002 | 02 NEBRASKA | 764570 | GEN-2020-002 | 69 | 7.376 | 8.0559 | 0.6799
GEN-2020-002 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 37.2251 | 37.2765 | 0.0514
GEN-2020-002 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 37.2251 | 37.2765 | 0.0514
GEN-2020-002 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 37.2251 | 37.2765 | 0.0514
GEN-2020-011 | 02 NEBRASKA | 530552 | GORHAM 3 | 115 | 3.2 | 3.2008 | 0.0008
GEN-2020-011 | 02 NEBRASKA | 530553 | S HAYS 3 | 115 | 8.577 | 8.5834 | 0.0064
GEN-2020-011 | 02 NEBRASKA | 530558 | KNOLL N 6 | 230 | 10.4179 | 10.4434 | 0.0255
GEN-2020-011 | 02 NEBRASKA | 530560 | WKNNY 3 | 115 | 2.2357 | 2.2361 | 0.0004
GEN-2020-011 | 02 NEBRASKA | 530561 | KNOLL 3 | 115 | 10.5156 | 10.5252 | 0.0096
GEN-2020-011 | 02 NEBRASKA | 530582 | S HAYS6 | 230 | 8.5981 | 8.6109 | 0.0128
GEN-2020-011 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 7.5592 | 7.5915 | 0.0323
GEN-2020-011 | 02 NEBRASKA | 530584 | POSTROCK6 | 230 | 10.4999 | 10.5259 | 0.026
GEN-2020-011 | 02 NEBRASKA | 530592 | SMOKYHL6 | 230 | 6.185 | 6.1869 | 0.0019
GEN-2020-011 | 02 NEBRASKA | 530593 | SMKYP1 6 | 230 | 5.4515 | 5.4529 | 0.0014
GEN-2020-011 | 02 NEBRASKA | 530599 | SMKYP2 6 | 230 | 5.7127 | 5.7143 | 0.0016
GEN-2020-011 | 02 NEBRASKA | 530610 | SHAYS_230 | 230 | 3.5059 | 3.5076 | 0.0017
GEN-2020-011 | 02 NEBRASKA | 530676 | GMEC 3 | 115 | 9.9571 | 9.9657 | 0.0086
GEN-2020-011 | 02 NEBRASKA | 530677 | OGALATP3 | 115 | 2.6458 | 2.6464 | 0.0006
GEN-2020-011 | 02 NEBRASKA | 530684 | RUSLPMP3 | 115 | 2.0979 | 2.0983 | 0.0004
GEN-2020-011 | 02 NEBRASKA | 530702 | BUCKEYE_230 | 230 | 7.8244 | 7.8382 | 0.0138
GEN-2020-011 | 02 NEBRASKA | 530714 | ANGUS 3 | 115 | 5.3485 | 5.351 | 0.0025
GEN-2020-011 | 02 NEBRASKA | 530720 | KNOLL S 6 | 230 | 10.4179 | 10.4434 | 0.0255
GEN-2020-011 | 02 NEBRASKA | 530725 | PFEIFER 3 | 115 | 3.5271 | 3.5282 | 0.0011
GEN-2020-011 | 02 NEBRASKA | 531429 | MINGO 3 | 115 | 12.5859 | 12.5893 | 0.0034
GEN-2020-011 | 02 NEBRASKA | 531449 | HOLCOMB7 | 345 | 9.0577 | 9.0608 | 0.0031
GEN-2020-011 | 02 NEBRASKA | 531451 | MINGO 7 | 345 | 6.137 | 6.1394 | 0.0024
GEN-2020-011 | 02 NEBRASKA | 531465 | SETAB 7 | 345 | 6.7518 | 6.7539 | 0.0021
GEN-2020-011 | 02 NEBRASKA | 531469 | SPERVIL7 | 345 | 10.9305 | 10.9412 | 0.0107
GEN-2020-011 | 02 NEBRASKA | 531492 | OG ONEOK | 115 | 2.1574 | 2.1578 | 0.0004
GEN-2020-011 | 02 NEBRASKA | 531497 | TURKEYR3 | 115 | 1.8067 | 1.807 | 0.0003
GEN-2020-011 | 02 NEBRASKA | 531501 | BUCKNER7 | 345 | 8.4583 | 8.4625 | 0.0042
GEN-2020-011 | 02 NEBRASKA | 531502 | CIMRRN 7 | 345 | 6.8663 | 6.8691 | 0.0028
GEN-2020-011 | 02 NEBRASKA | 531504 | CIMWD2 7 | 345 | 6.9814 | 6.9843 | 0.0029
GEN-2020-011 | 02 NEBRASKA | 531623 | EASTFORK3 | 115 | 10.0175 | 10.0197 | 0.0022
GEN-2020-011 | 02 NEBRASKA | 531632 | GEN-2015-065 | 345 | 5.4481 | 5.45 | 0.0019
GEN-2020-011 | 02 NEBRASKA | 539117 | SPRVILL-EHVB | 230 | 10.8973 | 10.904 | 0.0067
GEN-2020-011 | 02 NEBRASKA | 539132 | SPRVILL-EHV2 | 230 | 9.4885 | 9.4935 | 0.005
GEN-2020-011 | 02 NEBRASKA | 539628 | NW-DGTP3 | 115 | 3.549 | 3.5492 | 0.0002
GEN-2020-011 | 02 NEBRASKA | 539667 | HAGGARD3 | 115 | 2.5243 | 2.5244 | 0.0001
GEN-2020-011 | 02 NEBRASKA | 539679 | GRTBEND6 | 230 | 7.9286 | 7.9339 | 0.0053
GEN-2020-011 | 02 NEBRASKA | 539688 | S-DODGE3 | 115 | 6.6318 | 6.6325 | 0.0007
GEN-2020-011 | 02 NEBRASKA | 539694 | SPEARVL3 | 115 | 9.6545 | 9.6567 | 0.0022
GEN-2020-011 | 02 NEBRASKA | 539695 | SPEARVL6 | 230 | 11.1318 | 11.1387 | 0.0069
GEN-2020-011 | 02 NEBRASKA | 539699 | W-DODGE3 | 115 | 4.3445 | 4.3447 | 0.0002
GEN-2020-011 | 02 NEBRASKA | 539759 | SPRVL 3 | 115 | 12.2804 | 12.2844 | 0.004
GEN-2020-011 | 02 NEBRASKA | 539771 | NFTDODG3 | 115 | 9.2244 | 9.2259 | 0.0015
GEN-2020-011 | 02 NEBRASKA | 539778 | GYCOTAP3 | 115 | 2.5243 | 2.5244 | 0.0001
GEN-2020-011 | 02 NEBRASKA | 539779 | GRAY CO3 | 115 | 2.5243 | 2.5244 | 0.0001
GEN-2020-011 | 02 NEBRASKA | 539800 | CLARKCOUNTY7 | 345 | 10.1606 | 10.1668 | 0.0062
GEN-2020-011 | 02 NEBRASKA | 539803 | IRONWOOD7 | 345 | 10.5384 | 10.5481 | 0.0097
GEN-2020-011 | 02 NEBRASKA | 539813 | TRANSFORMER | 345 | 8.8631 | 8.8677 | 0.0046
GEN-2020-011 | 02 NEBRASKA | 539815 | IRONWOOD WF7 | 345 | 9.7319 | 9.7402 | 0.0083
GEN-2020-011 | 02 NEBRASKA | 539840 | GEN-2011-008 | 345 | 8.51 | 8.5142 | 0.0042
GEN-2020-011 | 02 NEBRASKA | 539841 | G-2011-008-1 | 345 | 8.51 | 8.5142 | 0.0042
GEN-2020-011 | 02 NEBRASKA | 539855 | G-2011-008-2 | 345 | 7.3344 | 7.3376 | 0.0032
GEN-2020-011 | 02 NEBRASKA | 539857 | G-2011-008-3 | 345 | 6.894 | 6.8969 | 0.0029
GEN-2020-011 | 02 NEBRASKA | 539944 | LOCHS | 115 | 3.2807 | 3.2809 | 0.0002
GEN-2020-011 | 02 NEBRASKA | 560080 | G16-046-TAP | 345 | 9.1847 | 9.1905 | 0.0058
GEN-2020-011 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.1386 | 7.3105 | 0.1719
GEN-2020-011 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.3918 | 43.4262 | 0.0344
GEN-2020-011 | 02 NEBRASKA | 579480 | GEN-2008-124 | 345 | 10.2425 | 10.2517 | 0.0092
GEN-2020-011 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.1804 | 19.1868 | 0.0064
GEN-2020-011 | 02 NEBRASKA | 584650 | GEN-2015-023 | 345 | 12.5995 | 12.6091 | 0.0096
GEN-2020-011 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.3031 | 12.348 | 0.0449
GEN-2020-011 | 02 NEBRASKA | 587310 | GEN-2016-046 | 345 | 8.1732 | 8.1779 | 0.0047
GEN-2020-011 | 02 NEBRASKA | 587311 | G16-046XFMR1 | 115 | 12.2838 | 12.2872 | 0.0034
GEN-2020-011 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.0369 | 6.1554 | 0.1185
GEN-2020-011 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.2983 | 6.3503 | 0.052
GEN-2020-011 | 02 NEBRASKA | 640063 | AURORA_7 | 115 | 7.281 | 7.2852 | 0.0042
GEN-2020-011 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 9.7609 | 10.2832 | 0.5223
GEN-2020-011 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 15.1295 | 15.3423 | 0.2128
GEN-2020-011 | 02 NEBRASKA | 640082 | BEVERLY7 | 115 | 4.8872 | 4.8882 | 0.001
GEN-2020-011 | 02 NEBRASKA | 640083 | BEVERLY8 | 69 | 4.4653 | 4.4658 | 0.0005
GEN-2020-011 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 15.9252 | 15.9271 | 0.0019
GEN-2020-011 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.2624 | 7.2745 | 0.0121
GEN-2020-011 | 02 NEBRASKA | 640096 | CALAMS 7 | 115 | 3.5516 | 3.5517 | 0.0001
GEN-2020-011 | 02 NEBRASKA | 640100 | CAMBRIG7 | 115 | 4.2914 | 4.2928 | 0.0014
GEN-2020-011 | 02 NEBRASKA | 640101 | CAMBRIG8 | 69 | 2.3141 | 2.3144 | 0.0003
GEN-2020-011 | 02 NEBRASKA | 640102 | CANADAY4 | 230 | 6.3526 | 6.3621 | 0.0095
GEN-2020-011 | 02 NEBRASKA | 640103 | CANADAY7 | 115 | 13.7873 | 13.8105 | 0.0232
GEN-2020-011 | 02 NEBRASKA | 640107 | CENCITY7 | 115 | 5.2925 | 5.2942 | 0.0017
GEN-2020-011 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 10.9049 | 10.9062 | 0.0013
GEN-2020-011 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 11.0142 | 11.0187 | 0.0045
GEN-2020-011 | 02 NEBRASKA | 640131 | COLMB.W4 | 230 | 10.379 | 10.3835 | 0.0045
GEN-2020-011 | 02 NEBRASKA | 640133 | COLMBUS4 | 230 | 12.1647 | 12.1699 | 0.0052
GEN-2020-011 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.9616 | 26.9666 | 0.005
GEN-2020-011 | 02 NEBRASKA | 640144 | COZAD 7 | 115 | 4.6037 | 4.6057 | 0.002
GEN-2020-011 | 02 NEBRASKA | 640145 | COZAD 8 | 69 | 3.414 | 3.4147 | 0.0007
GEN-2020-011 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4323 | 8.434 | 0.0017
GEN-2020-011 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.1934 | 6.204 | 0.0106
GEN-2020-011 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8676 | 3.8701 | 0.0025
GEN-2020-011 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9313 | 9.9374 | 0.0061
GEN-2020-011 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.311 | 4.3117 | 0.0007
GEN-2020-011 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.0245 | 16.0743 | 0.0498
GEN-2020-011 | 02 NEBRASKA | 640184 | GENTLMN4 | 230 | 19.3274 | 19.359 | 0.0316
GEN-2020-011 | 02 NEBRASKA | 640194 | GOSPER 7 | 115 | 4.4893 | 4.491 | 0.0017
GEN-2020-011 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.607 | 17.6735 | 0.0665
GEN-2020-011 | 02 NEBRASKA | 640201 | GR ISLD7 | 115 | 23.8342 | 23.8884 | 0.0542
GEN-2020-011 | 02 NEBRASKA | 640206 | GUIDE R7 | 115 | 4.3641 | 4.3682 | 0.0041
GEN-2020-011 | 02 NEBRASKA | 640207 | GUIDE R8 | 69 | 2.2437 | 2.2443 | 0.0006
GEN-2020-011 | 02 NEBRASKA | 640214 | HASTING4 | 230 | 7.6083 | 7.6235 | 0.0152
GEN-2020-011 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.5824 | 19.6465 | 0.0641
GEN-2020-011 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.5978 | 4.6059 | 0.0081
GEN-2020-011 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.6289 | 3.6319 | 0.003
GEN-2020-011 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 7.3473 | 7.3687 | 0.0214
GEN-2020-011 | 02 NEBRASKA | 640240 | JOHN.1 7 | 115 | 8.5101 | 8.5182 | 0.0081
GEN-2020-011 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 12.7749 | 12.7948 | 0.0199
GEN-2020-011 | 02 NEBRASKA | 640244 | JOHN.LK7 | 115 | 8.9299 | 8.9389 | 0.009
GEN-2020-011 | 02 NEBRASKA | 640245 | JOHN.LK8 | 69 | 4.2851 | 4.2863 | 0.0012
GEN-2020-011 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.8136 | 9.8474 | 0.0338
GEN-2020-011 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.49 | 12.5582 | 0.0682
GEN-2020-011 | 02 NEBRASKA | 640252 | KEYSTON3 | 345 | 8.8167 | 8.8278 | 0.0111
GEN-2020-011 | 02 NEBRASKA | 640253 | KEYSTON7 | 115 | 14.8597 | 14.8686 | 0.0089
GEN-2020-011 | 02 NEBRASKA | 640255 | KINGSLY7 | 115 | 9.2863 | 9.2895 | 0.0032
GEN-2020-011 | 02 NEBRASKA | 640256 | LXNGTN 7 | 115 | 7.182 | 7.1892 | 0.0072
GEN-2020-011 | 02 NEBRASKA | 640257 | LEXNGTN8 | 69 | 3.761 | 3.7622 | 0.0012
GEN-2020-011 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.4847 | 8.519 | 0.0343
GEN-2020-011 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2217 | 4.2267 | 0.005
GEN-2020-011 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.6534 | 8.6566 | 0.0032
GEN-2020-011 | 02 NEBRASKA | 640270 | MCCOOK 8 | 69 | 4.5773 | 4.5778 | 0.0005
GEN-2020-011 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.5495 | 11.5745 | 0.025
GEN-2020-011 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.758 | 14.7713 | 0.0133
GEN-2020-011 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7341 | 5.7353 | 0.0012
GEN-2020-011 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.508 | 7.5461 | 0.0381
GEN-2020-011 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.7795 | 23.8276 | 0.0481
GEN-2020-011 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.4508 | 44.4852 | 0.0344
GEN-2020-011 | 02 NEBRASKA | 640282 | N.HAST 7 | 115 | 13.7785 | 13.8115 | 0.033
GEN-2020-011 | 02 NEBRASKA | 640286 | N.PLATT4 | 230 | 13.3008 | 13.3179 | 0.0171
GEN-2020-011 | 02 NEBRASKA | 640287 | N.PLATT7 | 115 | 18.8018 | 18.8188 | 0.017
GEN-2020-011 | 02 NEBRASKA | 640288 | N.PLATT8 | 69 | 5.1258 | 5.1266 | 0.0008
GEN-2020-011 | 02 NEBRASKA | 640302 | OGALALA4 | 230 | 7.9051 | 7.9097 | 0.0046
GEN-2020-011 | 02 NEBRASKA | 640304 | OGALALANPPD7 | 115 | 14.8779 | 14.8864 | 0.0085
GEN-2020-011 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.622 | 2.6246 | 0.0026
GEN-2020-011 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.5594 | 2.561 | 0.0016
GEN-2020-011 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.3339 | 8.4703 | 0.1364
GEN-2020-011 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.8846 | 16.9883 | 0.1037
GEN-2020-011 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9403 | 4.9455 | 0.0052
GEN-2020-011 | 02 NEBRASKA | 640321 | PROSSER7 | 115 | 6.9821 | 6.9969 | 0.0148
GEN-2020-011 | 02 NEBRASKA | 640322 | PROSSER8 | 69 | 3.8955 | 3.8983 | 0.0028
GEN-2020-011 | 02 NEBRASKA | 640323 | RAVENNA7 | 115 | 6.208 | 6.2148 | 0.0068
GEN-2020-011 | 02 NEBRASKA | 640324 | RAVENNA8 | 69 | 3.8699 | 3.8715 | 0.0016
GEN-2020-011 | 02 NEBRASKA | 640325 | REDWILO3 | 345 | 6.3852 | 6.3901 | 0.0049
GEN-2020-011 | 02 NEBRASKA | 640326 | REDWILO7 | 115 | 11.3522 | 11.3575 | 0.0053
GEN-2020-011 | 02 NEBRASKA | 640330 | RIVERDL4 | 230 | 7.5662 | 7.5856 | 0.0194
GEN-2020-011 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.3694 | 13.4112 | 0.0418
GEN-2020-011 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.7125 | 6.7188 | 0.0063
GEN-2020-011 | 02 NEBRASKA | 640353 | ST.LIB 7 | 115 | 9.9331 | 9.9418 | 0.0087
GEN-2020-011 | 02 NEBRASKA | 640355 | ST.PAUL7 | 115 | 3.9819 | 3.9833 | 0.0014
GEN-2020-011 | 02 NEBRASKA | 640359 | STAPLETON 7 | 115 | 4.2474 | 4.2481 | 0.0007
GEN-2020-011 | 02 NEBRASKA | 640360 | STAPLETON 8 | 69 | 3.4638 | 3.4641 | 0.0003
GEN-2020-011 | 02 NEBRASKA | 640365 | STOCKVL7 | 115 | 4.6631 | 4.664 | 0.0009
GEN-2020-011 | 02 NEBRASKA | 640366 | STOCKVL8 | 69 | 3.4036 | 3.4039 | 0.0003
GEN-2020-011 | 02 NEBRASKA | 640368 | SUPEROR7 | 115 | 3.4639 | 3.4656 | 0.0017
GEN-2020-011 | 02 NEBRASKA | 640372 | SUTTON 7 | 115 | 6.5212 | 6.5251 | 0.0039
GEN-2020-011 | 02 NEBRASKA | 640373 | SUTTON 8 | 69 | 3.9249 | 3.9257 | 0.0008
GEN-2020-011 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 10.9945 | 11.1619 | 0.1674
GEN-2020-011 | 02 NEBRASKA | 640381 | THEDFRD7 | 115 | 9.2538 | 9.2568 | 0.003
GEN-2020-011 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.4333 | 9.4652 | 0.0319
GEN-2020-011 | 02 NEBRASKA | 640407 | WESTMIN7 | 115 | 8.1074 | 8.115 | 0.0076
GEN-2020-011 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.4163 | 8.4204 | 0.0041
GEN-2020-011 | 02 NEBRASKA | 640416 | AURORA_8 | 69 | 4.0866 | 4.0874 | 0.0008
GEN-2020-011 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5293 | 2.5295 | 0.0002
GEN-2020-011 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 4.0372 | 4.041 | 0.0038
GEN-2020-011 | 02 NEBRASKA | 640500 | THEDFRD3 | 345 | 5.5403 | 5.5439 | 0.0036
GEN-2020-011 | 02 NEBRASKA | 640510 | HOLT.CO3 | 345 | 12.7663 | 12.7762 | 0.0099
GEN-2020-011 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 12.2757 | 12.2812 | 0.0055
GEN-2020-011 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.3031 | 12.348 | 0.0449
GEN-2020-011 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.77 | 6.7825 | 0.0125
GEN-2020-011 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4706 | 5.4784 | 0.0078
GEN-2020-011 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.2573 | 23.3021 | 0.0448
GEN-2020-011 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.3918 | 43.4262 | 0.0344
GEN-2020-011 | 02 NEBRASKA | 641085 | E7THST 7 | 115 | 18.5059 | 18.5631 | 0.0572
GEN-2020-011 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.1908 | 18.2377 | 0.0469
GEN-2020-011 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.5824 | 19.6465 | 0.0641
GEN-2020-011 | 02 NEBRASKA | 641090 | S. 281 7 | 115 | 11.4267 | 11.4466 | 0.0199
GEN-2020-011 | 02 NEBRASKA | 642071 | SUB-D 7 | 115 | 17.5267 | 17.5563 | 0.0296
GEN-2020-011 | 02 NEBRASKA | 642072 | SUB-E 7 | 115 | 17.2198 | 17.247 | 0.0272
GEN-2020-011 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7871 | 17.8049 | 0.0178
GEN-2020-011 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3849 | 21.4023 | 0.0174
GEN-2020-011 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2806 | 21.3009 | 0.0203
GEN-2020-011 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.7373 | 25.7472 | 0.0099
GEN-2020-011 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 27.8663 | 27.8769 | 0.0106
GEN-2020-011 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.4489 | 23.4567 | 0.0078
GEN-2020-011 | 02 NEBRASKA | 652832 | GRPRAR1-LNX3 | 345 | 8.9052 | 8.9077 | 0.0025
GEN-2020-011 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 13.4233 | 13.4843 | 0.061
GEN-2020-011 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 13.3008 | 13.3604 | 0.0596
GEN-2020-011 | 02 NEBRASKA | 659133 | SIDNEY__-MB3 | 345 | 6.1501 | 6.1525 | 0.0024
GEN-2020-011 | 02 NEBRASKA | 659134 | SIDNEY___TS4 | 230 | 6.422 | 6.424 | 0.002
GEN-2020-011 | 02 NEBRASKA | 659425 | SD.LS-KS-MB3 | 345 | 6.1501 | 6.1525 | 0.0024
GEN-2020-011 | 02 NEBRASKA | 760767 | GEN-2017-144 | 345 | 11.9336 | 11.9422 | 0.0086
GEN-2020-011 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.1022 | 10.1209 | 0.0187
GEN-2020-011 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 6.9921 | 7.0051 | 0.013
GEN-2020-011 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8401 | 5.849 | 0.0089
GEN-2020-011 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 7.8309 | 7.8681 | 0.0372
GEN-2020-011 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 8.2248 | 8.2661 | 0.0413
GEN-2020-011 | 02 NEBRASKA | 763670 | GEN-2019-030 | 345 | 7.7633 | 7.7678 | 0.0045
GEN-2020-011 | 02 NEBRASKA | 763677 | G19-030-TAP | 345 | 9.2058 | 9.2122 | 0.0064
GEN-2020-011 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 43.2848 | 43.3189 | 0.0341
GEN-2020-011 | 02 NEBRASKA | 763758 | GEN-2019-044 | 115 | 6.0062 | 6.0068 | 0.0006
GEN-2020-011 | 02 NEBRASKA | 763846 | G19-053/055 | 230 | 6.3692 | 6.3719 | 0.0027
GEN-2020-011 | 02 NEBRASKA | 763850 | G19-055-TAP | 230 | 6.4466 | 6.4494 | 0.0028
GEN-2020-011 | 02 NEBRASKA | 763890 | GEN-2019-058 | 345 | 9.9951 | 10.001 | 0.0059
GEN-2020-011 | 02 NEBRASKA | 764420 | GEN-2020-011 | 345 | 9.7426 | 10.265 | 0.5224
GEN-2020-011 | 02 NEBRASKA | 764431 | G20-011-SS1 | 345 | 9.7318 | 10.2535 | 0.5217
GEN-2020-011 | 02 NEBRASKA | 764432 | G20-011-SS2 | 345 | 9.6178 | 10.1303 | 0.5125
GEN-2020-011 | 02 NEBRASKA | 764433 | G20-011-SS3 | 345 | 9.6523 | 10.1698 | 0.5175
GEN-2020-011 | 02 NEBRASKA | 764434 | G20-011-SS4 | 345 | 9.4549 | 9.9566 | 0.5017
GEN-2020-011 | 02 NEBRASKA | 764435 | GEN-2020-013 | 115 | 7.1535 | 7.1736 | 0.0201
GEN-2020-011 | 02 NEBRASKA | 764445 | G20-013-TAP | 115 | 7.1638 | 7.1839 | 0.0201
GEN-2020-011 | 02 NEBRASKA | 764446 | G20-013-SS1 | 115 | 7.1352 | 7.1551 | 0.0199
GEN-2020-011 | 02 NEBRASKA | 764447 | G20-013-SS2 | 115 | 6.8423 | 6.8605 | 0.0182
GEN-2020-011 | 02 NEBRASKA | 764448 | G20-013-SS3 | 115 | 6.7759 | 6.7937 | 0.0178
GEN-2020-011 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.927 | 11.93 | 0.003
GEN-2020-011 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7695 | 16.7756 | 0.0061
GEN-2020-013 | 02 NEBRASKA | 530583 | POSTROCK7 | 345 | 7.5856 | 7.5915 | 0.0059
GEN-2020-013 | 02 NEBRASKA | 560082 | G16-050-TAP | 345 | 7.2802 | 7.3105 | 0.0303
GEN-2020-013 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.3302 | 12.348 | 0.0178
GEN-2020-013 | 02 NEBRASKA | 587350 | GEN-2016-050 | 345 | 6.1346 | 6.1554 | 0.0208
GEN-2020-013 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.3372 | 6.3503 | 0.0131
GEN-2020-013 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 10.1896 | 10.2832 | 0.0936
GEN-2020-013 | 02 NEBRASKA | 640066 | AXTELL 7 | 115 | 14.9568 | 15.3423 | 0.3855
GEN-2020-013 | 02 NEBRASKA | 640093 | C.CREEK4 | 230 | 7.2297 | 7.2745 | 0.0448
GEN-2020-013 | 02 NEBRASKA | 640100 | CAMBRIG7 | 115 | 4.2853 | 4.2928 | 0.0075
GEN-2020-013 | 02 NEBRASKA | 640101 | CAMBRIG8 | 69 | 2.3131 | 2.3144 | 0.0013
GEN-2020-013 | 02 NEBRASKA | 640102 | CANADAY4 | 230 | 6.3138 | 6.3621 | 0.0483
GEN-2020-013 | 02 NEBRASKA | 640103 | CANADAY7 | 115 | 13.6391 | 13.8105 | 0.1714
GEN-2020-013 | 02 NEBRASKA | 640144 | COZAD 7 | 115 | 4.5902 | 4.6057 | 0.0155
GEN-2020-013 | 02 NEBRASKA | 640145 | COZAD 8 | 69 | 3.4095 | 3.4147 | 0.0052
GEN-2020-013 | 02 NEBRASKA | 640161 | ELMCRK_7 | 115 | 6.1689 | 6.204 | 0.0351
GEN-2020-013 | 02 NEBRASKA | 640162 | ELMCRK 8 | 69 | 3.8618 | 3.8701 | 0.0083
GEN-2020-013 | 02 NEBRASKA | 640183 | GENTLMN3 | 345 | 16.0482 | 16.0743 | 0.0261
GEN-2020-013 | 02 NEBRASKA | 640194 | GOSPER 7 | 115 | 4.4797 | 4.491 | 0.0113
GEN-2020-013 | 02 NEBRASKA | 640196 | GOTHNBG7 | 115 | 4.4605 | 4.4717 | 0.0112
GEN-2020-013 | 02 NEBRASKA | 640197 | GOTHNBG8 | 69 | 2.6074 | 2.6097 | 0.0023
GEN-2020-013 | 02 NEBRASKA | 640206 | GUIDE R7 | 115 | 4.3633 | 4.3682 | 0.0049
GEN-2020-013 | 02 NEBRASKA | 640207 | GUIDE R8 | 69 | 2.2435 | 2.2443 | 0.0008
GEN-2020-013 | 02 NEBRASKA | 640215 | HASTING7 | 115 | 19.5697 | 19.6465 | 0.0768
GEN-2020-013 | 02 NEBRASKA | 640222 | HILDRTH7 | 115 | 4.3944 | 4.6059 | 0.2115
GEN-2020-013 | 02 NEBRASKA | 640223 | HILDRTH8 | 69 | 3.5527 | 3.6319 | 0.0792
GEN-2020-013 | 02 NEBRASKA | 640224 | HOLDREG7 | 115 | 6.3054 | 7.3687 | 1.0633
GEN-2020-013 | 02 NEBRASKA | 640238 | JEFFREY7 | 115 | 6.2081 | 6.2225 | 0.0144
GEN-2020-013 | 02 NEBRASKA | 640240 | JOHN.1 7 | 115 | 8.4461 | 8.5182 | 0.0721
GEN-2020-013 | 02 NEBRASKA | 640242 | JOHN.2 7 | 115 | 12.6126 | 12.7948 | 0.1822
GEN-2020-013 | 02 NEBRASKA | 640244 | JOHN.LK7 | 115 | 8.858 | 8.9389 | 0.0809
GEN-2020-013 | 02 NEBRASKA | 640245 | JOHN.LK8 | 69 | 4.275 | 4.2863 | 0.0113
GEN-2020-013 | 02 NEBRASKA | 640248 | KEAR.NE7 | 115 | 9.7735 | 9.8474 | 0.0739
GEN-2020-013 | 02 NEBRASKA | 640250 | KEARNEY7 | 115 | 12.413 | 12.5582 | 0.1452
GEN-2020-013 | 02 NEBRASKA | 640256 | LXNGTN 7 | 115 | 7.1472 | 7.1892 | 0.042
GEN-2020-013 | 02 NEBRASKA | 640257 | LEXNGTN8 | 69 | 3.7551 | 3.7622 | 0.0071
GEN-2020-013 | 02 NEBRASKA | 640261 | LOWELL 7 | 115 | 8.4541 | 8.519 | 0.0649
GEN-2020-013 | 02 NEBRASKA | 640262 | LOWELL 8 | 69 | 4.2171 | 4.2267 | 0.0096
GEN-2020-013 | 02 NEBRASKA | 640269 | MCCOOK 7 | 115 | 8.6507 | 8.6566 | 0.0059
GEN-2020-013 | 02 NEBRASKA | 640270 | MCCOOK 8 | 69 | 4.5768 | 4.5778 | 0.001
GEN-2020-013 | 02 NEBRASKA | 640275 | MINDEN 7 | 115 | 7.4756 | 7.5461 | 0.0705
GEN-2020-013 | 02 NEBRASKA | 640310 | ORLEANS7 | 115 | 2.465 | 2.6246 | 0.1596
GEN-2020-013 | 02 NEBRASKA | 640311 | ORLEANS8 | 69 | 2.4683 | 2.561 | 0.0927
GEN-2020-013 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.4213 | 8.4703 | 0.049
GEN-2020-013 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.8575 | 16.9883 | 0.1308
GEN-2020-013 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9388 | 4.9455 | 0.0067
GEN-2020-013 | 02 NEBRASKA | 640321 | PROSSER7 | 115 | 6.9726 | 6.9969 | 0.0243
GEN-2020-013 | 02 NEBRASKA | 640322 | PROSSER8 | 69 | 3.8937 | 3.8983 | 0.0046
GEN-2020-013 | 02 NEBRASKA | 640331 | RIVERDL7 | 115 | 13.3148 | 13.4112 | 0.0964
GEN-2020-013 | 02 NEBRASKA | 640332 | RIVERDL8 | 69 | 6.7042 | 6.7188 | 0.0146
GEN-2020-013 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1195 | 11.1619 | 0.0424
GEN-2020-013 | 02 NEBRASKA | 640383 | TOWER 7 | 115 | 9.3956 | 9.4652 | 0.0696
GEN-2020-013 | 02 NEBRASKA | 640407 | WESTMIN7 | 115 | 8.0477 | 8.115 | 0.0673
GEN-2020-013 | 02 NEBRASKA | 640448 | HOLDREGE 8 | 69 | 3.8332 | 4.041 | 0.2078
GEN-2020-013 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.3302 | 12.348 | 0.0178
GEN-2020-013 | 02 NEBRASKA | 640583 | ROSEMONT 7 | 115 | 6.7672 | 6.7825 | 0.0153
GEN-2020-013 | 02 NEBRASKA | 640584 | COTTONWD 7 | 115 | 5.4688 | 5.4784 | 0.0096
GEN-2020-013 | 02 NEBRASKA | 641087 | EGYCNTR7 | 115 | 18.1817 | 18.2377 | 0.056
GEN-2020-013 | 02 NEBRASKA | 641088 | HASTCTY7 | 115 | 19.5697 | 19.6465 | 0.0768
GEN-2020-013 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 13.4479 | 13.4843 | 0.0364
GEN-2020-013 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 7 | 7.0051 | 0.0051
GEN-2020-013 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8455 | 5.849 | 0.0035
GEN-2020-013 | 02 NEBRASKA | 763406 | GEN-2018-125 | 345 | 7.8563 | 7.8681 | 0.0118
GEN-2020-013 | 02 NEBRASKA | 763410 | G18-125-TAP | 345 | 8.253 | 8.2661 | 0.0131
GEN-2020-013 | 02 NEBRASKA | 764420 | GEN-2020-011 | 345 | 10.1717 | 10.265 | 0.0933
GEN-2020-013 | 02 NEBRASKA | 764431 | G20-011-SS1 | 345 | 10.1605 | 10.2535 | 0.093
GEN-2020-013 | 02 NEBRASKA | 764432 | G20-011-SS2 | 345 | 10.0395 | 10.1303 | 0.0908
GEN-2020-013 | 02 NEBRASKA | 764433 | G20-011-SS3 | 345 | 10.0783 | 10.1698 | 0.0915
GEN-2020-013 | 02 NEBRASKA | 764434 | G20-011-SS4 | 345 | 9.8689 | 9.9566 | 0.0877
GEN-2020-013 | 02 NEBRASKA | 764435 | GEN-2020-013 | 115 | 6.1061 | 7.1736 | 1.0675
GEN-2020-013 | 02 NEBRASKA | 764445 | G20-013-TAP | 115 | 6.1168 | 7.1839 | 1.0671
GEN-2020-013 | 02 NEBRASKA | 764446 | G20-013-SS1 | 115 | 6.0912 | 7.1551 | 1.0639
GEN-2020-013 | 02 NEBRASKA | 764447 | G20-013-SS2 | 115 | 5.8218 | 6.8605 | 1.0387
GEN-2020-013 | 02 NEBRASKA | 764448 | G20-013-SS3 | 115 | 5.7681 | 6.7937 | 1.0256
GEN-2020-025 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3349 | 30.3907 | 0.0558
GEN-2020-025 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.1295 | 23.1965 | 0.067
GEN-2020-025 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.8512 | 30.0304 | 0.1792
GEN-2020-025 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.0238 | 33.2629 | 0.2391
GEN-2020-025 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.2414 | 35.4256 | 0.1842
GEN-2020-025 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9261 | 29.9659 | 0.0398
GEN-2020-025 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.8911 | 25.9917 | 0.1006
GEN-2020-025 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.7777 | 23.8584 | 0.0807
GEN-2020-025 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.608 | 23.762 | 0.154
GEN-2020-025 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.8705 | 12.9175 | 0.047
GEN-2020-025 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.9589 | 36.1193 | 0.1604
GEN-2020-025 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.7601 | 43.9561 | 0.196
GEN-2020-025 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8119 | 26.8986 | 0.0867
GEN-2020-025 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.8223 | 29.9627 | 0.1404
GEN-2020-025 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.2593 | 27.3637 | 0.1044
GEN-2020-025 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.9158 | 26.0705 | 0.1547
GEN-2020-025 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0199 | 33.0861 | 0.0662
GEN-2020-025 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.0592 | 28.1682 | 0.109
GEN-2020-025 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.187 | 34.4987 | 0.3117
GEN-2020-025 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.9316 | 50.3723 | 0.4407
GEN-2020-025 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.249 | 23.3507 | 0.1017
GEN-2020-025 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 39.6638 | 40.0447 | 0.3809
GEN-2020-025 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 41.7419 | 42.4281 | 0.6862
GEN-2020-025 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.934 | 28.0853 | 0.1513
GEN-2020-025 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 39.6455 | 40.3571 | 0.7116
GEN-2020-025 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.3043 | 23.5233 | 0.219
GEN-2020-025 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.1341 | 43.8416 | 0.7075
GEN-2020-025 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 40.2133 | 40.9548 | 0.7415
GEN-2020-025 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-025 | 02 NEBRASKA | 647014 | S914A 8 | 69 | 11.7243 | 11.736 | 0.0117
GEN-2020-025 | 02 NEBRASKA | 647079 | 979TP 8 | 69 | 7.0336 | 7.0384 | 0.0048
GEN-2020-025 | 02 NEBRASKA | 647100 | ASH GRV8 | 69 | 6.9498 | 6.9533 | 0.0035
GEN-2020-025 | 02 NEBRASKA | 647846 | S6846 8 | 69 | 8.0524 | 8.0559 | 0.0035
GEN-2020-025 | 02 NEBRASKA | 647900 | S900 8 | 69 | 8.1005 | 8.1053 | 0.0048
GEN-2020-025 | 02 NEBRASKA | 647914 | S914 8 | 69 | 7.9068 | 7.9119 | 0.0051
GEN-2020-025 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.4958 | 26.5228 | 0.027
GEN-2020-025 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4793 | 7.4855 | 0.0062
GEN-2020-025 | 02 NEBRASKA | 647979 | S979 8 | 69 | 6.8839 | 6.8885 | 0.0046
GEN-2020-025 | 02 NEBRASKA | 647988 | S988 8 | 69 | 2.9093 | 2.91 | 0.0007
GEN-2020-025 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7926 | 17.8049 | 0.0123
GEN-2020-025 | 02 NEBRASKA | 650169 | 70&BLUFF 5 | 161 | 8.9249 | 8.935 | 0.0101
GEN-2020-025 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3733 | 21.4023 | 0.029
GEN-2020-025 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2788 | 21.3009 | 0.0221
GEN-2020-025 | 02 NEBRASKA | 650269 | 70&BLUFF 7 | 115 | 25.6973 | 25.7129 | 0.0156
GEN-2020-025 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3574 | 32.3776 | 0.0202
GEN-2020-025 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1007 | 22.1619 | 0.0612
GEN-2020-025 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7277 | 22.8013 | 0.0736
GEN-2020-025 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.061 | 17.0842 | 0.0232
GEN-2020-025 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0187 | 17.0417 | 0.023
GEN-2020-025 | 02 NEBRASKA | 764570 | GEN-2020-002 | 69 | 8.0524 | 8.0559 | 0.0035
GEN-2020-025 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-025 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-025 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-025 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.7777 | 23.8584 | 0.0807
GEN-2020-028 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3349 | 30.3907 | 0.0558
GEN-2020-028 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.1295 | 23.1965 | 0.067
GEN-2020-028 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.8512 | 30.0304 | 0.1792
GEN-2020-028 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.0238 | 33.2629 | 0.2391
GEN-2020-028 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.2414 | 35.4256 | 0.1842
GEN-2020-028 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9261 | 29.9659 | 0.0398
GEN-2020-028 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.8911 | 25.9917 | 0.1006
GEN-2020-028 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.7777 | 23.8584 | 0.0807
GEN-2020-028 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.608 | 23.762 | 0.154
GEN-2020-028 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.8705 | 12.9175 | 0.047
GEN-2020-028 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.9589 | 36.1193 | 0.1604
GEN-2020-028 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.7601 | 43.9561 | 0.196
GEN-2020-028 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8119 | 26.8986 | 0.0867
GEN-2020-028 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.8223 | 29.9627 | 0.1404
GEN-2020-028 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.2593 | 27.3637 | 0.1044
GEN-2020-028 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.9158 | 26.0705 | 0.1547
GEN-2020-028 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0199 | 33.0861 | 0.0662
GEN-2020-028 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.0592 | 28.1682 | 0.109
GEN-2020-028 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.187 | 34.4987 | 0.3117
GEN-2020-028 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.9316 | 50.3723 | 0.4407
GEN-2020-028 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.249 | 23.3507 | 0.1017
GEN-2020-028 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 39.6638 | 40.0447 | 0.3809
GEN-2020-028 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 41.7419 | 42.4281 | 0.6862
GEN-2020-028 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.934 | 28.0853 | 0.1513
GEN-2020-028 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 39.6455 | 40.3571 | 0.7116
GEN-2020-028 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.3043 | 23.5233 | 0.219
GEN-2020-028 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.1341 | 43.8416 | 0.7075
GEN-2020-028 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 40.2133 | 40.9548 | 0.7415
GEN-2020-028 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-028 | 02 NEBRASKA | 647014 | S914A 8 | 69 | 11.7243 | 11.736 | 0.0117
GEN-2020-028 | 02 NEBRASKA | 647079 | 979TP 8 | 69 | 7.0336 | 7.0384 | 0.0048
GEN-2020-028 | 02 NEBRASKA | 647100 | ASH GRV8 | 69 | 6.9498 | 6.9533 | 0.0035
GEN-2020-028 | 02 NEBRASKA | 647846 | S6846 8 | 69 | 8.0524 | 8.0559 | 0.0035
GEN-2020-028 | 02 NEBRASKA | 647900 | S900 8 | 69 | 8.1005 | 8.1053 | 0.0048
GEN-2020-028 | 02 NEBRASKA | 647914 | S914 8 | 69 | 7.9068 | 7.9119 | 0.0051
GEN-2020-028 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.4958 | 26.5228 | 0.027
GEN-2020-028 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4793 | 7.4855 | 0.0062
GEN-2020-028 | 02 NEBRASKA | 647979 | S979 8 | 69 | 6.8839 | 6.8885 | 0.0046
GEN-2020-028 | 02 NEBRASKA | 647988 | S988 8 | 69 | 2.9093 | 2.91 | 0.0007
GEN-2020-028 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7926 | 17.8049 | 0.0123
GEN-2020-028 | 02 NEBRASKA | 650169 | 70&BLUFF 5 | 161 | 8.9249 | 8.935 | 0.0101
GEN-2020-028 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3733 | 21.4023 | 0.029
GEN-2020-028 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2788 | 21.3009 | 0.0221
GEN-2020-028 | 02 NEBRASKA | 650269 | 70&BLUFF 7 | 115 | 25.6973 | 25.7129 | 0.0156
GEN-2020-028 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3574 | 32.3776 | 0.0202
GEN-2020-028 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1007 | 22.1619 | 0.0612
GEN-2020-028 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7277 | 22.8013 | 0.0736
GEN-2020-028 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.061 | 17.0842 | 0.0232
GEN-2020-028 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0187 | 17.0417 | 0.023
GEN-2020-028 | 02 NEBRASKA | 764570 | GEN-2020-002 | 69 | 8.0524 | 8.0559 | 0.0035
GEN-2020-028 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-028 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-028 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 36.2308 | 37.2765 | 1.0457
GEN-2020-028 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.7777 | 23.8584 | 0.0807
GEN-2020-031 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.328 | 30.3907 | 0.0627
GEN-2020-031 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.1212 | 23.1965 | 0.0753
GEN-2020-031 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.8292 | 30.0304 | 0.2012
GEN-2020-031 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.9943 | 33.2629 | 0.2686
GEN-2020-031 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.2187 | 35.4256 | 0.2069
GEN-2020-031 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9212 | 29.9659 | 0.0447
GEN-2020-031 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.8786 | 25.9917 | 0.1131
GEN-2020-031 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.7677 | 23.8584 | 0.0907
GEN-2020-031 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.589 | 23.762 | 0.173
GEN-2020-031 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.8647 | 12.9175 | 0.0528
GEN-2020-031 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 35.939 | 36.1193 | 0.1803
GEN-2020-031 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.7359 | 43.9561 | 0.2202
GEN-2020-031 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8012 | 26.8986 | 0.0974
GEN-2020-031 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.8049 | 29.9627 | 0.1578
GEN-2020-031 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.2464 | 27.3637 | 0.1173
GEN-2020-031 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 25.8968 | 26.0705 | 0.1737
GEN-2020-031 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0117 | 33.0861 | 0.0744
GEN-2020-031 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.0457 | 28.1682 | 0.1225
GEN-2020-031 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.1487 | 34.4987 | 0.35
GEN-2020-031 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 49.8774 | 50.3723 | 0.4949
GEN-2020-031 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.2364 | 23.3507 | 0.1143
GEN-2020-031 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 39.617 | 40.0447 | 0.4277
GEN-2020-031 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 41.6583 | 42.4281 | 0.7698
GEN-2020-031 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 27.9153 | 28.0853 | 0.17
GEN-2020-031 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 39.5589 | 40.3571 | 0.7982
GEN-2020-031 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.2775 | 23.5233 | 0.2458
GEN-2020-031 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.0479 | 43.8416 | 0.7937
GEN-2020-031 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 40.1231 | 40.9548 | 0.8317
GEN-2020-031 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 36.1052 | 37.2765 | 1.1713
GEN-2020-031 | 02 NEBRASKA | 647014 | S914A 8 | 69 | 11.7229 | 11.736 | 0.0131
GEN-2020-031 | 02 NEBRASKA | 647079 | 979TP 8 | 69 | 7.033 | 7.0384 | 0.0054
GEN-2020-031 | 02 NEBRASKA | 647100 | ASH GRV8 | 69 | 6.9494 | 6.9533 | 0.0039
GEN-2020-031 | 02 NEBRASKA | 647846 | S6846 8 | 69 | 8.052 | 8.0559 | 0.0039
GEN-2020-031 | 02 NEBRASKA | 647900 | S900 8 | 69 | 8.1 | 8.1053 | 0.0053
GEN-2020-031 | 02 NEBRASKA | 647914 | S914 8 | 69 | 7.9062 | 7.9119 | 0.0057
GEN-2020-031 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.4924 | 26.5228 | 0.0304
GEN-2020-031 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4785 | 7.4855 | 0.007
GEN-2020-031 | 02 NEBRASKA | 647979 | S979 8 | 69 | 6.8834 | 6.8885 | 0.0051
GEN-2020-031 | 02 NEBRASKA | 647988 | S988 8 | 69 | 2.9092 | 2.91 | 0.0008
GEN-2020-031 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7911 | 17.8049 | 0.0138
GEN-2020-031 | 02 NEBRASKA | 650169 | 70&BLUFF 5 | 161 | 8.9236 | 8.935 | 0.0114
GEN-2020-031 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3697 | 21.4023 | 0.0326
GEN-2020-031 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.276 | 21.3009 | 0.0249
GEN-2020-031 | 02 NEBRASKA | 650269 | 70&BLUFF 7 | 115 | 25.6954 | 25.7129 | 0.0175
GEN-2020-031 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3549 | 32.3776 | 0.0227
GEN-2020-031 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.0932 | 22.1619 | 0.0687
GEN-2020-031 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7186 | 22.8013 | 0.0827
GEN-2020-031 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0582 | 17.0842 | 0.026
GEN-2020-031 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0159 | 17.0417 | 0.0258
GEN-2020-031 | 02 NEBRASKA | 764570 | GEN-2020-002 | 69 | 8.052 | 8.0559 | 0.0039
GEN-2020-031 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 36.1052 | 37.2765 | 1.1713
GEN-2020-031 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 36.1052 | 37.2765 | 1.1713
GEN-2020-031 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 36.1052 | 37.2765 | 1.1713
GEN-2020-031 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.7677 | 23.8584 | 0.0907
GEN-2020-038 | 02 NEBRASKA | 85831 | J583 | 345 | 6.0597 | 6.0607 | 0.001
GEN-2020-038 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 12.2543 | 12.2547 | 0.0004
GEN-2020-038 | 02 NEBRASKA | 87487 | J748POI | 345 | 13.4254 | 13.4259 | 0.0005
GEN-2020-038 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.6295 | 12.6313 | 0.0018
GEN-2020-038 | 02 NEBRASKA | 300076 | 5FAIRPTB2 | 161 | 16.7058 | 16.7067 | 0.0009
GEN-2020-038 | 02 NEBRASKA | 301347 | 5WINSLOW | 161 | 8.8921 | 8.8923 | 0.0002
GEN-2020-038 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.7231 | 16.724 | 0.0009
GEN-2020-038 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.6246 | 18.6256 | 0.001
GEN-2020-038 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 7.811 | 7.8137 | 0.0027
GEN-2020-038 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.0225 | 20.0254 | 0.0029
GEN-2020-038 | 02 NEBRASKA | 541201 | SIBLEY 7 | 345 | 21.1067 | 21.1077 | 0.001
GEN-2020-038 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.8734 | 20.8746 | 0.0012
GEN-2020-038 | 02 NEBRASKA | 541257 | COOK 5 | 161 | 14.5709 | 14.5715 | 0.0006
GEN-2020-038 | 02 NEBRASKA | 541258 | WOODBIN5 | 161 | 17.5331 | 17.534 | 0.0009
GEN-2020-038 | 02 NEBRASKA | 541394 | AVENUECTY 5 | 161 | 9.925 | 9.9252 | 0.0002
GEN-2020-038 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.5748 | 18.5767 | 0.0019
GEN-2020-038 | 02 NEBRASKA | 541401 | EASTOWN5 | 161 | 17.8706 | 17.8715 | 0.0009
GEN-2020-038 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 7.4792 | 7.4816 | 0.0024
GEN-2020-038 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 7.4792 | 7.4816 | 0.0024
GEN-2020-038 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 7.4792 | 7.4816 | 0.0024
GEN-2020-038 | 02 NEBRASKA | 541414 | SIB REA1 | 345 | 18.8485 | 18.8493 | 0.0008
GEN-2020-038 | 02 NEBRASKA | 541500 | KETCHEM7 | 345 | 7.8162 | 7.8175 | 0.0013
GEN-2020-038 | 02 NEBRASKA | 541501 | OSBORN7 | 345 | 6.9756 | 6.9767 | 0.0011
GEN-2020-038 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9033 | 8.9079 | 0.0046
GEN-2020-038 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9413 | 6.9439 | 0.0026
GEN-2020-038 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8582 | 8.8628 | 0.0046
GEN-2020-038 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7463 | 5.748 | 0.0017
GEN-2020-038 | 02 NEBRASKA | 542980 | NASHUA 7 | 345 | 22.8022 | 22.8033 | 0.0011
GEN-2020-038 | 02 NEBRASKA | 542982 | IATAN 7 | 345 | 29.7968 | 29.798 | 0.0012
GEN-2020-038 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.4025 | 43.4262 | 0.0237
GEN-2020-038 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.1824 | 19.1868 | 0.0044
GEN-2020-038 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.3431 | 12.348 | 0.0049
GEN-2020-038 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 31.9738 | 32.0776 | 0.1038
GEN-2020-038 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6473 | 39.7193 | 0.072
GEN-2020-038 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.2256 | 25.2374 | 0.0118
GEN-2020-038 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 21.9889 | 22.0114 | 0.0225
GEN-2020-038 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.0992 | 29.1834 | 0.0842
GEN-2020-038 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3184 | 27.3913 | 0.0729
GEN-2020-038 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.4699 | 31.5131 | 0.0432
GEN-2020-038 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.0647 | 29.1487 | 0.084
GEN-2020-038 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.392 | 17.4024 | 0.0104
GEN-2020-038 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.593 | 16.6021 | 0.0091
GEN-2020-038 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.1401 | 36.1993 | 0.0592
GEN-2020-038 | 02 NEBRASKA | 635100 | RLHILLS3 | 345 | 13.0795 | 13.0852 | 0.0057
GEN-2020-038 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.3418 | 27.3485 | 0.0067
GEN-2020-038 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0721 | 28.0756 | 0.0035
GEN-2020-038 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.0883 | 10.0889 | 0.0006
GEN-2020-038 | 02 NEBRASKA | 635570 | ORIENT 3 | 345 | 17.3839 | 17.39 | 0.0061
GEN-2020-038 | 02 NEBRASKA | 635589 | ECLIPSE3 | 345 | 9.0565 | 9.0588 | 0.0023
GEN-2020-038 | 02 NEBRASKA | 635590 | FALLOW 3 | 345 | 10.9902 | 10.9936 | 0.0034
GEN-2020-038 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.5097 | 16.5188 | 0.0091
GEN-2020-038 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 11.0163 | 11.0187 | 0.0024
GEN-2020-038 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5335 | 23.5362 | 0.0027
GEN-2020-038 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.9373 | 26.9666 | 0.0293
GEN-2020-038 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1264 | 18.1324 | 0.006
GEN-2020-038 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6822 | 4.6824 | 0.0002
GEN-2020-038 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 2.0145 | 2.0146 | 0.0001
GEN-2020-038 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0149 | 7.0155 | 0.0006
GEN-2020-038 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 16.4132 | 16.4151 | 0.0019
GEN-2020-038 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.8326 | 7.8333 | 0.0007
GEN-2020-038 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.5716 | 11.5745 | 0.0029
GEN-2020-038 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.799 | 23.8276 | 0.0286
GEN-2020-038 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.4613 | 44.4852 | 0.0239
GEN-2020-038 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.8011 | 11.8032 | 0.0021
GEN-2020-038 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.4972 | 11.4993 | 0.0021
GEN-2020-038 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7799 | 4.78 | 0.0001
GEN-2020-038 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.3431 | 12.348 | 0.0049
GEN-2020-038 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 13.6648 | 13.666 | 0.0012
GEN-2020-038 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 10.6634 | 10.6641 | 0.0007
GEN-2020-038 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.275 | 23.3021 | 0.0271
GEN-2020-038 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.4025 | 43.4262 | 0.0237
GEN-2020-038 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 10.0837 | 10.0843 | 0.0006
GEN-2020-038 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 13.3292 | 13.3304 | 0.0012
GEN-2020-038 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3324 | 30.3907 | 0.0583
GEN-2020-038 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.117 | 23.1965 | 0.0795
GEN-2020-038 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.748 | 30.0304 | 0.2824
GEN-2020-038 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 32.9423 | 33.2629 | 0.3206
GEN-2020-038 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.1962 | 35.4256 | 0.2294
GEN-2020-038 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.8421 | 29.9659 | 0.1238
GEN-2020-038 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.882 | 25.9917 | 0.1097
GEN-2020-038 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.3116 | 23.8584 | 0.5468
GEN-2020-038 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.6059 | 23.762 | 0.1561
GEN-2020-038 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.8843 | 31.939 | 0.0547
GEN-2020-038 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.5283 | 44.6473 | 0.119
GEN-2020-038 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.941 | 48.0983 | 0.1573
GEN-2020-038 | 02 NEBRASKA | 646214 | S1214 5 | 161 | 12.9065 | 12.9175 | 0.011
GEN-2020-038 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7325 | 30.7909 | 0.0584
GEN-2020-038 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.4833 | 33.5535 | 0.0702
GEN-2020-038 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.7419 | 28.7855 | 0.0436
GEN-2020-038 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.0135 | 36.1193 | 0.1058
GEN-2020-038 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.5305 | 25.5677 | 0.0372
GEN-2020-038 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9259 | 32.9992 | 0.0733
GEN-2020-038 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 28.8456 | 28.8915 | 0.0459
GEN-2020-038 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.815 | 43.9561 | 0.1411
GEN-2020-038 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8483 | 26.8986 | 0.0503
GEN-2020-038 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.8796 | 29.9627 | 0.0831
GEN-2020-038 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.2998 | 27.3637 | 0.0639
GEN-2020-038 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6391 | 34.7331 | 0.094
GEN-2020-038 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.1849 | 22.2128 | 0.0279
GEN-2020-038 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 26.0063 | 26.0705 | 0.0642
GEN-2020-038 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.486 | 35.5565 | 0.0705
GEN-2020-038 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.017 | 33.0861 | 0.0691
GEN-2020-038 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.1052 | 28.1682 | 0.063
GEN-2020-038 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.3802 | 34.4987 | 0.1185
GEN-2020-038 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.1192 | 50.3723 | 0.2531
GEN-2020-038 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3027 | 23.3507 | 0.048
GEN-2020-038 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 39.8994 | 40.0447 | 0.1453
GEN-2020-038 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 42.2704 | 42.4281 | 0.1577
GEN-2020-038 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.4585 | 8.4599 | 0.0014
GEN-2020-038 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 28.0199 | 28.0853 | 0.0654
GEN-2020-038 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.4448 | 10.4466 | 0.0018
GEN-2020-038 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 40.2186 | 40.3571 | 0.1385
GEN-2020-038 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.6077 | 26.6452 | 0.0375
GEN-2020-038 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.4791 | 23.5233 | 0.0442
GEN-2020-038 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1759 | 19.1979 | 0.022
GEN-2020-038 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 30.1033 | 30.1595 | 0.0562
GEN-2020-038 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.6057 | 28.6567 | 0.051
GEN-2020-038 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.8253 | 27.8737 | 0.0484
GEN-2020-038 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.7669 | 33.8402 | 0.0733
GEN-2020-038 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.6684 | 43.8416 | 0.1732
GEN-2020-038 | 02 NEBRASKA | 646362 | S1362 5 | 161 | 40.8112 | 40.9548 | 0.1436
GEN-2020-038 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 37.174 | 37.2765 | 0.1025
GEN-2020-038 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.3779 | 16.3924 | 0.0145
GEN-2020-038 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2172 | 32.241 | 0.0238
GEN-2020-038 | 02 NEBRASKA | 647015 | S6815T1&T2 8 | 69 | 12.0627 | 12.066 | 0.0033
GEN-2020-038 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.5313 | 17.538 | 0.0067
GEN-2020-038 | 02 NEBRASKA | 647017 | 6815TP98 | 69 | 12.649 | 12.6526 | 0.0036
GEN-2020-038 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.4282 | 11.431 | 0.0028
GEN-2020-038 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.6115 | 8.6132 | 0.0017
GEN-2020-038 | 02 NEBRASKA | 647901 | S901 8 | 69 | 26.3097 | 26.3216 | 0.0119
GEN-2020-038 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.7481 | 8.7497 | 0.0016
GEN-2020-038 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6493 | 32.6716 | 0.0223
GEN-2020-038 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1488 | 27.1676 | 0.0188
GEN-2020-038 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8176 | 23.8322 | 0.0146
GEN-2020-038 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5034 | 26.5228 | 0.0194
GEN-2020-038 | 02 NEBRASKA | 647924 | S924 8 | 69 | 24.3834 | 24.3955 | 0.0121
GEN-2020-038 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.2264 | 17.2336 | 0.0072
GEN-2020-038 | 02 NEBRASKA | 647938 | S938 8 | 69 | 21.7244 | 21.7349 | 0.0105
GEN-2020-038 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9308 | 20.9424 | 0.0116
GEN-2020-038 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.1919 | 16.1987 | 0.0068
GEN-2020-038 | 02 NEBRASKA | 647960 | S960 8 | 69 | 7.4838 | 7.4855 | 0.0017
GEN-2020-038 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.4879 | 9.4899 | 0.002
GEN-2020-038 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7855 | 17.8049 | 0.0194
GEN-2020-038 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3552 | 21.4023 | 0.0471
GEN-2020-038 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2615 | 21.3009 | 0.0394
GEN-2020-038 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.4822 | 21.4905 | 0.0083
GEN-2020-038 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.7354 | 25.7472 | 0.0118
GEN-2020-038 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.2047 | 22.2138 | 0.0091
GEN-2020-038 | 02 NEBRASKA | 650262 | 57&GARLAND7 | 115 | 25.5163 | 25.5293 | 0.013
GEN-2020-038 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.6218 | 29.6398 | 0.018
GEN-2020-038 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.5649 | 27.5796 | 0.0147
GEN-2020-038 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.241 | 25.2534 | 0.0124
GEN-2020-038 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 21.9769 | 21.9865 | 0.0096
GEN-2020-038 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.7359 | 22.7463 | 0.0104
GEN-2020-038 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 21.8561 | 21.8649 | 0.0088
GEN-2020-038 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.7818 | 21.7922 | 0.0104
GEN-2020-038 | 02 NEBRASKA | 650283 | WAVERLY 7 | 115 | 21.2551 | 21.2645 | 0.0094
GEN-2020-038 | 02 NEBRASKA | 650284 | 84FLETCHER7 | 115 | 25.0523 | 25.0647 | 0.0124
GEN-2020-038 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3528 | 32.3776 | 0.0248
GEN-2020-038 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.7336 | 25.7446 | 0.011
GEN-2020-038 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.8735 | 15.8749 | 0.0014
GEN-2020-038 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.021 | 8.0247 | 0.0037
GEN-2020-038 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 9.6061 | 9.6067 | 0.0006
GEN-2020-038 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 24.9538 | 24.9645 | 0.0107
GEN-2020-038 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.1187 | 10.1209 | 0.0022
GEN-2020-038 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 7.0037 | 7.0051 | 0.0014
GEN-2020-038 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.848 | 5.849 | 0.001
GEN-2020-038 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 7.5833 | 7.5835 | 0.0002
GEN-2020-038 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 16.5049 | 16.5059 | 0.001
GEN-2020-038 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.0894 | 22.1619 | 0.0725
GEN-2020-038 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.3021 | 22.8013 | 0.4992
GEN-2020-038 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0567 | 17.0842 | 0.0275
GEN-2020-038 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0145 | 17.0417 | 0.0272
GEN-2020-038 | 02 NEBRASKA | 763505 | GEN-2019-009 | 161 | 8.1523 | 8.1535 | 0.0012
GEN-2020-038 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 43.2954 | 43.3189 | 0.0235
GEN-2020-038 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 37.174 | 37.2765 | 0.1025
GEN-2020-038 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 37.174 | 37.2765 | 0.1025
GEN-2020-038 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 37.174 | 37.2765 | 0.1025
GEN-2020-038 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.3116 | 23.8584 | 0.5468
GEN-2020-038 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.7657 | 33.8389 | 0.0732
GEN-2020-038 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.7657 | 33.8389 | 0.0732
GEN-2020-038 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.7657 | 33.8389 | 0.0732
GEN-2020-038 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.915 | 11.93 | 0.015
GEN-2020-038 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7454 | 16.7756 | 0.0302
GEN-2020-043 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9076 | 8.9079 | 0.0003
GEN-2020-043 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9437 | 6.9439 | 0.0002
GEN-2020-043 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8625 | 8.8628 | 0.0003
GEN-2020-043 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7478 | 5.748 | 0.0002
GEN-2020-043 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.0528 | 32.0776 | 0.0248
GEN-2020-043 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6966 | 39.7193 | 0.0227
GEN-2020-043 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.5073 | 21.5181 | 0.0108
GEN-2020-043 | 02 NEBRASKA | 635004 | SUB701 8 | 69 | 22.3649 | 22.369 | 0.0041
GEN-2020-043 | 02 NEBRASKA | 635005 | SUB702 5 | 161 | 20.8691 | 20.8784 | 0.0093
GEN-2020-043 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.1632 | 29.1834 | 0.0202
GEN-2020-043 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3736 | 27.3913 | 0.0177
GEN-2020-043 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.1286 | 29.1487 | 0.0201
GEN-2020-043 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.3462 | 27.3485 | 0.0023
GEN-2020-043 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0742 | 28.0756 | 0.0014
GEN-2020-043 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.964 | 26.9666 | 0.0026
GEN-2020-043 | 02 NEBRASKA | 640300 | OAKLAND7 | 115 | 8.0293 | 8.0297 | 0.0004
GEN-2020-043 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3754 | 9.3769 | 0.0015
GEN-2020-043 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.648 | 8.6487 | 0.0007
GEN-2020-043 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3604 | 30.3907 | 0.0303
GEN-2020-043 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.169 | 23.1965 | 0.0275
GEN-2020-043 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.9976 | 30.0304 | 0.0328
GEN-2020-043 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.2188 | 33.2629 | 0.0441
GEN-2020-043 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.3759 | 35.4256 | 0.0497
GEN-2020-043 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9574 | 29.9659 | 0.0085
GEN-2020-043 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.9442 | 25.9917 | 0.0475
GEN-2020-043 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-043 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.7391 | 23.762 | 0.0229
GEN-2020-043 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.9072 | 31.939 | 0.0318
GEN-2020-043 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.6017 | 44.6473 | 0.0456
GEN-2020-043 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.9253 | 48.0983 | 0.173
GEN-2020-043 | 02 NEBRASKA | 646210 | S1210 5 | 161 | 28.1347 | 28.1614 | 0.0267
GEN-2020-043 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.1331 | 36.1772 | 0.0441
GEN-2020-043 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7603 | 30.7909 | 0.0306
GEN-2020-043 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.5123 | 33.5535 | 0.0412
GEN-2020-043 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.7593 | 28.7855 | 0.0262
GEN-2020-043 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.0613 | 36.1193 | 0.058
GEN-2020-043 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.5382 | 25.5677 | 0.0295
GEN-2020-043 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9498 | 32.9992 | 0.0494
GEN-2020-043 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.8479 | 43.9561 | 0.1082
GEN-2020-043 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8817 | 26.8986 | 0.0169
GEN-2020-043 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.9291 | 29.9627 | 0.0336
GEN-2020-043 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.3273 | 27.3637 | 0.0364
GEN-2020-043 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6585 | 34.7331 | 0.0746
GEN-2020-043 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.8926 | 24.9515 | 0.0589
GEN-2020-043 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 22.3236 | 22.3655 | 0.0419
GEN-2020-043 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.2022 | 22.2128 | 0.0106
GEN-2020-043 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.5011 | 35.5565 | 0.0554
GEN-2020-043 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0502 | 33.0861 | 0.0359
GEN-2020-043 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 30.3512 | 30.4729 | 0.1217
GEN-2020-043 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.1214 | 28.1682 | 0.0468
GEN-2020-043 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4695 | 34.4987 | 0.0292
GEN-2020-043 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.3023 | 50.3723 | 0.07
GEN-2020-043 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3276 | 23.3507 | 0.0231
GEN-2020-043 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 40.0055 | 40.0447 | 0.0392
GEN-2020-043 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1541 | 7.1557 | 0.0016
GEN-2020-043 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1839 | 19.1979 | 0.014
GEN-2020-043 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 30.1277 | 30.1595 | 0.0318
GEN-2020-043 | 02 NEBRASKA | 646299 | S1299 5 | 161 | 27.9945 | 28.0205 | 0.026
GEN-2020-043 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.6282 | 28.6567 | 0.0285
GEN-2020-043 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.847 | 27.8737 | 0.0267
GEN-2020-043 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.9824 | 23.0395 | 0.0571
GEN-2020-043 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.6112 | 33.8402 | 0.229
GEN-2020-043 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.8011 | 43.8416 | 0.0405
GEN-2020-043 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 22.0941 | 22.1285 | 0.0344
GEN-2020-043 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2301 | 32.241 | 0.0109
GEN-2020-043 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6892 | 14.6931 | 0.0039
GEN-2020-043 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.7111 | 12.7124 | 0.0013
GEN-2020-043 | 02 NEBRASKA | 647422 | FREM B 8 | 69 | 15.0001 | 15.0012 | 0.0011
GEN-2020-043 | 02 NEBRASKA | 647902 | S902 8 | 69 | 9.2042 | 9.2048 | 0.0006
GEN-2020-043 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6621 | 32.6716 | 0.0095
GEN-2020-043 | 02 NEBRASKA | 647907 | S907 8 | 69 | 18.016 | 18.021 | 0.005
GEN-2020-043 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1538 | 27.1676 | 0.0138
GEN-2020-043 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.2967 | 21.3033 | 0.0066
GEN-2020-043 | 02 NEBRASKA | 647913 | S913 8 | 69 | 16.1924 | 16.1959 | 0.0035
GEN-2020-043 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8237 | 23.8322 | 0.0085
GEN-2020-043 | 02 NEBRASKA | 647917 | S917 8 | 69 | 25.9954 | 26.0061 | 0.0107
GEN-2020-043 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.9867 | 22.9958 | 0.0091
GEN-2020-043 | 02 NEBRASKA | 647919 | S919 8 | 69 | 21.5605 | 21.5684 | 0.0079
GEN-2020-043 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5114 | 26.5228 | 0.0114
GEN-2020-043 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.23 | 17.2336 | 0.0036
GEN-2020-043 | 02 NEBRASKA | 647930 | S930 8 | 69 | 21.6086 | 21.6168 | 0.0082
GEN-2020-043 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1469 | 9.1477 | 0.0008
GEN-2020-043 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1752 | 20.1826 | 0.0074
GEN-2020-043 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9356 | 20.9424 | 0.0068
GEN-2020-043 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.1951 | 16.1987 | 0.0036
GEN-2020-043 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.3829 | 20.3901 | 0.0072
GEN-2020-043 | 02 NEBRASKA | 647983 | S983 8 | 69 | 7.6262 | 7.6266 | 0.0004
GEN-2020-043 | 02 NEBRASKA | 647984 | S984 8 | 69 | 7.9964 | 7.9968 | 0.0004
GEN-2020-043 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3972 | 21.4023 | 0.0051
GEN-2020-043 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.0245 | 8.0247 | 0.0002
GEN-2020-043 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-043 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-043 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1368 | 22.1619 | 0.0251
GEN-2020-043 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7876 | 22.8013 | 0.0137
GEN-2020-043 | 02 NEBRASKA | 762712 | G18-037-TAP | 161 | 35.508 | 35.5504 | 0.0424
GEN-2020-043 | 02 NEBRASKA | 762713 | GEN-2018-037 | 161 | 33.346 | 33.3833 | 0.0373
GEN-2020-043 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0747 | 17.0842 | 0.0095
GEN-2020-043 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0323 | 17.0417 | 0.0094
GEN-2020-043 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-043 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-043 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-043 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-043 | 02 NEBRASKA | 764765 | GEN-2020-078 | 161 | 16.3945 | 16.4101 | 0.0156
GEN-2020-043 | 02 NEBRASKA | 764775 | G20-078-TAP | 161 | 16.4295 | 16.4451 | 0.0156
GEN-2020-043 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.9288 | 11.93 | 0.0012
GEN-2020-043 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7731 | 16.7756 | 0.0025
GEN-2020-044 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9076 | 8.9079 | 0.0003
GEN-2020-044 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9437 | 6.9439 | 0.0002
GEN-2020-044 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8625 | 8.8628 | 0.0003
GEN-2020-044 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7478 | 5.748 | 0.0002
GEN-2020-044 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.0528 | 32.0776 | 0.0248
GEN-2020-044 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6966 | 39.7193 | 0.0227
GEN-2020-044 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.5073 | 21.5181 | 0.0108
GEN-2020-044 | 02 NEBRASKA | 635004 | SUB701 8 | 69 | 22.3649 | 22.369 | 0.0041
GEN-2020-044 | 02 NEBRASKA | 635005 | SUB702 5 | 161 | 20.8691 | 20.8784 | 0.0093
GEN-2020-044 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.1632 | 29.1834 | 0.0202
GEN-2020-044 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3736 | 27.3913 | 0.0177
GEN-2020-044 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.1286 | 29.1487 | 0.0201
GEN-2020-044 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.3462 | 27.3485 | 0.0023
GEN-2020-044 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0742 | 28.0756 | 0.0014
GEN-2020-044 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.964 | 26.9666 | 0.0026
GEN-2020-044 | 02 NEBRASKA | 640300 | OAKLAND7 | 115 | 8.0293 | 8.0297 | 0.0004
GEN-2020-044 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3754 | 9.3769 | 0.0015
GEN-2020-044 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.648 | 8.6487 | 0.0007
GEN-2020-044 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3604 | 30.3907 | 0.0303
GEN-2020-044 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.169 | 23.1965 | 0.0275
GEN-2020-044 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.9976 | 30.0304 | 0.0328
GEN-2020-044 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.2188 | 33.2629 | 0.0441
GEN-2020-044 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.3759 | 35.4256 | 0.0497
GEN-2020-044 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9574 | 29.9659 | 0.0085
GEN-2020-044 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.9442 | 25.9917 | 0.0475
GEN-2020-044 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-044 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.7391 | 23.762 | 0.0229
GEN-2020-044 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.9072 | 31.939 | 0.0318
GEN-2020-044 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.6017 | 44.6473 | 0.0456
GEN-2020-044 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.9253 | 48.0983 | 0.173
GEN-2020-044 | 02 NEBRASKA | 646210 | S1210 5 | 161 | 28.1347 | 28.1614 | 0.0267
GEN-2020-044 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.1331 | 36.1772 | 0.0441
GEN-2020-044 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7603 | 30.7909 | 0.0306
GEN-2020-044 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.5123 | 33.5535 | 0.0412
GEN-2020-044 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.7593 | 28.7855 | 0.0262
GEN-2020-044 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.0613 | 36.1193 | 0.058
GEN-2020-044 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.5382 | 25.5677 | 0.0295
GEN-2020-044 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9498 | 32.9992 | 0.0494
GEN-2020-044 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.8479 | 43.9561 | 0.1082
GEN-2020-044 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8817 | 26.8986 | 0.0169
GEN-2020-044 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.9291 | 29.9627 | 0.0336
GEN-2020-044 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.3273 | 27.3637 | 0.0364
GEN-2020-044 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6585 | 34.7331 | 0.0746
GEN-2020-044 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.8926 | 24.9515 | 0.0589
GEN-2020-044 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 22.3236 | 22.3655 | 0.0419
GEN-2020-044 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.2022 | 22.2128 | 0.0106
GEN-2020-044 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.5011 | 35.5565 | 0.0554
GEN-2020-044 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0502 | 33.0861 | 0.0359
GEN-2020-044 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 30.3512 | 30.4729 | 0.1217
GEN-2020-044 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.1214 | 28.1682 | 0.0468
GEN-2020-044 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4695 | 34.4987 | 0.0292
GEN-2020-044 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.3023 | 50.3723 | 0.07
GEN-2020-044 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3276 | 23.3507 | 0.0231
GEN-2020-044 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 40.0055 | 40.0447 | 0.0392
GEN-2020-044 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1541 | 7.1557 | 0.0016
GEN-2020-044 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1839 | 19.1979 | 0.014
GEN-2020-044 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 30.1277 | 30.1595 | 0.0318
GEN-2020-044 | 02 NEBRASKA | 646299 | S1299 5 | 161 | 27.9945 | 28.0205 | 0.026
GEN-2020-044 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.6282 | 28.6567 | 0.0285
GEN-2020-044 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.847 | 27.8737 | 0.0267
GEN-2020-044 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.9824 | 23.0395 | 0.0571
GEN-2020-044 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.6112 | 33.8402 | 0.229
GEN-2020-044 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.8011 | 43.8416 | 0.0405
GEN-2020-044 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 22.0941 | 22.1285 | 0.0344
GEN-2020-044 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2301 | 32.241 | 0.0109
GEN-2020-044 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6892 | 14.6931 | 0.0039
GEN-2020-044 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.7111 | 12.7124 | 0.0013
GEN-2020-044 | 02 NEBRASKA | 647422 | FREM B 8 | 69 | 15.0001 | 15.0012 | 0.0011
GEN-2020-044 | 02 NEBRASKA | 647902 | S902 8 | 69 | 9.2042 | 9.2048 | 0.0006
GEN-2020-044 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6621 | 32.6716 | 0.0095
GEN-2020-044 | 02 NEBRASKA | 647907 | S907 8 | 69 | 18.016 | 18.021 | 0.005
GEN-2020-044 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1538 | 27.1676 | 0.0138
GEN-2020-044 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.2967 | 21.3033 | 0.0066
GEN-2020-044 | 02 NEBRASKA | 647913 | S913 8 | 69 | 16.1924 | 16.1959 | 0.0035
GEN-2020-044 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8237 | 23.8322 | 0.0085
GEN-2020-044 | 02 NEBRASKA | 647917 | S917 8 | 69 | 25.9954 | 26.0061 | 0.0107
GEN-2020-044 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.9867 | 22.9958 | 0.0091
GEN-2020-044 | 02 NEBRASKA | 647919 | S919 8 | 69 | 21.5605 | 21.5684 | 0.0079
GEN-2020-044 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5114 | 26.5228 | 0.0114
GEN-2020-044 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.23 | 17.2336 | 0.0036
GEN-2020-044 | 02 NEBRASKA | 647930 | S930 8 | 69 | 21.6086 | 21.6168 | 0.0082
GEN-2020-044 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1469 | 9.1477 | 0.0008
GEN-2020-044 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1752 | 20.1826 | 0.0074
GEN-2020-044 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9356 | 20.9424 | 0.0068
GEN-2020-044 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.1951 | 16.1987 | 0.0036
GEN-2020-044 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.3829 | 20.3901 | 0.0072
GEN-2020-044 | 02 NEBRASKA | 647983 | S983 8 | 69 | 7.6262 | 7.6266 | 0.0004
GEN-2020-044 | 02 NEBRASKA | 647984 | S984 8 | 69 | 7.9964 | 7.9968 | 0.0004
GEN-2020-044 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3972 | 21.4023 | 0.0051
GEN-2020-044 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.0245 | 8.0247 | 0.0002
GEN-2020-044 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-044 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-044 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1368 | 22.1619 | 0.0251
GEN-2020-044 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7876 | 22.8013 | 0.0137
GEN-2020-044 | 02 NEBRASKA | 762712 | G18-037-TAP | 161 | 35.508 | 35.5504 | 0.0424
GEN-2020-044 | 02 NEBRASKA | 762713 | GEN-2018-037 | 161 | 33.346 | 33.3833 | 0.0373
GEN-2020-044 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0747 | 17.0842 | 0.0095
GEN-2020-044 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0323 | 17.0417 | 0.0094
GEN-2020-044 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-044 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-044 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-044 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-044 | 02 NEBRASKA | 764765 | GEN-2020-078 | 161 | 16.3945 | 16.4101 | 0.0156
GEN-2020-044 | 02 NEBRASKA | 764775 | G20-078-TAP | 161 | 16.4295 | 16.4451 | 0.0156
GEN-2020-044 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.9288 | 11.93 | 0.0012
GEN-2020-044 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7731 | 16.7756 | 0.0025
GEN-2020-045 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9076 | 8.9079 | 0.0003
GEN-2020-045 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9437 | 6.9439 | 0.0002
GEN-2020-045 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8625 | 8.8628 | 0.0003
GEN-2020-045 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7478 | 5.748 | 0.0002
GEN-2020-045 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.0528 | 32.0776 | 0.0248
GEN-2020-045 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6966 | 39.7193 | 0.0227
GEN-2020-045 | 02 NEBRASKA | 635003 | SUB701 5 | 161 | 21.5073 | 21.5181 | 0.0108
GEN-2020-045 | 02 NEBRASKA | 635004 | SUB701 8 | 69 | 22.3649 | 22.369 | 0.0041
GEN-2020-045 | 02 NEBRASKA | 635005 | SUB702 5 | 161 | 20.8691 | 20.8784 | 0.0093
GEN-2020-045 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.1632 | 29.1834 | 0.0202
GEN-2020-045 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3736 | 27.3913 | 0.0177
GEN-2020-045 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.1286 | 29.1487 | 0.0201
GEN-2020-045 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.3462 | 27.3485 | 0.0023
GEN-2020-045 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0742 | 28.0756 | 0.0014
GEN-2020-045 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.964 | 26.9666 | 0.0026
GEN-2020-045 | 02 NEBRASKA | 640300 | OAKLAND7 | 115 | 8.0293 | 8.0297 | 0.0004
GEN-2020-045 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3754 | 9.3769 | 0.0015
GEN-2020-045 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.648 | 8.6487 | 0.0007
GEN-2020-045 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3604 | 30.3907 | 0.0303
GEN-2020-045 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.169 | 23.1965 | 0.0275
GEN-2020-045 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.9976 | 30.0304 | 0.0328
GEN-2020-045 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.2188 | 33.2629 | 0.0441
GEN-2020-045 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.3759 | 35.4256 | 0.0497
GEN-2020-045 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.9574 | 29.9659 | 0.0085
GEN-2020-045 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.9442 | 25.9917 | 0.0475
GEN-2020-045 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-045 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.7391 | 23.762 | 0.0229
GEN-2020-045 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.9072 | 31.939 | 0.0318
GEN-2020-045 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.6017 | 44.6473 | 0.0456
GEN-2020-045 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.9253 | 48.0983 | 0.173
GEN-2020-045 | 02 NEBRASKA | 646210 | S1210 5 | 161 | 28.1347 | 28.1614 | 0.0267
GEN-2020-045 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.1331 | 36.1772 | 0.0441
GEN-2020-045 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7603 | 30.7909 | 0.0306
GEN-2020-045 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.5123 | 33.5535 | 0.0412
GEN-2020-045 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.7593 | 28.7855 | 0.0262
GEN-2020-045 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.0613 | 36.1193 | 0.058
GEN-2020-045 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.5382 | 25.5677 | 0.0295
GEN-2020-045 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9498 | 32.9992 | 0.0494
GEN-2020-045 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.8479 | 43.9561 | 0.1082
GEN-2020-045 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8817 | 26.8986 | 0.0169
GEN-2020-045 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.9291 | 29.9627 | 0.0336
GEN-2020-045 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.3273 | 27.3637 | 0.0364
GEN-2020-045 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6585 | 34.7331 | 0.0746
GEN-2020-045 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.8926 | 24.9515 | 0.0589
GEN-2020-045 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 22.3236 | 22.3655 | 0.0419
GEN-2020-045 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.2022 | 22.2128 | 0.0106
GEN-2020-045 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.5011 | 35.5565 | 0.0554
GEN-2020-045 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0502 | 33.0861 | 0.0359
GEN-2020-045 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 30.3512 | 30.4729 | 0.1217
GEN-2020-045 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.1214 | 28.1682 | 0.0468
GEN-2020-045 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4695 | 34.4987 | 0.0292
GEN-2020-045 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.3023 | 50.3723 | 0.07
GEN-2020-045 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3276 | 23.3507 | 0.0231
GEN-2020-045 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 40.0055 | 40.0447 | 0.0392
GEN-2020-045 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1541 | 7.1557 | 0.0016
GEN-2020-045 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1839 | 19.1979 | 0.014
GEN-2020-045 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 30.1277 | 30.1595 | 0.0318
GEN-2020-045 | 02 NEBRASKA | 646299 | S1299 5 | 161 | 27.9945 | 28.0205 | 0.026
GEN-2020-045 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.6282 | 28.6567 | 0.0285
GEN-2020-045 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.847 | 27.8737 | 0.0267
GEN-2020-045 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.9824 | 23.0395 | 0.0571
GEN-2020-045 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.6112 | 33.8402 | 0.229
GEN-2020-045 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.8011 | 43.8416 | 0.0405
GEN-2020-045 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 22.0941 | 22.1285 | 0.0344
GEN-2020-045 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2301 | 32.241 | 0.0109
GEN-2020-045 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6892 | 14.6931 | 0.0039
GEN-2020-045 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.7111 | 12.7124 | 0.0013
GEN-2020-045 | 02 NEBRASKA | 647422 | FREM B 8 | 69 | 15.0001 | 15.0012 | 0.0011
GEN-2020-045 | 02 NEBRASKA | 647902 | S902 8 | 69 | 9.2042 | 9.2048 | 0.0006
GEN-2020-045 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6621 | 32.6716 | 0.0095
GEN-2020-045 | 02 NEBRASKA | 647907 | S907 8 | 69 | 18.016 | 18.021 | 0.005
GEN-2020-045 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1538 | 27.1676 | 0.0138
GEN-2020-045 | 02 NEBRASKA | 647911 | S911 8 | 69 | 21.2967 | 21.3033 | 0.0066
GEN-2020-045 | 02 NEBRASKA | 647913 | S913 8 | 69 | 16.1924 | 16.1959 | 0.0035
GEN-2020-045 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8237 | 23.8322 | 0.0085
GEN-2020-045 | 02 NEBRASKA | 647917 | S917 8 | 69 | 25.9954 | 26.0061 | 0.0107
GEN-2020-045 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.9867 | 22.9958 | 0.0091
GEN-2020-045 | 02 NEBRASKA | 647919 | S919 8 | 69 | 21.5605 | 21.5684 | 0.0079
GEN-2020-045 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5114 | 26.5228 | 0.0114
GEN-2020-045 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.23 | 17.2336 | 0.0036
GEN-2020-045 | 02 NEBRASKA | 647930 | S930 8 | 69 | 21.6086 | 21.6168 | 0.0082
GEN-2020-045 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1469 | 9.1477 | 0.0008
GEN-2020-045 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1752 | 20.1826 | 0.0074
GEN-2020-045 | 02 NEBRASKA | 647940 | S940 8 | 69 | 20.9356 | 20.9424 | 0.0068
GEN-2020-045 | 02 NEBRASKA | 647942 | S942 8 | 69 | 16.1951 | 16.1987 | 0.0036
GEN-2020-045 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.3829 | 20.3901 | 0.0072
GEN-2020-045 | 02 NEBRASKA | 647983 | S983 8 | 69 | 7.6262 | 7.6266 | 0.0004
GEN-2020-045 | 02 NEBRASKA | 647984 | S984 8 | 69 | 7.9964 | 7.9968 | 0.0004
GEN-2020-045 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3972 | 21.4023 | 0.0051
GEN-2020-045 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.0245 | 8.0247 | 0.0002
GEN-2020-045 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-045 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7952 | 8.7964 | 0.0012
GEN-2020-045 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1368 | 22.1619 | 0.0251
GEN-2020-045 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7876 | 22.8013 | 0.0137
GEN-2020-045 | 02 NEBRASKA | 762712 | G18-037-TAP | 161 | 35.508 | 35.5504 | 0.0424
GEN-2020-045 | 02 NEBRASKA | 762713 | GEN-2018-037 | 161 | 33.346 | 33.3833 | 0.0373
GEN-2020-045 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0747 | 17.0842 | 0.0095
GEN-2020-045 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0323 | 17.0417 | 0.0094
GEN-2020-045 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.8433 | 23.8584 | 0.0151
GEN-2020-045 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-045 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-045 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.61 | 33.8389 | 0.2289
GEN-2020-045 | 02 NEBRASKA | 764765 | GEN-2020-078 | 161 | 16.3945 | 16.4101 | 0.0156
GEN-2020-045 | 02 NEBRASKA | 764775 | G20-078-TAP | 161 | 16.4295 | 16.4451 | 0.0156
GEN-2020-045 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.9288 | 11.93 | 0.0012
GEN-2020-045 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7731 | 16.7756 | 0.0025
GEN-2020-078 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.3417 | 27.3485 | 0.0068
GEN-2020-078 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0704 | 28.0756 | 0.0052
GEN-2020-078 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.2129 | 23.2163 | 0.0034
GEN-2020-078 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.551 | 26.5556 | 0.0046
GEN-2020-078 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1422 | 15.1434 | 0.0012
GEN-2020-078 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 25.8535 | 25.8578 | 0.0043
GEN-2020-078 | 02 NEBRASKA | 640070 | BANCRFT7 | 115 | 5.3283 | 5.329 | 0.0007
GEN-2020-078 | 02 NEBRASKA | 640300 | OAKLAND7 | 115 | 8.0273 | 8.0297 | 0.0024
GEN-2020-078 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.366 | 9.3769 | 0.0109
GEN-2020-078 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.6439 | 8.6487 | 0.0048
GEN-2020-078 | 02 NEBRASKA | 640400 | W.POINT7 | 115 | 5.267 | 5.2678 | 0.0008
GEN-2020-078 | 02 NEBRASKA | 640409 | WINSLOW7 | 115 | 5.7531 | 5.7542 | 0.0011
GEN-2020-078 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.2632 | 30.3907 | 0.1275
GEN-2020-078 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.1296 | 23.1965 | 0.0669
GEN-2020-078 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.9769 | 30.0304 | 0.0535
GEN-2020-078 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.9299 | 25.9917 | 0.0618
GEN-2020-078 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.9571 | 48.0983 | 0.1412
GEN-2020-078 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.3375 | 25.5677 | 0.2302
GEN-2020-078 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.842 | 43.9561 | 0.1141
GEN-2020-078 | 02 NEBRASKA | 646234 | S1234 5 | 161 | 27.3116 | 27.3637 | 0.0521
GEN-2020-078 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6245 | 34.7331 | 0.1086
GEN-2020-078 | 02 NEBRASKA | 646236 | S1236 5 | 161 | 24.8784 | 24.9515 | 0.0731
GEN-2020-078 | 02 NEBRASKA | 646237 | S1237 5 | 161 | 22.2085 | 22.3655 | 0.157
GEN-2020-078 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 26.0315 | 26.0705 | 0.039
GEN-2020-078 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.4933 | 35.5565 | 0.0632
GEN-2020-078 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.935 | 33.0861 | 0.1511
GEN-2020-078 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 30.3376 | 30.4729 | 0.1353
GEN-2020-078 | 02 NEBRASKA | 646253 | S1253 5 | 161 | 28.0722 | 28.1682 | 0.096
GEN-2020-078 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3061 | 23.3507 | 0.0446
GEN-2020-078 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1436 | 7.1557 | 0.0121
GEN-2020-078 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1642 | 19.1979 | 0.0337
GEN-2020-078 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 30.0028 | 30.1595 | 0.1567
GEN-2020-078 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.5197 | 28.6567 | 0.137
GEN-2020-078 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.7488 | 27.8737 | 0.1249
GEN-2020-078 | 02 NEBRASKA | 646345 | S1345 5 | 161 | 22.9242 | 23.0395 | 0.1153
GEN-2020-078 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.7328 | 33.8402 | 0.1074
GEN-2020-078 | 02 NEBRASKA | 646367 | S1367 5 | 161 | 22.0296 | 22.1285 | 0.0989
GEN-2020-078 | 02 NEBRASKA | 647291 | S991 E 8 | 69 | 12.7041 | 12.7124 | 0.0083
GEN-2020-078 | 02 NEBRASKA | 647421 | FREM A 8 | 69 | 14.6858 | 14.6906 | 0.0048
GEN-2020-078 | 02 NEBRASKA | 647422 | FREM B 8 | 69 | 14.9952 | 15.0012 | 0.006
GEN-2020-078 | 02 NEBRASKA | 647423 | FREM C 8 | 69 | 12.8317 | 12.8358 | 0.0041
GEN-2020-078 | 02 NEBRASKA | 647424 | FREM D 8 | 69 | 13.2477 | 13.2519 | 0.0042
GEN-2020-078 | 02 NEBRASKA | 647427 | FREM G 8 | 69 | 14.4205 | 14.4251 | 0.0046
GEN-2020-078 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1532 | 27.1676 | 0.0144
GEN-2020-078 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7881 | 8.7964 | 0.0083
GEN-2020-078 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7881 | 8.7964 | 0.0083
GEN-2020-078 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1008 | 22.1619 | 0.0611
GEN-2020-078 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0608 | 17.0842 | 0.0234
GEN-2020-078 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0185 | 17.0417 | 0.0232
GEN-2020-078 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.7315 | 33.8389 | 0.1074
GEN-2020-078 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.7315 | 33.8389 | 0.1074
GEN-2020-078 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.7315 | 33.8389 | 0.1074
GEN-2020-078 | 02 NEBRASKA | 764765 | GEN-2020-078 | 161 | 16.043 | 16.4101 | 0.3671
GEN-2020-078 | 02 NEBRASKA | 764775 | G20-078-TAP | 161 | 16.078 | 16.4451 | 0.3671
GEN-2020-084 | 02 NEBRASKA | 45816 | J1581 SUB | 345 | 12.3795 | 12.3802 | 0.0007
GEN-2020-084 | 02 NEBRASKA | 87486 | J748GENTIE | 345 | 12.2496 | 12.2547 | 0.0051
GEN-2020-084 | 02 NEBRASKA | 87487 | J748POI | 345 | 13.4197 | 13.4259 | 0.0062
GEN-2020-084 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9067 | 8.9079 | 0.0012
GEN-2020-084 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9432 | 6.9439 | 0.0007
GEN-2020-084 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8616 | 8.8628 | 0.0012
GEN-2020-084 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7475 | 5.748 | 0.0005
GEN-2020-084 | 02 NEBRASKA | 601006 | SPLT RK3 | 345 | 15.4368 | 15.4387 | 0.0019
GEN-2020-084 | 02 NEBRASKA | 601034 | NOBLES 3 | 345 | 12.3795 | 12.3802 | 0.0007
GEN-2020-084 | 02 NEBRASKA | 603016 | SPLT RK7 | 115 | 40.4533 | 40.4564 | 0.0031
GEN-2020-084 | 02 NEBRASKA | 603149 | ANSON4 | 115 | 38.237 | 38.2399 | 0.0029
GEN-2020-084 | 02 NEBRASKA | 603200 | ANSON 7 | 115 | 36.6154 | 36.6179 | 0.0025
GEN-2020-084 | 02 NEBRASKA | 603228 | SPLITRK CAP7 | 115 | 39.8185 | 39.8216 | 0.0031
GEN-2020-084 | 02 NEBRASKA | 603264 | PROSE WIND7 | 115 | 5.1091 | 5.1092 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 603265 | PROSE CAP7 | 115 | 38.2977 | 38.3005 | 0.0028
GEN-2020-084 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.0012 | 32.0776 | 0.0764
GEN-2020-084 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6604 | 39.7193 | 0.0589
GEN-2020-084 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.1214 | 29.1834 | 0.062
GEN-2020-084 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3373 | 27.3913 | 0.054
GEN-2020-084 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.0869 | 29.1487 | 0.0618
GEN-2020-084 | 02 NEBRASKA | 635200 | RAUN 3 | 345 | 27.2573 | 27.3485 | 0.0912
GEN-2020-084 | 02 NEBRASKA | 635201 | RAUN 5 | 161 | 28.0391 | 28.0756 | 0.0365
GEN-2020-084 | 02 NEBRASKA | 635202 | NEAL S 5 | 161 | 23.1925 | 23.2163 | 0.0238
GEN-2020-084 | 02 NEBRASKA | 635203 | NEAL N 5 | 161 | 26.5231 | 26.5556 | 0.0325
GEN-2020-084 | 02 NEBRASKA | 635204 | NEAL N 8 | 69 | 10.2344 | 10.2364 | 0.002
GEN-2020-084 | 02 NEBRASKA | 635206 | IDA CO 3 | 345 | 9.7239 | 9.7285 | 0.0046
GEN-2020-084 | 02 NEBRASKA | 635219 | GARD AVE 3 | 345 | 9.3718 | 9.3755 | 0.0037
GEN-2020-084 | 02 NEBRASKA | 635220 | INTCHG 5 | 161 | 15.1342 | 15.1434 | 0.0092
GEN-2020-084 | 02 NEBRASKA | 635221 | KELLOGG5 | 161 | 17.8134 | 17.8254 | 0.012
GEN-2020-084 | 02 NEBRASKA | 635222 | KELLOGG8 | 69 | 18.4971 | 18.5023 | 0.0052
GEN-2020-084 | 02 NEBRASKA | 635225 | MORNSD 5 | 161 | 11.3186 | 11.3228 | 0.0042
GEN-2020-084 | 02 NEBRASKA | 635226 | LEEDS 5 | 161 | 16.4921 | 16.5012 | 0.0091
GEN-2020-084 | 02 NEBRASKA | 635227 | SBRIDGE T8 | 69 | 8.9379 | 8.9394 | 0.0015
GEN-2020-084 | 02 NEBRASKA | 635229 | AIRPORT 5 | 161 | 17.6719 | 17.6851 | 0.0132
GEN-2020-084 | 02 NEBRASKA | 635230 | LIBERTY5 | 161 | 25.8272 | 25.8578 | 0.0306
GEN-2020-084 | 02 NEBRASKA | 635235 | SALIX 5 | 161 | 15.2241 | 15.2334 | 0.0093
GEN-2020-084 | 02 NEBRASKA | 635236 | SALIX 8 | 69 | 13.8483 | 13.8513 | 0.003
GEN-2020-084 | 02 NEBRASKA | 635237 | SLOAN 8 | 69 | 4.9042 | 4.9046 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 635252 | J412 POI 3 | 345 | 10.0831 | 10.0889 | 0.0058
GEN-2020-084 | 02 NEBRASKA | 635300 | MONONA 5 | 161 | 5.7219 | 5.7226 | 0.0007
GEN-2020-084 | 02 NEBRASKA | 635301 | MONONA 8 | 69 | 4.7309 | 4.7311 | 0.0002
GEN-2020-084 | 02 NEBRASKA | 635302 | MAPLTN 8 | 69 | 3.1859 | 3.186 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 635303 | SMITHLD8 | 69 | 2.4747 | 2.4748 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 635330 | CRWFRD 5 | 161 | 5.128 | 5.1284 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 635368 | OBRIEN 3 | 345 | 14.5709 | 14.5735 | 0.0026
GEN-2020-084 | 02 NEBRASKA | 635399 | CHEROKEE 3 | 345 | 13.3818 | 13.3874 | 0.0056
GEN-2020-084 | 02 NEBRASKA | 635400 | HIGHLND 3 | 345 | 13.5713 | 13.5747 | 0.0034
GEN-2020-084 | 02 NEBRASKA | 636010 | LEHIGH 3 | 345 | 13.2876 | 13.2897 | 0.0021
GEN-2020-084 | 02 NEBRASKA | 637009 | GLACIAL EDGE | 345 | 13.2023 | 13.2077 | 0.0054
GEN-2020-084 | 02 NEBRASKA | 637024 | RICHLAND W | 345 | 9.3032 | 9.3069 | 0.0037
GEN-2020-084 | 02 NEBRASKA | 640072 | BATTLCR7 | 115 | 8.1227 | 8.1231 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 640073 | BATTLCR8 | 69 | 4.1582 | 4.1583 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 640080 | BELDEN 7 | 115 | 6.3328 | 6.3331 | 0.0003
GEN-2020-084 | 02 NEBRASKA | 640081 | BELDEN 8 | 69 | 3.8987 | 3.8988 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 11.0161 | 11.0187 | 0.0026
GEN-2020-084 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.9571 | 26.9666 | 0.0095
GEN-2020-084 | 02 NEBRASKA | 640212 | HARTGTN7 | 115 | 5.4829 | 5.4831 | 0.0002
GEN-2020-084 | 02 NEBRASKA | 640213 | HARTGTN8 | 69 | 3.6849 | 3.6849 | 0
GEN-2020-084 | 02 NEBRASKA | 640226 | HOSKINS3 | 345 | 16.4085 | 16.4151 | 0.0066
GEN-2020-084 | 02 NEBRASKA | 640227 | HOSKINS4 | 230 | 14.3757 | 14.3791 | 0.0034
GEN-2020-084 | 02 NEBRASKA | 640228 | HOSKINS7 | 115 | 20.4323 | 20.4357 | 0.0034
GEN-2020-084 | 02 NEBRASKA | 640263 | MADISON7 | 115 | 6.5662 | 6.5665 | 0.0003
GEN-2020-084 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.8146 | 23.8276 | 0.013
GEN-2020-084 | 02 NEBRASKA | 640296 | NORFK.N7 | 115 | 14.6364 | 14.6381 | 0.0017
GEN-2020-084 | 02 NEBRASKA | 640298 | NORFOLK7 | 115 | 13.6324 | 13.6338 | 0.0014
GEN-2020-084 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.4965 | 11.4993 | 0.0028
GEN-2020-084 | 02 NEBRASKA | 640343 | SHELCRK4 | 230 | 11.5468 | 11.5483 | 0.0015
GEN-2020-084 | 02 NEBRASKA | 640357 | STANTON7 | 115 | 5.4427 | 5.4431 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 640363 | STNTN.N7 | 115 | 7.4894 | 7.49 | 0.0006
GEN-2020-084 | 02 NEBRASKA | 640377 | TEKAMAH5 | 161 | 9.3695 | 9.3769 | 0.0074
GEN-2020-084 | 02 NEBRASKA | 640378 | TEKAMAH7 | 115 | 8.6452 | 8.6487 | 0.0035
GEN-2020-084 | 02 NEBRASKA | 640386 | TWIN CH4 | 230 | 9.5128 | 9.515 | 0.0022
GEN-2020-084 | 02 NEBRASKA | 640387 | TWIN CH7 | 115 | 11.4266 | 11.4282 | 0.0016
GEN-2020-084 | 02 NEBRASKA | 640388 | TWIN CH8 | 69 | 8.2062 | 8.2067 | 0.0005
GEN-2020-084 | 02 NEBRASKA | 640424 | S.SIOUXCITY7 | 115 | 7.7882 | 7.7889 | 0.0007
GEN-2020-084 | 02 NEBRASKA | 640425 | S.SIOUXCITY8 | 69 | 4.7328 | 4.7329 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 640520 | ANTELOPE 3 | 345 | 12.2795 | 12.2812 | 0.0017
GEN-2020-084 | 02 NEBRASKA | 640560 | WAKEFIELD 4 | 230 | 8.7819 | 8.7832 | 0.0013
GEN-2020-084 | 02 NEBRASKA | 640561 | RTLSNAKE.W 4 | 230 | 7.7663 | 7.7672 | 0.0009
GEN-2020-084 | 02 NEBRASKA | 640588 | TURTLE.CRK 3 | 345 | 13.6617 | 13.666 | 0.0043
GEN-2020-084 | 02 NEBRASKA | 640589 | SHOLES.W 3 | 345 | 10.6616 | 10.6641 | 0.0025
GEN-2020-084 | 02 NEBRASKA | 640598 | HAYSTACK.WD3 | 345 | 10.0821 | 10.0843 | 0.0022
GEN-2020-084 | 02 NEBRASKA | 643271 | PLUMBCR.W 3 | 345 | 13.3263 | 13.3304 | 0.0041
GEN-2020-084 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.1838 | 30.3907 | 0.2069
GEN-2020-084 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 22.8346 | 23.1965 | 0.3619
GEN-2020-084 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.8903 | 30.0304 | 0.1401
GEN-2020-084 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.1153 | 33.2629 | 0.1476
GEN-2020-084 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.2635 | 35.4256 | 0.1621
GEN-2020-084 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.935 | 29.9659 | 0.0309
GEN-2020-084 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.8219 | 25.9917 | 0.1698
GEN-2020-084 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.802 | 23.8584 | 0.0564
GEN-2020-084 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.6883 | 23.762 | 0.0737
GEN-2020-084 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.8815 | 31.939 | 0.0575
GEN-2020-084 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.5487 | 44.6473 | 0.0986
GEN-2020-084 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 47.8997 | 48.0983 | 0.1986
GEN-2020-084 | 02 NEBRASKA | 646211 | S1211 5 | 161 | 36.0984 | 36.1772 | 0.0788
GEN-2020-084 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7367 | 30.7909 | 0.0542
GEN-2020-084 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.0289 | 36.1193 | 0.0904
GEN-2020-084 | 02 NEBRASKA | 646226 | S1226 5 | 161 | 25.4659 | 25.5677 | 0.1018
GEN-2020-084 | 02 NEBRASKA | 646227 | S1227 5 | 161 | 32.9262 | 32.9992 | 0.073
GEN-2020-084 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.8119 | 43.9561 | 0.1442
GEN-2020-084 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8612 | 26.8986 | 0.0374
GEN-2020-084 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.9036 | 29.9627 | 0.0591
GEN-2020-084 | 02 NEBRASKA | 646235 | S1235 5 | 161 | 34.6418 | 34.7331 | 0.0913
GEN-2020-084 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.1898 | 22.2128 | 0.023
GEN-2020-084 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 26.0266 | 26.0705 | 0.0439
GEN-2020-084 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.4609 | 35.5565 | 0.0956
GEN-2020-084 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 32.8411 | 33.0861 | 0.245
GEN-2020-084 | 02 NEBRASKA | 646252 | S1252 5 | 161 | 30.3907 | 30.4729 | 0.0822
GEN-2020-084 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4265 | 34.4987 | 0.0722
GEN-2020-084 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.2172 | 50.3723 | 0.1551
GEN-2020-084 | 02 NEBRASKA | 646256 | S1256 5 | 161 | 23.3127 | 23.3507 | 0.038
GEN-2020-084 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 39.9548 | 40.0447 | 0.0899
GEN-2020-084 | 02 NEBRASKA | 646260 | S1260 5 | 161 | 42.3351 | 42.4281 | 0.093
GEN-2020-084 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 40.275 | 40.3571 | 0.0821
GEN-2020-084 | 02 NEBRASKA | 646287 | S1287 5 | 161 | 23.4971 | 23.5233 | 0.0262
GEN-2020-084 | 02 NEBRASKA | 646291 | S1291 5 | 161 | 7.1501 | 7.1557 | 0.0056
GEN-2020-084 | 02 NEBRASKA | 646297 | S1297 5 | 161 | 19.1444 | 19.1979 | 0.0535
GEN-2020-084 | 02 NEBRASKA | 646298 | S1298 5 | 161 | 29.9689 | 30.1595 | 0.1906
GEN-2020-084 | 02 NEBRASKA | 646305 | S1305 5 | 161 | 28.4826 | 28.6567 | 0.1741
GEN-2020-084 | 02 NEBRASKA | 646341 | S1341 5 | 161 | 27.7071 | 27.8737 | 0.1666
GEN-2020-084 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.7454 | 33.8402 | 0.0948
GEN-2020-084 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.7411 | 43.8416 | 0.1005
GEN-2020-084 | 02 NEBRASKA | 646363 | S1363 5 | 161 | 37.2161 | 37.2765 | 0.0604
GEN-2020-084 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2201 | 32.241 | 0.0209
GEN-2020-084 | 02 NEBRASKA | 647104 | MUD LNG8 | 69 | 14.6871 | 14.6931 | 0.006
GEN-2020-084 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6524 | 32.6716 | 0.0192
GEN-2020-084 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1471 | 27.1676 | 0.0205
GEN-2020-084 | 02 NEBRASKA | 647918 | S918 8 | 69 | 22.9816 | 22.9958 | 0.0142
GEN-2020-084 | 02 NEBRASKA | 647921 | S921 8 | 69 | 26.5044 | 26.5228 | 0.0184
GEN-2020-084 | 02 NEBRASKA | 647937 | S937 8 | 69 | 9.1462 | 9.1477 | 0.0015
GEN-2020-084 | 02 NEBRASKA | 647939 | S939 8 | 69 | 20.1713 | 20.1826 | 0.0113
GEN-2020-084 | 02 NEBRASKA | 647950 | S950 8 | 69 | 20.378 | 20.3901 | 0.0121
GEN-2020-084 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7952 | 17.8049 | 0.0097
GEN-2020-084 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.3807 | 21.4023 | 0.0216
GEN-2020-084 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.2842 | 21.3009 | 0.0167
GEN-2020-084 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.7413 | 25.7472 | 0.0059
GEN-2020-084 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.631 | 29.6398 | 0.0088
GEN-2020-084 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.2474 | 25.2534 | 0.006
GEN-2020-084 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.7871 | 21.7922 | 0.0051
GEN-2020-084 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3657 | 32.3776 | 0.0119
GEN-2020-084 | 02 NEBRASKA | 652509 | FTRANDL4 | 230 | 10.824 | 10.8245 | 0.0005
GEN-2020-084 | 02 NEBRASKA | 652537 | WHITE 3 | 345 | 20.1753 | 20.1757 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 652552 | SIOUXCY2 | 230 | 20.865 | 20.879 | 0.014
GEN-2020-084 | 02 NEBRASKA | 652564 | SIOUXCY3 | 345 | 15.8578 | 15.8749 | 0.0171
GEN-2020-084 | 02 NEBRASKA | 652565 | SIOUXCY4 | 230 | 20.865 | 20.879 | 0.014
GEN-2020-084 | 02 NEBRASKA | 652566 | SIOUXCY5 | 161 | 21.7202 | 21.7322 | 0.012
GEN-2020-084 | 02 NEBRASKA | 652567 | DENISON4 | 230 | 4.825 | 4.8254 | 0.0004
GEN-2020-084 | 02 NEBRASKA | 652864 | SIOUXCY-LNX3 | 345 | 15.672 | 15.6886 | 0.0166
GEN-2020-084 | 02 NEBRASKA | 655126 | MOS-VERM-ER8 | 69 | 2.0196 | 2.0197 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655129 | SW806-ER8 | 69 | 0.8786 | 0.8786 | 0
GEN-2020-084 | 02 NEBRASKA | 655130 | SW808-ER8 | 69 | 2.5376 | 2.5377 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655133 | SW822-ER8 | 69 | 2.1933 | 2.1934 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655136 | SW832-ER8 | 69 | 2.6198 | 2.6199 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655137 | SW833-ER8 | 69 | 2.0923 | 2.0923 | 0
GEN-2020-084 | 02 NEBRASKA | 655145 | SW870-ER8 | 69 | 2.8849 | 2.8849 | 0
GEN-2020-084 | 02 NEBRASKA | 655146 | SW873-ER8 | 69 | 2.8836 | 2.8836 | 0
GEN-2020-084 | 02 NEBRASKA | 655147 | MOS-JEFF-ER8 | 69 | 2.5383 | 2.5384 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655151 | MOS-BGSP-ER8 | 69 | 1.364 | 1.364 | 0
GEN-2020-084 | 02 NEBRASKA | 655152 | SW894-ER8 | 69 | 2.0653 | 2.0653 | 0
GEN-2020-084 | 02 NEBRASKA | 655308 | ALCESTER-ER8 | 69 | 1.026 | 1.026 | 0
GEN-2020-084 | 02 NEBRASKA | 655311 | AKRON-ER8 | 69 | 1.5302 | 1.5302 | 0
GEN-2020-084 | 02 NEBRASKA | 655313 | RICHLAND-ER8 | 69 | 2.5293 | 2.5294 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655314 | ELKPNTCY-ER8 | 69 | 1.9368 | 1.9368 | 0
GEN-2020-084 | 02 NEBRASKA | 655315 | ELKPOINT-ER8 | 69 | 1.9361 | 1.9361 | 0
GEN-2020-084 | 02 NEBRASKA | 655316 | BURBANK-ER8 | 69 | 1.8789 | 1.8789 | 0
GEN-2020-084 | 02 NEBRASKA | 655326 | BGSPRING-ER8 | 69 | 1.1803 | 1.1803 | 0
GEN-2020-084 | 02 NEBRASKA | 655327 | UNIONCRK-ER8 | 69 | 1.9997 | 1.9997 | 0
GEN-2020-084 | 02 NEBRASKA | 655359 | JEFERSON-ER8 | 69 | 1.6867 | 1.6867 | 0
GEN-2020-084 | 02 NEBRASKA | 655360 | MCOOKLK-ER8 | 69 | 1.3601 | 1.3602 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655393 | SWR5123-ER8 | 69 | 0.9785 | 0.9786 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 655427 | MOS-ALC2-ER8 | 69 | 1.026 | 1.026 | 0
GEN-2020-084 | 02 NEBRASKA | 655428 | BIGSPRGS-ER8 | 69 | 1.1803 | 1.1803 | 0
GEN-2020-084 | 02 NEBRASKA | 655484 | RASMUSN-ER4 | 230 | 6.85 | 6.851 | 0.001
GEN-2020-084 | 02 NEBRASKA | 655485 | RASMUSN-ER8 | 69 | 3.3134 | 3.3135 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 658122 | ROCKRPDMUNI8 | 69 | 2.8472 | 2.8472 | 0
GEN-2020-084 | 02 NEBRASKA | 658124 | LUVERNEMUNW8 | 69 | 1.8262 | 1.8262 | 0
GEN-2020-084 | 02 NEBRASKA | 658126 | LUVERNEMUNE8 | 69 | 1.7289 | 1.7289 | 0
GEN-2020-084 | 02 NEBRASKA | 658128 | LUVERNEMUNS8 | 69 | 1.8319 | 1.8319 | 0
GEN-2020-084 | 02 NEBRASKA | 659286 | DEERCREK-BE3 | 345 | 19.5603 | 19.5606 | 0.0003
GEN-2020-084 | 02 NEBRASKA | 659311 | PAHOJA__-BE4 | 230 | 7.6733 | 7.6739 | 0.0006
GEN-2020-084 | 02 NEBRASKA | 659708 | LITLRCKT-LO8 | 69 | 1.9732 | 1.9732 | 0
GEN-2020-084 | 02 NEBRASKA | 659709 | LITLRCK -LO8 | 69 | 1.9323 | 1.9323 | 0
GEN-2020-084 | 02 NEBRASKA | 659710 | GEORGETP-LO8 | 69 | 2.3907 | 2.3907 | 0
GEN-2020-084 | 02 NEBRASKA | 659711 | GEORGE -LO8 | 69 | 2.3288 | 2.3288 | 0
GEN-2020-084 | 02 NEBRASKA | 659712 | RKRMUNTP-LO8 | 69 | 3.3916 | 3.3916 | 0
GEN-2020-084 | 02 NEBRASKA | 659714 | RKRPDTAP-LO8 | 69 | 3.6063 | 3.6064 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 659715 | ROCKRPDS-LO8 | 69 | 3.4498 | 3.4499 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 659726 | STEEN -LO8 | 69 | 2.3485 | 2.3485 | 0
GEN-2020-084 | 02 NEBRASKA | 659727 | LUVERNE -LO8 | 69 | 1.8651 | 1.8652 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 659735 | CLEVELND-LO4 | 230 | 5.1145 | 5.1148 | 0.0003
GEN-2020-084 | 02 NEBRASKA | 659736 | CLEVELND-LO8 | 69 | 4.4478 | 4.4478 | 0
GEN-2020-084 | 02 NEBRASKA | 659900 | EAGLE___-NI4 | 230 | 7.5292 | 7.5302 | 0.001
GEN-2020-084 | 02 NEBRASKA | 659901 | EAGLE___-NI8 | 69 | 14.4297 | 14.4308 | 0.0011
GEN-2020-084 | 02 NEBRASKA | 760515 | GEN-2017-222 | 230 | 3.3656 | 3.3659 | 0.0003
GEN-2020-084 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.0238 | 8.0247 | 0.0009
GEN-2020-084 | 02 NEBRASKA | 760788 | GEN-2017-201 | 345 | 9.6046 | 9.6067 | 0.0021
GEN-2020-084 | 02 NEBRASKA | 762069 | G17-105TAP | 161 | 8.7902 | 8.7964 | 0.0062
GEN-2020-084 | 02 NEBRASKA | 762070 | GEN-2017-105 | 161 | 8.7902 | 8.7964 | 0.0062
GEN-2020-084 | 02 NEBRASKA | 762508 | GEN-2018-131 | 345 | 12.6165 | 12.6192 | 0.0027
GEN-2020-084 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 21.8315 | 22.1619 | 0.3304
GEN-2020-084 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.75 | 22.8013 | 0.0513
GEN-2020-084 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 16.5141 | 17.0842 | 0.5701
GEN-2020-084 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 16.4715 | 17.0417 | 0.5702
GEN-2020-084 | 02 NEBRASKA | 763031 | G18-065-TAP | 345 | 12.3609 | 12.3632 | 0.0023
GEN-2020-084 | 02 NEBRASKA | 763032 | GEN-2018-068 | 345 | 9.242 | 9.2433 | 0.0013
GEN-2020-084 | 02 NEBRASKA | 763098 | GEN-2018-074 | 230 | 3.1612 | 3.1614 | 0.0002
GEN-2020-084 | 02 NEBRASKA | 763142 | GEN-2018-083 | 345 | 2.3001 | 2.3002 | 0.0001
GEN-2020-084 | 02 NEBRASKA | 763439 | GEN-2018-132 | 345 | 12.6165 | 12.6192 | 0.0027
GEN-2020-084 | 02 NEBRASKA | 763443 | G18-131-TAP | 345 | 12.6356 | 12.6384 | 0.0028
GEN-2020-084 | 02 NEBRASKA | 763450 | GEN-2018-132 | 345 | 11.6734 | 11.6757 | 0.0023
GEN-2020-084 | 02 NEBRASKA | 763978 | GEN-2019-069 | 345 | 13.0605 | 13.0643 | 0.0038
GEN-2020-084 | 02 NEBRASKA | 763982 | G19-069-TAP | 345 | 13.1061 | 13.1099 | 0.0038
GEN-2020-084 | 02 NEBRASKA | 764600 | GEN-2020-025 | 161 | 37.2161 | 37.2765 | 0.0604
GEN-2020-084 | 02 NEBRASKA | 764630 | GEN-2020-028 | 161 | 37.2161 | 37.2765 | 0.0604
GEN-2020-084 | 02 NEBRASKA | 764660 | GEN-2020-031 | 161 | 37.2161 | 37.2765 | 0.0604
GEN-2020-084 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.802 | 23.8584 | 0.0564
GEN-2020-084 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.7442 | 33.8389 | 0.0947
GEN-2020-084 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.7442 | 33.8389 | 0.0947
GEN-2020-084 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.7442 | 33.8389 | 0.0947
GEN-2020-084 | 02 NEBRASKA | 764765 | GEN-2020-078 | 161 | 16.3762 | 16.4101 | 0.0339
GEN-2020-084 | 02 NEBRASKA | 764775 | G20-078-TAP | 161 | 16.4111 | 16.4451 | 0.034
GEN-2020-084 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.9252 | 11.93 | 0.0048
GEN-2020-084 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.7658 | 16.7756 | 0.0098
GEN-2020-094 | 02 NEBRASKA | 85831 | J583 | 345 | 6.0603 | 6.0607 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 300039 | 7FAIRPT | 345 | 12.6283 | 12.6313 | 0.003
GEN-2020-094 | 02 NEBRASKA | 300076 | 5FAIRPTB2 | 161 | 16.7053 | 16.7067 | 0.0014
GEN-2020-094 | 02 NEBRASKA | 301347 | 5WINSLOW | 161 | 8.8919 | 8.8923 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 301559 | 5FAIRPTXF3 | 161 | 16.7226 | 16.724 | 0.0014
GEN-2020-094 | 02 NEBRASKA | 541147 | ST JOE_CAP5 | 161 | 18.624 | 18.6256 | 0.0016
GEN-2020-094 | 02 NEBRASKA | 541197 | MULLNCR7 | 345 | 7.8092 | 7.8137 | 0.0045
GEN-2020-094 | 02 NEBRASKA | 541199 | ST JOE 7 | 345 | 20.0206 | 20.0254 | 0.0048
GEN-2020-094 | 02 NEBRASKA | 541201 | SIBLEY 7 | 345 | 21.106 | 21.1077 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 541253 | ST JOE 5 | 161 | 20.8726 | 20.8746 | 0.002
GEN-2020-094 | 02 NEBRASKA | 541257 | COOK 5 | 161 | 14.5706 | 14.5715 | 0.0009
GEN-2020-094 | 02 NEBRASKA | 541258 | WOODBIN5 | 161 | 17.5325 | 17.534 | 0.0015
GEN-2020-094 | 02 NEBRASKA | 541394 | AVENUECTY 5 | 161 | 9.9248 | 9.9252 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 541400 | EASTOWN7 | 345 | 18.5736 | 18.5767 | 0.0031
GEN-2020-094 | 02 NEBRASKA | 541401 | EASTOWN5 | 161 | 17.8701 | 17.8715 | 0.0014
GEN-2020-094 | 02 NEBRASKA | 541411 | MC REAC1 | 345 | 7.4775 | 7.4816 | 0.0041
GEN-2020-094 | 02 NEBRASKA | 541412 | MC REAC2 | 345 | 7.4775 | 7.4816 | 0.0041
GEN-2020-094 | 02 NEBRASKA | 541413 | MC REAC3 | 345 | 7.4775 | 7.4816 | 0.0041
GEN-2020-094 | 02 NEBRASKA | 541414 | SIB REA1 | 345 | 18.848 | 18.8493 | 0.0013
GEN-2020-094 | 02 NEBRASKA | 541500 | KETCHEM7 | 345 | 7.8153 | 7.8175 | 0.0022
GEN-2020-094 | 02 NEBRASKA | 541501 | OSBORN7 | 345 | 6.9749 | 6.9767 | 0.0018
GEN-2020-094 | 02 NEBRASKA | 541510 | HOLT 7 | 345 | 8.9002 | 8.9079 | 0.0077
GEN-2020-094 | 02 NEBRASKA | 541511 | ROCKCK7 | 345 | 6.9396 | 6.9439 | 0.0043
GEN-2020-094 | 02 NEBRASKA | 541517 | HOLT_REACT7 | 345 | 8.8551 | 8.8628 | 0.0077
GEN-2020-094 | 02 NEBRASKA | 541543 | OUTLAW | 345 | 5.7451 | 5.748 | 0.0029
GEN-2020-094 | 02 NEBRASKA | 542980 | NASHUA 7 | 345 | 22.8014 | 22.8033 | 0.0019
GEN-2020-094 | 02 NEBRASKA | 542982 | IATAN 7 | 345 | 29.7959 | 29.798 | 0.0021
GEN-2020-094 | 02 NEBRASKA | 560746 | G13-002-TAP | 115 | 43.3516 | 43.4262 | 0.0746
GEN-2020-094 | 02 NEBRASKA | 583700 | GEN-2013-019 | 115 | 19.1728 | 19.1868 | 0.014
GEN-2020-094 | 02 NEBRASKA | 585241 | GEN-2015-088 | 345 | 12.3309 | 12.348 | 0.0171
GEN-2020-094 | 02 NEBRASKA | 587680 | GEN-2016-074 | 345 | 6.3499 | 6.3503 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 635000 | CBLUFFS3 | 345 | 32.0482 | 32.0776 | 0.0294
GEN-2020-094 | 02 NEBRASKA | 635001 | CBLUFFS5 | 161 | 39.6992 | 39.7193 | 0.0201
GEN-2020-094 | 02 NEBRASKA | 635002 | CBLUFFS8 | 69 | 25.2342 | 25.2374 | 0.0032
GEN-2020-094 | 02 NEBRASKA | 635011 | INDNCRK5 | 161 | 22.0052 | 22.0114 | 0.0062
GEN-2020-094 | 02 NEBRASKA | 635013 | PNYCRK 3 | 345 | 29.1593 | 29.1834 | 0.0241
GEN-2020-094 | 02 NEBRASKA | 635014 | OVRLND 3 | 345 | 27.3705 | 27.3913 | 0.0208
GEN-2020-094 | 02 NEBRASKA | 635015 | OVRLND 5 | 161 | 31.5009 | 31.5131 | 0.0122
GEN-2020-094 | 02 NEBRASKA | 635016 | STHLND 3 | 345 | 29.1247 | 29.1487 | 0.024
GEN-2020-094 | 02 NEBRASKA | 635017 | ATCHSN 3 | 345 | 17.3857 | 17.4024 | 0.0167
GEN-2020-094 | 02 NEBRASKA | 635018 | WESTBORO 3 | 345 | 16.5876 | 16.6021 | 0.0145
GEN-2020-094 | 02 NEBRASKA | 635030 | RIVRBND5 | 161 | 36.1827 | 36.1993 | 0.0166
GEN-2020-094 | 02 NEBRASKA | 635100 | RLHILLS3 | 345 | 13.0827 | 13.0852 | 0.0025
GEN-2020-094 | 02 NEBRASKA | 635570 | ORIENT 3 | 345 | 17.3863 | 17.39 | 0.0037
GEN-2020-094 | 02 NEBRASKA | 635589 | ECLIPSE3 | 345 | 9.058 | 9.0588 | 0.0008
GEN-2020-094 | 02 NEBRASKA | 635590 | FALLOW 3 | 345 | 10.9925 | 10.9936 | 0.0011
GEN-2020-094 | 02 NEBRASKA | 637084 | J476 SHENHLL | 345 | 16.5044 | 16.5188 | 0.0144
GEN-2020-094 | 02 NEBRASKA | 640065 | AXTELL 3 | 345 | 10.2815 | 10.2832 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 640074 | BEAT. S7 | 115 | 5.3776 | 5.378 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 640076 | BEATRCE7 | 115 | 13.1512 | 13.1533 | 0.0021
GEN-2020-094 | 02 NEBRASKA | 640088 | BPS SUB7 | 115 | 15.9239 | 15.9271 | 0.0032
GEN-2020-094 | 02 NEBRASKA | 640111 | CLATONA7 | 115 | 10.9036 | 10.9062 | 0.0026
GEN-2020-094 | 02 NEBRASKA | 640125 | COLMB.E3 | 345 | 11.013 | 11.0187 | 0.0057
GEN-2020-094 | 02 NEBRASKA | 640127 | COLMB.E7 | 115 | 23.5304 | 23.5362 | 0.0058
GEN-2020-094 | 02 NEBRASKA | 640139 | COOPER 3 | 345 | 26.9148 | 26.9666 | 0.0518
GEN-2020-094 | 02 NEBRASKA | 640140 | COOPER 5 | 161 | 18.1229 | 18.1324 | 0.0095
GEN-2020-094 | 02 NEBRASKA | 640141 | COOPER_ESST8 | 69 | 4.6821 | 4.6824 | 0.0003
GEN-2020-094 | 02 NEBRASKA | 640143 | COOPER_602 8 | 69 | 2.0145 | 2.0146 | 0.0001
GEN-2020-094 | 02 NEBRASKA | 640153 | CRETE__7 | 115 | 8.4318 | 8.434 | 0.0022
GEN-2020-094 | 02 NEBRASKA | 640171 | FIRTH 7 | 115 | 7.0138 | 7.0155 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 640174 | FRIEND 7 | 115 | 5.7096 | 5.7104 | 0.0008
GEN-2020-094 | 02 NEBRASKA | 640178 | GENEVA 7 | 115 | 9.9358 | 9.9374 | 0.0016
GEN-2020-094 | 02 NEBRASKA | 640179 | GENEVA 8 | 69 | 4.3115 | 4.3117 | 0.0002
GEN-2020-094 | 02 NEBRASKA | 640200 | GR ISLD4 | 230 | 17.6683 | 17.6735 | 0.0052
GEN-2020-094 | 02 NEBRASKA | 640234 | HUMBOLT5 | 161 | 7.8325 | 7.8333 | 0.0008
GEN-2020-094 | 02 NEBRASKA | 640271 | MCCOOL 3 | 345 | 11.565 | 11.5745 | 0.0095
GEN-2020-094 | 02 NEBRASKA | 640272 | MCCOOL 7 | 115 | 14.7668 | 14.7713 | 0.0045
GEN-2020-094 | 02 NEBRASKA | 640273 | MCCOOL 8 | 69 | 5.7349 | 5.7353 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 640277 | MOORE 3 | 345 | 23.7271 | 23.8276 | 0.1005
GEN-2020-094 | 02 NEBRASKA | 640278 | SHELDON7 | 115 | 44.4105 | 44.4852 | 0.0747
GEN-2020-094 | 02 NEBRASKA | 640312 | PAULINE3 | 345 | 8.4674 | 8.4703 | 0.0029
GEN-2020-094 | 02 NEBRASKA | 640313 | PAULINE7 | 115 | 16.9857 | 16.9883 | 0.0026
GEN-2020-094 | 02 NEBRASKA | 640314 | PAULINE8 | 69 | 4.9454 | 4.9455 | 0.0001
GEN-2020-094 | 02 NEBRASKA | 640316 | PAWNEEL7 | 115 | 11.7977 | 11.8032 | 0.0055
GEN-2020-094 | 02 NEBRASKA | 640342 | SHELCRK3 | 345 | 11.4946 | 11.4993 | 0.0047
GEN-2020-094 | 02 NEBRASKA | 640374 | SWEET W3 | 345 | 11.1603 | 11.1619 | 0.0016
GEN-2020-094 | 02 NEBRASKA | 640413 | YORK SW7 | 115 | 8.419 | 8.4204 | 0.0014
GEN-2020-094 | 02 NEBRASKA | 640446 | COOPER 8 | 69 | 4.7798 | 4.78 | 0.0002
GEN-2020-094 | 02 NEBRASKA | 640447 | YORK.SW T2 8 | 69 | 2.5294 | 2.5295 | 0.0001
GEN-2020-094 | 02 NEBRASKA | 640525 | TOBIAS 3 | 345 | 12.3309 | 12.348 | 0.0171
GEN-2020-094 | 02 NEBRASKA | 640590 | MONOLITH 3 | 345 | 23.2076 | 23.3021 | 0.0945
GEN-2020-094 | 02 NEBRASKA | 640591 | MONOLITH 7 | 115 | 43.3516 | 43.4262 | 0.0746
GEN-2020-094 | 02 NEBRASKA | 645100 | FC1A 5 | 161 | 30.3758 | 30.3907 | 0.0149
GEN-2020-094 | 02 NEBRASKA | 645451 | S3451 3 | 345 | 23.1763 | 23.1965 | 0.0202
GEN-2020-094 | 02 NEBRASKA | 645454 | S3454 3 | 345 | 29.965 | 30.0304 | 0.0654
GEN-2020-094 | 02 NEBRASKA | 645455 | S3455 3 | 345 | 33.1969 | 33.2629 | 0.066
GEN-2020-094 | 02 NEBRASKA | 645456 | S3456 3 | 345 | 35.3627 | 35.4256 | 0.0629
GEN-2020-094 | 02 NEBRASKA | 645458 | S3458 3 | 345 | 29.7592 | 29.9659 | 0.2067
GEN-2020-094 | 02 NEBRASKA | 645459 | S3459 3 | 345 | 25.9628 | 25.9917 | 0.0289
GEN-2020-094 | 02 NEBRASKA | 645740 | S3740 3 | 345 | 23.8126 | 23.8584 | 0.0458
GEN-2020-094 | 02 NEBRASKA | 645761 | S3761 3 | 345 | 23.7294 | 23.762 | 0.0326
GEN-2020-094 | 02 NEBRASKA | 646201 | S1201 5 | 161 | 31.9247 | 31.939 | 0.0143
GEN-2020-094 | 02 NEBRASKA | 646206 | S1206 5 | 161 | 44.6154 | 44.6473 | 0.0319
GEN-2020-094 | 02 NEBRASKA | 646209 | S1209 5 | 161 | 48.0583 | 48.0983 | 0.04
GEN-2020-094 | 02 NEBRASKA | 646216 | S1216 5 | 161 | 30.7757 | 30.7909 | 0.0152
GEN-2020-094 | 02 NEBRASKA | 646217 | S1217 5 | 161 | 33.5354 | 33.5535 | 0.0181
GEN-2020-094 | 02 NEBRASKA | 646220 | S1220 5 | 161 | 28.7741 | 28.7855 | 0.0114
GEN-2020-094 | 02 NEBRASKA | 646221 | S1221 5 | 161 | 36.094 | 36.1193 | 0.0253
GEN-2020-094 | 02 NEBRASKA | 646229 | S1229 5 | 161 | 28.8795 | 28.8915 | 0.012
GEN-2020-094 | 02 NEBRASKA | 646231 | S1231 5 | 161 | 43.9212 | 43.9561 | 0.0349
GEN-2020-094 | 02 NEBRASKA | 646232 | S1232 5 | 161 | 26.8858 | 26.8986 | 0.0128
GEN-2020-094 | 02 NEBRASKA | 646233 | S1233 5 | 161 | 29.9436 | 29.9627 | 0.0191
GEN-2020-094 | 02 NEBRASKA | 646244 | S1244 5 | 161 | 22.205 | 22.2128 | 0.0078
GEN-2020-094 | 02 NEBRASKA | 646249 | S1249 5 | 161 | 26.0551 | 26.0705 | 0.0154
GEN-2020-094 | 02 NEBRASKA | 646250 | S1250 5 | 161 | 35.5384 | 35.5565 | 0.0181
GEN-2020-094 | 02 NEBRASKA | 646251 | S1251 5 | 161 | 33.0684 | 33.0861 | 0.0177
GEN-2020-094 | 02 NEBRASKA | 646254 | S1254 5 | 161 | 34.4702 | 34.4987 | 0.0285
GEN-2020-094 | 02 NEBRASKA | 646255 | S1255 5 | 161 | 50.3153 | 50.3723 | 0.057
GEN-2020-094 | 02 NEBRASKA | 646259 | S1259 5 | 161 | 40.0109 | 40.0447 | 0.0338
GEN-2020-094 | 02 NEBRASKA | 646263 | S1263 5 | 161 | 8.4586 | 8.4599 | 0.0013
GEN-2020-094 | 02 NEBRASKA | 646278 | S1278 5 | 161 | 28.0697 | 28.0853 | 0.0156
GEN-2020-094 | 02 NEBRASKA | 646280 | S1280 5 | 161 | 10.4445 | 10.4466 | 0.0021
GEN-2020-094 | 02 NEBRASKA | 646281 | S1281 5 | 161 | 40.3231 | 40.3571 | 0.034
GEN-2020-094 | 02 NEBRASKA | 646286 | S1286 5 | 161 | 26.6354 | 26.6452 | 0.0098
GEN-2020-094 | 02 NEBRASKA | 646347 | S1347 5 | 161 | 33.8217 | 33.8402 | 0.0185
GEN-2020-094 | 02 NEBRASKA | 646361 | S1361 5 | 161 | 43.801 | 43.8416 | 0.0406
GEN-2020-094 | 02 NEBRASKA | 646366 | S1366 5 | 161 | 16.3881 | 16.3924 | 0.0043
GEN-2020-094 | 02 NEBRASKA | 647006 | S906 N 8 | 69 | 32.2346 | 32.241 | 0.0064
GEN-2020-094 | 02 NEBRASKA | 647015 | S6815T1&T2 8 | 69 | 12.0651 | 12.066 | 0.0009
GEN-2020-094 | 02 NEBRASKA | 647016 | 6815TP38 | 69 | 17.5361 | 17.538 | 0.0019
GEN-2020-094 | 02 NEBRASKA | 647017 | 6815TP98 | 69 | 12.6516 | 12.6526 | 0.001
GEN-2020-094 | 02 NEBRASKA | 647815 | S6815T3 8 | 69 | 11.4302 | 11.431 | 0.0008
GEN-2020-094 | 02 NEBRASKA | 647874 | S6874 8 | 69 | 8.6127 | 8.6132 | 0.0005
GEN-2020-094 | 02 NEBRASKA | 647901 | S901 8 | 69 | 26.3184 | 26.3216 | 0.0032
GEN-2020-094 | 02 NEBRASKA | 647904 | S904 8 | 69 | 8.7491 | 8.7497 | 0.0006
GEN-2020-094 | 02 NEBRASKA | 647906 | S906 S 8 | 69 | 32.6654 | 32.6716 | 0.0062
GEN-2020-094 | 02 NEBRASKA | 647909 | S909 8 | 69 | 27.1627 | 27.1676 | 0.0049
GEN-2020-094 | 02 NEBRASKA | 647916 | S916 8 | 69 | 23.8284 | 23.8322 | 0.0038
GEN-2020-094 | 02 NEBRASKA | 647924 | S924 8 | 69 | 24.3921 | 24.3955 | 0.0034
GEN-2020-094 | 02 NEBRASKA | 647928 | S928 8 | 69 | 17.2317 | 17.2336 | 0.0019
GEN-2020-094 | 02 NEBRASKA | 647938 | S938 8 | 69 | 21.7321 | 21.7349 | 0.0028
GEN-2020-094 | 02 NEBRASKA | 647995 | S995 8 | 69 | 9.4893 | 9.4899 | 0.0006
GEN-2020-094 | 02 NEBRASKA | 650114 | NW68HOLDRG3 | 345 | 17.7491 | 17.8049 | 0.0558
GEN-2020-094 | 02 NEBRASKA | 650185 | WAGENER 3 | 345 | 21.2832 | 21.4023 | 0.1191
GEN-2020-094 | 02 NEBRASKA | 650189 | 103&ROKEBY3 | 345 | 21.1186 | 21.3009 | 0.1823
GEN-2020-094 | 02 NEBRASKA | 650210 | NW70FAIRFD7 | 115 | 21.4698 | 21.4905 | 0.0207
GEN-2020-094 | 02 NEBRASKA | 650214 | NW68HOLDRG7 | 115 | 25.7172 | 25.7472 | 0.03
GEN-2020-094 | 02 NEBRASKA | 650216 | SW27&F 7 | 115 | 22.1917 | 22.2138 | 0.0221
GEN-2020-094 | 02 NEBRASKA | 650238 | 20PIONEERS7 | 115 | 27.4306 | 27.4641 | 0.0335
GEN-2020-094 | 02 NEBRASKA | 650242 | FOLSM&PHIL7 | 115 | 27.8438 | 27.8769 | 0.0331
GEN-2020-094 | 02 NEBRASKA | 650246 | SW7&BENNET7 | 115 | 23.4336 | 23.4567 | 0.0231
GEN-2020-094 | 02 NEBRASKA | 650247 | 40&BENNET 7 | 115 | 21.5033 | 21.5234 | 0.0201
GEN-2020-094 | 02 NEBRASKA | 650262 | 57&GARLAND7 | 115 | 25.4991 | 25.5293 | 0.0302
GEN-2020-094 | 02 NEBRASKA | 650267 | 84LEIGHTON7 | 115 | 29.5983 | 29.6398 | 0.0415
GEN-2020-094 | 02 NEBRASKA | 650270 | 70&CALVERT7 | 115 | 27.5444 | 27.5796 | 0.0352
GEN-2020-094 | 02 NEBRASKA | 650271 | 81&OCHENEY7 | 115 | 25.2235 | 25.2534 | 0.0299
GEN-2020-094 | 02 NEBRASKA | 650272 | 91&A 7 | 115 | 21.9639 | 21.9865 | 0.0226
GEN-2020-094 | 02 NEBRASKA | 650273 | 93&O 7 | 115 | 22.722 | 22.7463 | 0.0243
GEN-2020-094 | 02 NEBRASKA | 650274 | 91&HWY2 7 | 115 | 21.8432 | 21.8649 | 0.0217
GEN-2020-094 | 02 NEBRASKA | 650279 | 120&ALVO 7 | 115 | 21.7689 | 21.7922 | 0.0233
GEN-2020-094 | 02 NEBRASKA | 650283 | WAVERLY 7 | 115 | 21.244 | 21.2645 | 0.0205
GEN-2020-094 | 02 NEBRASKA | 650284 | 84FLETCHER7 | 115 | 25.0378 | 25.0647 | 0.0269
GEN-2020-094 | 02 NEBRASKA | 650285 | WAGENER 7 | 115 | 32.3188 | 32.3776 | 0.0588
GEN-2020-094 | 02 NEBRASKA | 650290 | ROKEBY 7 | 115 | 25.7166 | 25.7446 | 0.028
GEN-2020-094 | 02 NEBRASKA | 653571 | GR ISLD3 | 345 | 13.4791 | 13.4843 | 0.0052
GEN-2020-094 | 02 NEBRASKA | 653871 | GR ISLD-LNX3 | 345 | 13.3553 | 13.3604 | 0.0051
GEN-2020-094 | 02 NEBRASKA | 760746 | GEN-2017-115 | 345 | 8.0184 | 8.0247 | 0.0063
GEN-2020-094 | 02 NEBRASKA | 760872 | GEN-2017-198 | 69 | 24.9616 | 24.9645 | 0.0029
GEN-2020-094 | 02 NEBRASKA | 761208 | GEN-2017-210 | 345 | 10.1137 | 10.1209 | 0.0072
GEN-2020-094 | 02 NEBRASKA | 761292 | GEN-2017-181 | 345 | 7.0002 | 7.0051 | 0.0049
GEN-2020-094 | 02 NEBRASKA | 761313 | GEN-2017-182 | 345 | 5.8456 | 5.849 | 0.0034
GEN-2020-094 | 02 NEBRASKA | 761376 | GEN-2017-183 | 345 | 7.5831 | 7.5835 | 0.0004
GEN-2020-094 | 02 NEBRASKA | 761383 | G17-183-TAP | 345 | 16.5042 | 16.5059 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 762603 | GEN-2018-025 | 345 | 22.1435 | 22.1619 | 0.0184
GEN-2020-094 | 02 NEBRASKA | 762691 | GEN-2018-033 | 345 | 22.7596 | 22.8013 | 0.0417
GEN-2020-094 | 02 NEBRASKA | 762779 | G18-043-TAP | 345 | 17.0769 | 17.0842 | 0.0073
GEN-2020-094 | 02 NEBRASKA | 762780 | GEN-2018-043 | 345 | 17.0346 | 17.0417 | 0.0071
GEN-2020-094 | 02 NEBRASKA | 763505 | GEN-2019-009 | 161 | 8.1523 | 8.1535 | 0.0012
GEN-2020-094 | 02 NEBRASKA | 763725 | GEN-2019-041 | 115 | 43.2448 | 43.3189 | 0.0741
GEN-2020-094 | 02 NEBRASKA | 764420 | GEN-2020-011 | 345 | 10.2632 | 10.265 | 0.0018
GEN-2020-094 | 02 NEBRASKA | 764431 | G20-011-SS1 | 345 | 10.2518 | 10.2535 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 764432 | G20-011-SS2 | 345 | 10.1286 | 10.1303 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 764433 | G20-011-SS3 | 345 | 10.1681 | 10.1698 | 0.0017
GEN-2020-094 | 02 NEBRASKA | 764434 | G20-011-SS4 | 345 | 9.955 | 9.9566 | 0.0016
GEN-2020-094 | 02 NEBRASKA | 764705 | GEN-2020-038 | 345 | 23.8126 | 23.8584 | 0.0458
GEN-2020-094 | 02 NEBRASKA | 764720 | GEN-2020-043 | 161 | 33.8205 | 33.8389 | 0.0184
GEN-2020-094 | 02 NEBRASKA | 764735 | GEN-2020-044 | 161 | 33.8205 | 33.8389 | 0.0184
GEN-2020-094 | 02 NEBRASKA | 764750 | GEN-2020-045 | 161 | 33.8205 | 33.8389 | 0.0184
GEN-2020-094 | 02 NEBRASKA | 764795 | GEN-2020-094 | 345 | 11.5171 | 11.93 | 0.4129
GEN-2020-094 | 02 NEBRASKA | 764805 | G20-094-TAP | 345 | 16.3665 | 16.7756 | 0.4091
ASGI-2020-001 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.7834 | 6.8375 | 0.0541
ASGI-2020-001 | 03 CENTRAL | 300540 | 2NORTON | 69 | 6.1586 | 6.1708 | 0.0122
ASGI-2020-001 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.2947 | 6.3341 | 0.0394
ASGI-2020-001 | 03 CENTRAL | 345221 | 5MOBERLY | 161 | 16.1731 | 16.1816 | 0.0085
ASGI-2020-001 | 03 CENTRAL | 543012 | SWAVCAP2 | 69 | 3.8956 | 4.2492 | 0.3536
ASGI-2020-001 | 03 CENTRAL | 543013 | SWAVCAP5 | 161 | 3.4492 | 3.5069 | 0.0577
ASGI-2020-001 | 03 CENTRAL | 543059 | MALTABN5 | 161 | 4.1467 | 4.2043 | 0.0576
ASGI-2020-001 | 03 CENTRAL | 543061 | BRUNSWK5 | 161 | 5.9565 | 5.9608 | 0.0043
ASGI-2020-001 | 03 CENTRAL | 543062 | SALSBRY5 | 161 | 12.1711 | 12.1952 | 0.0241
ASGI-2020-001 | 03 CENTRAL | 543063 | SWAVRLY5 | 161 | 3.5194 | 3.5794 | 0.06
ASGI-2020-001 | 03 CENTRAL | 543064 | NORTON 5 | 161 | 6.8058 | 6.8611 | 0.0553
ASGI-2020-001 | 03 CENTRAL | 543070 | WEST---5 | 161 | 4.7411 | 4.7679 | 0.0268
ASGI-2020-001 | 03 CENTRAL | 543071 | S EAST 5 | 161 | 4.9322 | 4.9611 | 0.0289
ASGI-2020-001 | 03 CENTRAL | 543072 | MRSHLJT5 | 161 | 5.9366 | 5.9786 | 0.042
ASGI-2020-001 | 03 CENTRAL | 543073 | MIAMI_ 5 | 161 | 4.8112 | 4.8388 | 0.0276
ASGI-2020-001 | 03 CENTRAL | 543094 | SWAVRLY2 | 69 | 3.8973 | 4.2512 | 0.3539
ASGI-2020-001 | 03 CENTRAL | 543097 | CORDER 2 | 69 | 3.6973 | 3.9163 | 0.219
ASGI-2020-001 | 03 CENTRAL | 543098 | CTY HIG2 | 69 | 3.9902 | 4.1952 | 0.205
ASGI-2020-001 | 03 CENTRAL | 543099 | HIGNSVL2 | 69 | 4.0028 | 4.204 | 0.2012
ASGI-2020-001 | 03 CENTRAL | 543101 | DOVER2 | 69 | 3.6903 | 3.9149 | 0.2246
ASGI-2020-001 | 03 CENTRAL | 543102 | WHGNSVL2 | 69 | 4.1476 | 4.3211 | 0.1735
ASGI-2020-001 | 03 CENTRAL | 543144 | HGNSCTYW2 | 69 | 3.6393 | 3.8087 | 0.1694
ASGI-2020-001 | 03 CENTRAL | 543146 | HGNSCTYPLNT2 | 69 | 3.946 | 4.1464 | 0.2004
ASGI-2020-001 | 03 CENTRAL | 543657 | CORDERTP2 | 69 | 3.8931 | 4.1361 | 0.243
ASGI-2020-001 | 03 CENTRAL | 543658 | DOVER_TAP2 | 69 | 3.8851 | 4.1342 | 0.2491
ASGI-2020-001 | 03 CENTRAL | 762383 | ASG-2018-007 | 161 | 12.1597 | 12.1838 | 0.0241
ASGI-2020-001 | 03 CENTRAL | 765235 | AGI-2020-001 | 69 | 3.8973 | 4.2512 | 0.3539
ASGI-2020-003 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 15.6344 | 15.6431 | 0.0087
ASGI-2020-003 | 03 CENTRAL | 300066 | 5HIGBEEB1 | 161 | 13.0399 | 13.0477 | 0.0078
ASGI-2020-003 | 03 CENTRAL | 300091 | 5LATHRP | 161 | 7.3101 | 7.3123 | 0.0022
ASGI-2020-003 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.4511 | 19.483 | 0.0319
ASGI-2020-003 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.8287 | 6.8375 | 0.0088
ASGI-2020-003 | 03 CENTRAL | 300120 | 5THMHILB1 | 161 | 32.5367 | 32.5703 | 0.0336
ASGI-2020-003 | 03 CENTRAL | 300126 | 5MOBTAP | 161 | 16.173 | 16.1922 | 0.0192
ASGI-2020-003 | 03 CENTRAL | 300132 | 5THMHLB2 | 161 | 32.6841 | 32.718 | 0.0339
ASGI-2020-003 | 03 CENTRAL | 300133 | 5THMHLB3 | 161 | 32.5812 | 32.6148 | 0.0336
ASGI-2020-003 | 03 CENTRAL | 300304 | 2MOCITY | 69 | 9.537 | 9.5391 | 0.0021
ASGI-2020-003 | 03 CENTRAL | 300381 | 5BEVIER | 161 | 7.9725 | 7.9743 | 0.0018
ASGI-2020-003 | 03 CENTRAL | 300500 | 5HUNTSDL | 161 | 11.0805 | 11.0815 | 0.001
ASGI-2020-003 | 03 CENTRAL | 300540 | 2NORTON | 69 | 6.1688 | 6.1708 | 0.002
ASGI-2020-003 | 03 CENTRAL | 300953 | 5HARRSBRG | 161 | 9.4339 | 9.4365 | 0.0026
ASGI-2020-003 | 03 CENTRAL | 301443 | 5THMHLB4 | 161 | 32.2866 | 32.3207 | 0.0341
ASGI-2020-003 | 03 CENTRAL | 301494 | 5HIGBEEB2 | 161 | 13.04 | 13.0479 | 0.0079
ASGI-2020-003 | 03 CENTRAL | 301503 | 7THOMHLGSU3 | 345 | 15.5054 | 15.5138 | 0.0084
ASGI-2020-003 | 03 CENTRAL | 301504 | 5THOMHLGSU1 | 161 | 31.4686 | 31.4997 | 0.0311
ASGI-2020-003 | 03 CENTRAL | 301505 | 5THOMHLGSU2 | 161 | 31.4432 | 31.4743 | 0.0311
ASGI-2020-003 | 03 CENTRAL | 301507 | 5THOMHLU3SU | 161 | 30.928 | 30.9583 | 0.0303
ASGI-2020-003 | 03 CENTRAL | 301508 | 5THOMHLXF1 | 161 | 31.1754 | 31.2063 | 0.0309
ASGI-2020-003 | 03 CENTRAL | 301510 | 5THOMHLXF4 | 161 | 31.9625 | 31.9957 | 0.0332
ASGI-2020-003 | 03 CENTRAL | 301511 | 5THMHILTFERB | 161 | 32.2566 | 32.2897 | 0.0331
ASGI-2020-003 | 03 CENTRAL | 301563 | 5MOCITYB1 | 161 | 19.4751 | 19.5069 | 0.0318
ASGI-2020-003 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.3278 | 6.3341 | 0.0063
ASGI-2020-003 | 03 CENTRAL | 344557 | 5MAURER 1 | 161 | 8.2548 | 8.2919 | 0.0371
ASGI-2020-003 | 03 CENTRAL | 344558 | 5MAURER 2 | 161 | 8.2548 | 8.2919 | 0.0371
ASGI-2020-003 | 03 CENTRAL | 345221 | 5MOBERLY | 161 | 16.1624 | 16.1816 | 0.0192
ASGI-2020-003 | 03 CENTRAL | 345222 | 2MOBERLY | 69 | 8.0603 | 8.0619 | 0.0016
ASGI-2020-003 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 14.8026 | 14.8047 | 0.0021
ASGI-2020-003 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.5389 | 22.5433 | 0.0044
ASGI-2020-003 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 22.5389 | 22.5433 | 0.0044
ASGI-2020-003 | 03 CENTRAL | 346048 | 2MAURER | 69 | 3.3003 | 3.3028 | 0.0025
ASGI-2020-003 | 03 CENTRAL | 346096 | 2MACON_AM | 69 | 1.6192 | 1.6193 | 0.0001
ASGI-2020-003 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.7015 | 3.7015 | 0
ASGI-2020-003 | 03 CENTRAL | 346169 | 2DUPONT | 69 | 6.9873 | 6.9885 | 0.0012
ASGI-2020-003 | 03 CENTRAL | 346170 | 2ROTH TAP | 69 | 1.8428 | 1.8428 | 0
ASGI-2020-003 | 03 CENTRAL | 346171 | 2SPRK TAP | 69 | 7.2044 | 7.2057 | 0.0013
ASGI-2020-003 | 03 CENTRAL | 541248 | LBRTYST5 | 161 | 19.4241 | 19.4346 | 0.0105
ASGI-2020-003 | 03 CENTRAL | 543013 | SWAVCAP5 | 161 | 3.5048 | 3.5069 | 0.0021
ASGI-2020-003 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 26.9505 | 26.9596 | 0.0091
ASGI-2020-003 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.9105 | 13.9129 | 0.0024
ASGI-2020-003 | 03 CENTRAL | 543059 | MALTABN5 | 161 | 4.2012 | 4.2043 | 0.0031
ASGI-2020-003 | 03 CENTRAL | 543060 | CAROLTN5 | 161 | 4.5726 | 4.7232 | 0.1506
ASGI-2020-003 | 03 CENTRAL | 543061 | BRUNSWK5 | 161 | 5.8692 | 5.9608 | 0.0916
ASGI-2020-003 | 03 CENTRAL | 543062 | SALSBRY5 | 161 | 12.1308 | 12.1952 | 0.0644
ASGI-2020-003 | 03 CENTRAL | 543063 | SWAVRLY5 | 161 | 3.5773 | 3.5794 | 0.0021
ASGI-2020-003 | 03 CENTRAL | 543064 | NORTON 5 | 161 | 6.8521 | 6.8611 | 0.009
ASGI-2020-003 | 03 CENTRAL | 543070 | WEST---5 | 161 | 4.7636 | 4.7679 | 0.0043
ASGI-2020-003 | 03 CENTRAL | 543071 | S EAST 5 | 161 | 4.9564 | 4.9611 | 0.0047
ASGI-2020-003 | 03 CENTRAL | 543072 | MRSHLJT5 | 161 | 5.9718 | 5.9786 | 0.0068
ASGI-2020-003 | 03 CENTRAL | 543073 | MIAMI_ 5 | 161 | 4.8343 | 4.8388 | 0.0045
ASGI-2020-003 | 03 CENTRAL | 543095 | LIBRTYS2 | 69 | 12.4457 | 12.4464 | 0.0007
ASGI-2020-003 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.6503 | 25.6684 | 0.0181
ASGI-2020-003 | 03 CENTRAL | 762383 | ASG-2018-007 | 161 | 12.1195 | 12.1838 | 0.0643
ASGI-2020-003 | 03 CENTRAL | 765265 | AGI-2020-003 | 161 | 4.5726 | 4.7232 | 0.1506
GEN-2020-003 | 03 CENTRAL | 532981 | CRESWLN4 | 138 | 9.2393 | 9.301 | 0.0617
GEN-2020-003 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 11.0534 | 11.0914 | 0.038
GEN-2020-003 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 12.5075 | 12.5495 | 0.042
GEN-2020-003 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 6.2232 | 6.2446 | 0.0214
GEN-2020-003 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.7074 | 6.7322 | 0.0248
GEN-2020-003 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 12.3397 | 12.3774 | 0.0377
GEN-2020-003 | 03 CENTRAL | 533070 | SLATECRK4 | 138 | 6.1709 | 6.1962 | 0.0253
GEN-2020-003 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.6812 | 24.6915 | 0.0103
GEN-2020-003 | 03 CENTRAL | 533541 | AKRON 2 | 69 | 7.5293 | 7.571 | 0.0417
GEN-2020-003 | 03 CENTRAL | 533543 | CRESWLN2 | 69 | 14.3443 | 14.4874 | 0.1431
GEN-2020-003 | 03 CENTRAL | 533545 | FLORAL 2 | 69 | 2.5845 | 2.5889 | 0.0044
GEN-2020-003 | 03 CENTRAL | 533546 | FLORALJ2 | 69 | 2.9367 | 2.9424 | 0.0057
GEN-2020-003 | 03 CENTRAL | 533547 | OAK 2 | 69 | 10.0138 | 10.2116 | 0.1978
GEN-2020-003 | 03 CENTRAL | 533549 | RAINBOW2 | 69 | 7.8192 | 8.0157 | 0.1965
GEN-2020-003 | 03 CENTRAL | 533550 | RICHLAN2 | 69 | 6.3057 | 6.3184 | 0.0127
GEN-2020-003 | 03 CENTRAL | 533551 | SC1KING2 | 69 | 3.5541 | 3.5626 | 0.0085
GEN-2020-003 | 03 CENTRAL | 533553 | SC4ROME2 | 69 | 6.5741 | 6.5902 | 0.0161
GEN-2020-003 | 03 CENTRAL | 533554 | SC5SILV2 | 69 | 7.5439 | 7.6273 | 0.0834
GEN-2020-003 | 03 CENTRAL | 533555 | SC7CRES2 | 69 | 14.3208 | 14.4634 | 0.1426
GEN-2020-003 | 03 CENTRAL | 533556 | STROTHR2 | 69 | 8.0198 | 8.2554 | 0.2356
GEN-2020-003 | 03 CENTRAL | 533557 | TIMBER 2 | 69 | 2.5977 | 2.602 | 0.0043
GEN-2020-003 | 03 CENTRAL | 533558 | TIMBJCT2 | 69 | 9.2528 | 9.316 | 0.0632
GEN-2020-003 | 03 CENTRAL | 533559 | UDALL 2 | 69 | 7.8109 | 7.8494 | 0.0385
GEN-2020-003 | 03 CENTRAL | 533561 | WINFLD 2 | 69 | 9.1088 | 9.478 | 0.3692
GEN-2020-003 | 03 CENTRAL | 533562 | PRAIRIE2 | 69 | 7.7094 | 7.8141 | 0.1047
GEN-2020-003 | 03 CENTRAL | 533563 | PRAIRIJ2 | 69 | 8.5128 | 8.6407 | 0.1279
GEN-2020-003 | 03 CENTRAL | 533573 | CRESWLS2 | 69 | 14.3395 | 14.4824 | 0.1429
GEN-2020-003 | 03 CENTRAL | 533836 | ROSEHIL2 | 69 | 5.7146 | 5.7202 | 0.0056
GEN-2020-003 | 03 CENTRAL | 533837 | RH JCT 2 | 69 | 7.0055 | 7.0139 | 0.0084
GEN-2020-003 | 03 CENTRAL | 533990 | EAST SUB 2 | 69 | 7.4995 | 8.0225 | 0.523
GEN-2020-003 | 03 CENTRAL | 533991 | WEST SUB 2 | 69 | 7.0258 | 7.3229 | 0.2971
GEN-2020-003 | 03 CENTRAL | 533992 | VIKING SUB 2 | 69 | 6.8486 | 7.2189 | 0.3703
GEN-2020-003 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 9.4526 | 9.4752 | 0.0226
GEN-2020-003 | 03 CENTRAL | 765085 | GEN-2020-003 | 69 | 7.4995 | 8.0225 | 0.523
GEN-2020-007 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 12.9324 | 12.9346 | 0.0022
GEN-2020-007 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.2551 | 16.2782 | 0.0231
GEN-2020-007 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5688 | 24.5713 | 0.0025
GEN-2020-007 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 40.8896 | 40.8915 | 0.0019
GEN-2020-007 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.1873 | 13.1981 | 0.0108
GEN-2020-007 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.1574 | 13.1619 | 0.0045
GEN-2020-007 | 03 CENTRAL | 509807 | ONETA--7 | 345 | 29.0071 | 29.0084 | 0.0013
GEN-2020-007 | 03 CENTRAL | 509836 | OEC 7 | 345 | 28.7469 | 28.7481 | 0.0012
GEN-2020-007 | 03 CENTRAL | 509852 | T.NO.--7 | 345 | 23.5873 | 23.5895 | 0.0022
GEN-2020-007 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.4759 | 11.478 | 0.0021
GEN-2020-007 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.0506 | 12.0572 | 0.0066
GEN-2020-007 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.168 | 19.1718 | 0.0038
GEN-2020-007 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.9114 | 26.9139 | 0.0025
GEN-2020-007 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12.0001 | 12.0021 | 0.002
GEN-2020-007 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.03 | 12.032 | 0.002
GEN-2020-007 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5738 | 16.5846 | 0.0108
GEN-2020-007 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3938 | 16.4043 | 0.0105
GEN-2020-007 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.7712 | 12.7759 | 0.0047
GEN-2020-007 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.4587 | 11.4605 | 0.0018
GEN-2020-007 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.7047 | 16.7394 | 0.0347
GEN-2020-007 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 21.0101 | 21.0589 | 0.0488
GEN-2020-007 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8818 | 13.8894 | 0.0076
GEN-2020-007 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9153 | 11.9338 | 0.0185
GEN-2020-007 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.0224 | 11.0381 | 0.0157
GEN-2020-007 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7597 | 9.7665 | 0.0068
GEN-2020-007 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4891 | 9.4954 | 0.0063
GEN-2020-007 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.7384 | 20.7452 | 0.0068
GEN-2020-007 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.4745 | 7.4751 | 0.0006
GEN-2020-007 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.2005 | 6.2009 | 0.0004
GEN-2020-007 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.1526 | 5.1528 | 0.0002
GEN-2020-007 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9334 | 18.9486 | 0.0152
GEN-2020-007 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0714 | 7.0718 | 0.0004
GEN-2020-007 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1758 | 18.2288 | 0.053
GEN-2020-007 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.5105 | 18.527 | 0.0165
GEN-2020-007 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6969 | 5.6971 | 0.0002
GEN-2020-007 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.6698 | 23.6806 | 0.0108
GEN-2020-007 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.1176 | 18.2036 | 0.086
GEN-2020-007 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1483 | 14.1504 | 0.0021
GEN-2020-007 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.1318 | 16.2276 | 0.0958
GEN-2020-007 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3732 | 10.3802 | 0.007
GEN-2020-007 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2141 | 9.2196 | 0.0055
GEN-2020-007 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5049 | 13.5715 | 0.0666
GEN-2020-007 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.4121 | 10.415 | 0.0029
GEN-2020-007 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.5729 | 13.5784 | 0.0055
GEN-2020-007 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.0106 | 14.016 | 0.0054
GEN-2020-007 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.8808 | 13.8861 | 0.0053
GEN-2020-007 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.7139 | 21.739 | 0.0251
GEN-2020-007 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.0206 | 11.0257 | 0.0051
GEN-2020-007 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0346 | 14.0386 | 0.004
GEN-2020-007 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1641 | 11.1769 | 0.0128
GEN-2020-007 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1382 | 5.1385 | 0.0003
GEN-2020-007 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.2109 | 8.2126 | 0.0017
GEN-2020-007 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2077 | 8.2093 | 0.0016
GEN-2020-007 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7678 | 23.7942 | 0.0264
GEN-2020-007 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.2738 | 28.2854 | 0.0116
GEN-2020-007 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2448 | 19.2501 | 0.0053
GEN-2020-007 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2937 | 11.2955 | 0.0018
GEN-2020-007 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4871 | 22.4942 | 0.0071
GEN-2020-007 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.139 | 4.1393 | 0.0003
GEN-2020-007 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 13.1264 | 13.1323 | 0.0059
GEN-2020-007 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2566 | 7.2579 | 0.0013
GEN-2020-007 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.3592 | 25.3852 | 0.026
GEN-2020-007 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4023 | 25.4284 | 0.0261
GEN-2020-007 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.2838 | 25.3096 | 0.0258
GEN-2020-007 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8833 | 19.889 | 0.0057
GEN-2020-007 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.2739 | 25.2817 | 0.0078
GEN-2020-007 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3811 | 32.3893 | 0.0082
GEN-2020-007 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5736 | 20.5787 | 0.0051
GEN-2020-007 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.2193 | 31.2348 | 0.0155
GEN-2020-007 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.8477 | 19.8528 | 0.0051
GEN-2020-007 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5467 | 3.5471 | 0.0004
GEN-2020-007 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.162 | 3.1623 | 0.0003
GEN-2020-007 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.154 | 5.1549 | 0.0009
GEN-2020-007 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5453 | 3.5457 | 0.0004
GEN-2020-007 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.8173 | 4.8182 | 0.0009
GEN-2020-007 | 03 CENTRAL | 533630 | CC3WEST2 | 69 | 4.7613 | 4.762 | 0.0007
GEN-2020-007 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.9734 | 8.9742 | 0.0008
GEN-2020-007 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2271 | 6.2285 | 0.0014
GEN-2020-007 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.3311 | 6.3318 | 0.0007
GEN-2020-007 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.7695 | 8.7709 | 0.0014
GEN-2020-007 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.6362 | 7.637 | 0.0008
GEN-2020-007 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 24.0176 | 24.0283 | 0.0107
GEN-2020-007 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0427 | 24.0535 | 0.0108
GEN-2020-007 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.6095 | 20.748 | 0.1385
GEN-2020-007 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.7906 | 18.8625 | 0.0719
GEN-2020-007 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.3776 | 21.4074 | 0.0298
GEN-2020-007 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 14.2438 | 14.2566 | 0.0128
GEN-2020-007 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 33.4723 | 33.5175 | 0.0452
GEN-2020-007 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.3837 | 19.4192 | 0.0355
GEN-2020-007 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 20.4288 | 20.4689 | 0.0401
GEN-2020-007 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 22.7931 | 22.8468 | 0.0537
GEN-2020-007 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.5608 | 4.5614 | 0.0006
GEN-2020-007 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.2201 | 21.2654 | 0.0453
GEN-2020-007 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.0643 | 19.088 | 0.0237
GEN-2020-007 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6742 | 2.6772 | 0.003
GEN-2020-007 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.8301 | 20.9429 | 0.1128
GEN-2020-007 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 34.6159 | 34.6829 | 0.067
GEN-2020-007 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.5365 | 30.5801 | 0.0436
GEN-2020-007 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.3304 | 27.6185 | 0.2881
GEN-2020-007 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.0547 | 30.1269 | 0.0722
GEN-2020-007 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.5223 | 25.8373 | 0.315
GEN-2020-007 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.7764 | 40.9756 | 0.1992
GEN-2020-007 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.0776 | 22.1427 | 0.0651
GEN-2020-007 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 43.2856 | 43.3904 | 0.1048
GEN-2020-007 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 26.3215 | 27.8947 | 1.5732
GEN-2020-007 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.0931 | 37.1574 | 0.0643
GEN-2020-007 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.9766 | 20.0023 | 0.0257
GEN-2020-007 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.1291 | 25.1791 | 0.05
GEN-2020-007 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 36.5434 | 36.5991 | 0.0557
GEN-2020-007 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 17.8553 | 17.879 | 0.0237
GEN-2020-007 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.2896 | 21.3275 | 0.0379
GEN-2020-007 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.8382 | 30.8912 | 0.053
GEN-2020-007 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2232 | 23.2777 | 0.0545
GEN-2020-007 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.0309 | 25.092 | 0.0611
GEN-2020-007 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8437 | 10.8531 | 0.0094
GEN-2020-007 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.6232 | 16.6436 | 0.0204
GEN-2020-007 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 20.9963 | 21.0435 | 0.0472
GEN-2020-007 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3249 | 9.3342 | 0.0093
GEN-2020-007 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4876 | 14.5072 | 0.0196
GEN-2020-007 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.6249 | 10.6325 | 0.0076
GEN-2020-007 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.09 | 29.1564 | 0.0664
GEN-2020-007 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8433 | 13.864 | 0.0207
GEN-2020-007 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.167 | 22.2051 | 0.0381
GEN-2020-007 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.6609 | 27.154 | 1.4931
GEN-2020-007 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.6609 | 27.154 | 1.4931
GEN-2020-007 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8129 | 2.8163 | 0.0034
GEN-2020-007 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6725 | 0.6735 | 0.001
GEN-2020-007 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6442 | 0.6451 | 0.0009
GEN-2020-007 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.9521 | 24.955 | 0.0029
GEN-2020-007 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.5227 | 23.5252 | 0.0025
GEN-2020-007 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.0892 | 23.0916 | 0.0024
GEN-2020-007 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.4711 | 24.4738 | 0.0027
GEN-2020-007 | 03 CENTRAL | 560053 | G15-052T | 345 | 12.4326 | 12.4369 | 0.0043
GEN-2020-007 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2327 | 5.2329 | 0.0002
GEN-2020-007 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.5997 | 6.6008 | 0.0011
GEN-2020-007 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.1528 | 8.1545 | 0.0017
GEN-2020-007 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.3845 | 12.3887 | 0.0042
GEN-2020-007 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4332 | 7.4336 | 0.0004
GEN-2020-007 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7916 | 7.7921 | 0.0005
GEN-2020-007 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.4549 | 29.4616 | 0.0067
GEN-2020-007 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.521 | 6.5213 | 0.0003
GEN-2020-007 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.9624 | 11.9669 | 0.0045
GEN-2020-007 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.9624 | 11.9669 | 0.0045
GEN-2020-007 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.6308 | 20.6376 | 0.0068
GEN-2020-007 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.2098 | 32.2178 | 0.008
GEN-2020-007 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.5228 | 6.5235 | 0.0007
GEN-2020-007 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 9.4224 | 9.4242 | 0.0018
GEN-2020-007 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.2601 | 27.5465 | 0.2864
GEN-2020-007 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.185 | 27.4699 | 0.2849
GEN-2020-007 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.356 | 3.3567 | 0.0007
GEN-2020-007 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9883 | 12.0113 | 0.023
GEN-2020-007 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.6736 | 17.6759 | 0.0023
GEN-2020-007 | 03 CENTRAL | 763109 | GEN-2018-079 | 138 | 6.6034 | 6.604 | 0.0006
GEN-2020-007 | 03 CENTRAL | 763113 | G18-079-TAP | 138 | 9.3922 | 9.3935 | 0.0013
GEN-2020-007 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 15.4382 | 15.4402 | 0.002
GEN-2020-007 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 18.6477 | 18.6507 | 0.003
GEN-2020-007 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.7904 | 20.9028 | 0.1124
GEN-2020-007 | 03 CENTRAL | 764390 | GEN-2020-073 | 161 | 8.3582 | 8.3619 | 0.0037
GEN-2020-007 | 03 CENTRAL | 764400 | G20-073-TAP | 161 | 8.4385 | 8.4423 | 0.0038
GEN-2020-007 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.7905 | 20.9029 | 0.1124
GEN-2020-007 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 9.0216 | 9.0335 | 0.0119
GEN-2020-007 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3429 | 10.3587 | 0.0158
GEN-2020-007 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 23.0149 | 24.6242 | 1.6093
GEN-2020-007 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.5166 | 27.1153 | 1.5987
GEN-2020-008 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 17.056 | 17.1033 | 0.0473
GEN-2020-008 | 03 CENTRAL | 515554 | BVRCNTY7 | 345 | 10.7451 | 10.8731 | 0.128
GEN-2020-008 | 03 CENTRAL | 515590 | PALDR2W7 | 345 | 9.5643 | 9.6643 | 0.1
GEN-2020-008 | 03 CENTRAL | 515618 | BALKOW 7 | 345 | 9.4267 | 9.5235 | 0.0968
GEN-2020-008 | 03 CENTRAL | 515634 | PALDR1W7 | 345 | 8.5355 | 8.614 | 0.0785
GEN-2020-008 | 03 CENTRAL | 515677 | BADGER 7 | 345 | 10.6623 | 10.7571 | 0.0948
GEN-2020-008 | 03 CENTRAL | 515686 | BLUWND 7 | 345 | 9.7906 | 9.8705 | 0.0799
GEN-2020-008 | 03 CENTRAL | 515825 | GRTWSRN7 | 345 | 8.2491 | 8.2602 | 0.0111
GEN-2020-008 | 03 CENTRAL | 515951 | PERSIMN7 | 345 | 9.8886 | 9.9045 | 0.0159
GEN-2020-008 | 03 CENTRAL | 515961 | GUTHRIE7 | 345 | 11.0917 | 11.1116 | 0.0199
GEN-2020-008 | 03 CENTRAL | 516146 | 25MILE 7 | 345 | 9.2086 | 9.2367 | 0.0281
GEN-2020-008 | 03 CENTRAL | 516159 | 25MILZ 7 | 345 | 9.1987 | 9.2268 | 0.0281
GEN-2020-008 | 03 CENTRAL | 522899 | ANTHONY 3 | 115 | 2.2969 | 2.2986 | 0.0017
GEN-2020-008 | 03 CENTRAL | 522912 | Y ROAD 3 | 115 | 4.514 | 4.5211 | 0.0071
GEN-2020-008 | 03 CENTRAL | 522914 | BOYD 3 | 115 | 4.2288 | 4.2345 | 0.0057
GEN-2020-008 | 03 CENTRAL | 522926 | BOURK 2 | 69 | 8.1527 | 8.1666 | 0.0139
GEN-2020-008 | 03 CENTRAL | 522930 | RED DEVIL 3 | 115 | 2.3909 | 2.3929 | 0.002
GEN-2020-008 | 03 CENTRAL | 522931 | REED 2 | 69 | 8.1527 | 8.1666 | 0.0139
GEN-2020-008 | 03 CENTRAL | 522935 | GOODWELL 3 | 115 | 3.4604 | 3.4646 | 0.0042
GEN-2020-008 | 03 CENTRAL | 522942 | LITTAU 3 | 115 | 2.868 | 2.8706 | 0.0026
GEN-2020-008 | 03 CENTRAL | 522952 | ROSE 3 | 115 | 1.5096 | 1.5103 | 0.0007
GEN-2020-008 | 03 CENTRAL | 523012 | TC-ANTHY_TP3 | 115 | 2.4402 | 2.442 | 0.0018
GEN-2020-008 | 03 CENTRAL | 523024 | TC-BEAVER 3 | 115 | 1.5096 | 1.5103 | 0.0007
GEN-2020-008 | 03 CENTRAL | 523089 | TC-TXCOUNTY2 | 69 | 8.1527 | 8.1666 | 0.0139
GEN-2020-008 | 03 CENTRAL | 523090 | TEXAS_CNTY 3 | 115 | 7.8731 | 7.8947 | 0.0216
GEN-2020-008 | 03 CENTRAL | 523093 | HITCHLAND 3 | 115 | 15.8245 | 15.9053 | 0.0808
GEN-2020-008 | 03 CENTRAL | 523095 | HITCHLAND 6 | 230 | 12.2259 | 12.3549 | 0.129
GEN-2020-008 | 03 CENTRAL | 523097 | HITCHLAND 7 | 345 | 10.8178 | 11.0101 | 0.1923
GEN-2020-008 | 03 CENTRAL | 523101 | NOBLE_WND 7 | 345 | 10.7858 | 10.977 | 0.1912
GEN-2020-008 | 03 CENTRAL | 523103 | NOBLE_WND 3 | 115 | 9.0413 | 9.0854 | 0.0441
GEN-2020-008 | 03 CENTRAL | 523106 | TXPHSF 3 | 115 | 4.259 | 4.2665 | 0.0075
GEN-2020-008 | 03 CENTRAL | 523111 | NOVUS1 3 | 115 | 6.4703 | 6.4928 | 0.0225
GEN-2020-008 | 03 CENTRAL | 523112 | NOVUS1 7 | 345 | 10.6531 | 10.8396 | 0.1865
GEN-2020-008 | 03 CENTRAL | 523113 | TC-MCMURRY 3 | 115 | 6.1925 | 6.2058 | 0.0133
GEN-2020-008 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.1198 | 6.1688 | 0.049
GEN-2020-008 | 03 CENTRAL | 523120 | COLE 3 | 115 | 4.2288 | 4.2345 | 0.0057
GEN-2020-008 | 03 CENTRAL | 523130 | GRPLNS-HV4-3 | 115 | 6.231 | 6.252 | 0.021
GEN-2020-008 | 03 CENTRAL | 523131 | GRPLNS-HV2-3 | 115 | 8.3073 | 8.3445 | 0.0372
GEN-2020-008 | 03 CENTRAL | 523135 | LIPSCOMB 3 | 115 | 2.7685 | 2.7708 | 0.0023
GEN-2020-008 | 03 CENTRAL | 523140 | TXFARMS 3 | 115 | 5.2274 | 5.2344 | 0.007
GEN-2020-008 | 03 CENTRAL | 523145 | WADE_TP 3 | 115 | 3.5172 | 3.5209 | 0.0037
GEN-2020-008 | 03 CENTRAL | 523147 | WADE 3 | 115 | 3.3255 | 3.3289 | 0.0034
GEN-2020-008 | 03 CENTRAL | 523154 | OCHILTREE 3 | 115 | 6.0588 | 6.07 | 0.0112
GEN-2020-008 | 03 CENTRAL | 523155 | OCHILTREE 6 | 230 | 4.1229 | 4.1356 | 0.0127
GEN-2020-008 | 03 CENTRAL | 523157 | PERRYTON 2 | 69 | 2.4556 | 2.4567 | 0.0011
GEN-2020-008 | 03 CENTRAL | 523158 | PERRYTON 3 | 115 | 5.7804 | 5.7905 | 0.0101
GEN-2020-008 | 03 CENTRAL | 523160 | FRISCO_WND 3 | 115 | 6.5733 | 6.5839 | 0.0106
GEN-2020-008 | 03 CENTRAL | 523174 | GOODWELLWND3 | 115 | 6.7317 | 6.7412 | 0.0095
GEN-2020-008 | 03 CENTRAL | 523175 | LASLEY 3 | 115 | 5.5409 | 5.5458 | 0.0049
GEN-2020-008 | 03 CENTRAL | 523177 | RB-SPURLCK+3 | 115 | 5.6621 | 5.6659 | 0.0038
GEN-2020-008 | 03 CENTRAL | 523185 | SPEARMAN 2 | 69 | 4.3036 | 4.3052 | 0.0016
GEN-2020-008 | 03 CENTRAL | 523186 | SPEARMAN 3 | 115 | 8.6829 | 8.6935 | 0.0106
GEN-2020-008 | 03 CENTRAL | 523195 | HANSFORD 3 | 115 | 9.2973 | 9.3196 | 0.0223
GEN-2020-008 | 03 CENTRAL | 523215 | GEN-2011-022 | 345 | 7.8593 | 7.9603 | 0.101
GEN-2020-008 | 03 CENTRAL | 523217 | RB-KEMP 3 | 115 | 3.9753 | 3.9765 | 0.0012
GEN-2020-008 | 03 CENTRAL | 523221 | XIT_INTG 6 | 230 | 3.2559 | 3.2571 | 0.0012
GEN-2020-008 | 03 CENTRAL | 523256 | ETTER 3 | 115 | 5.5917 | 5.5944 | 0.0027
GEN-2020-008 | 03 CENTRAL | 523267 | PRINGLE 6 | 230 | 4.4214 | 4.4229 | 0.0015
GEN-2020-008 | 03 CENTRAL | 523277 | VALERO 3 | 115 | 9.5977 | 9.606 | 0.0083
GEN-2020-008 | 03 CENTRAL | 523304 | MOORE_W 3 | 115 | 10.5632 | 10.5733 | 0.0101
GEN-2020-008 | 03 CENTRAL | 523308 | MOORE_E 3 | 115 | 10.5632 | 10.5733 | 0.0101
GEN-2020-008 | 03 CENTRAL | 523309 | MOORE_CNTY 6 | 230 | 6.7389 | 6.7493 | 0.0104
GEN-2020-008 | 03 CENTRAL | 523322 | MCDWL_CREEK3 | 115 | 10.1362 | 10.141 | 0.0048
GEN-2020-008 | 03 CENTRAL | 523323 | MCDWL_CREEK6 | 230 | 9.0802 | 9.089 | 0.0088
GEN-2020-008 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 6.359 | 6.8784 | 0.5194
GEN-2020-008 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 9.7494 | 9.8825 | 0.1331
GEN-2020-008 | 03 CENTRAL | 523869 | CHAN+TASCOS6 | 230 | 4.3823 | 4.3839 | 0.0016
GEN-2020-008 | 03 CENTRAL | 523959 | POTTER_CO 6 | 230 | 21.6771 | 21.7022 | 0.0251
GEN-2020-008 | 03 CENTRAL | 523961 | POTTER_CO 7 | 345 | 9.8265 | 9.8464 | 0.0199
GEN-2020-008 | 03 CENTRAL | 523977 | HARRNG_WST 6 | 230 | 26.7273 | 26.7471 | 0.0198
GEN-2020-008 | 03 CENTRAL | 523978 | HARRNG_MID 6 | 230 | 26.7273 | 26.7471 | 0.0198
GEN-2020-008 | 03 CENTRAL | 523979 | HARRNG_EST 6 | 230 | 26.7273 | 26.7471 | 0.0198
GEN-2020-008 | 03 CENTRAL | 524007 | ROLLHILLS 3 | 115 | 20.0833 | 20.089 | 0.0057
GEN-2020-008 | 03 CENTRAL | 524009 | CHERRY 3 | 115 | 19.218 | 19.2233 | 0.0053
GEN-2020-008 | 03 CENTRAL | 524010 | ROLLHILLS 6 | 230 | 20.0906 | 20.1057 | 0.0151
GEN-2020-008 | 03 CENTRAL | 524266 | BUSHLAND 3 | 115 | 9.7928 | 9.7942 | 0.0014
GEN-2020-008 | 03 CENTRAL | 524267 | BUSHLAND 6 | 230 | 10.1605 | 10.164 | 0.0035
GEN-2020-008 | 03 CENTRAL | 524276 | WILDOR_WND 6 | 230 | 5.3608 | 5.3616 | 0.0008
GEN-2020-008 | 03 CENTRAL | 524290 | WILDOR2_JUS6 | 230 | 7.0959 | 7.0975 | 0.0016
GEN-2020-008 | 03 CENTRAL | 524296 | SPNSPUR_WND7 | 345 | 5.1118 | 5.1163 | 0.0045
GEN-2020-008 | 03 CENTRAL | 524299 | SPNSPUR_COL7 | 345 | 5.1118 | 5.1163 | 0.0045
GEN-2020-008 | 03 CENTRAL | 524623 | DEAFSMITH 6 | 230 | 7.7773 | 7.7783 | 0.001
GEN-2020-008 | 03 CENTRAL | 524909 | ROOSEVELT 6 | 230 | 9.2888 | 9.2892 | 0.0004
GEN-2020-008 | 03 CENTRAL | 525213 | SWISHER 6 | 230 | 10.4362 | 10.4374 | 0.0012
GEN-2020-008 | 03 CENTRAL | 525460 | NEWHART 3 | 115 | 14.6145 | 14.6158 | 0.0013
GEN-2020-008 | 03 CENTRAL | 525461 | NEWHART 6 | 230 | 10.6449 | 10.6465 | 0.0016
GEN-2020-008 | 03 CENTRAL | 525481 | PLANT_X 6 | 230 | 22.1666 | 22.1695 | 0.0029
GEN-2020-008 | 03 CENTRAL | 525531 | TOLK 6 | 230 | 27.8248 | 27.829 | 0.0042
GEN-2020-008 | 03 CENTRAL | 525549 | TOLK 7 | 345 | 12.6454 | 12.6481 | 0.0027
GEN-2020-008 | 03 CENTRAL | 525584 | BLUECLDCOL 6 | 230 | 10.109 | 10.1095 | 0.0005
GEN-2020-008 | 03 CENTRAL | 525585 | BLUECLDPOI 6 | 230 | 10.6769 | 10.6774 | 0.0005
GEN-2020-008 | 03 CENTRAL | 525586 | NEEDMORE 6 | 230 | 10.6769 | 10.6774 | 0.0005
GEN-2020-008 | 03 CENTRAL | 525637 | LAMB_CNTY 6 | 230 | 5.6476 | 5.6477 | 0.0001
GEN-2020-008 | 03 CENTRAL | 525830 | TUCO_INT 6 | 230 | 21.6946 | 21.6962 | 0.0016
GEN-2020-008 | 03 CENTRAL | 525840 | ANTELOPE_1 6 | 230 | 21.5213 | 21.5229 | 0.0016
GEN-2020-008 | 03 CENTRAL | 525957 | HALE_WNDCL16 | 230 | 10.7509 | 10.7512 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527598 | SAGA_NDCOL 7 | 345 | 7.4961 | 7.4964 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527599 | SAGA_SDCOL 7 | 345 | 8.6891 | 8.6895 | 0.0004
GEN-2020-008 | 03 CENTRAL | 527600 | SAGA_SMEAS 7 | 345 | 8.6891 | 8.6895 | 0.0004
GEN-2020-008 | 03 CENTRAL | 527601 | SAGA_NCOL 7 | 345 | 7.4961 | 7.4964 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527610 | SAGA_SCOL 7 | 345 | 8.6891 | 8.6895 | 0.0004
GEN-2020-008 | 03 CENTRAL | 527654 | RSVLT_CC_W 7 | 345 | 8.0122 | 8.0125 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527655 | RSVLT_CC_E 7 | 345 | 8.9822 | 8.9826 | 0.0004
GEN-2020-008 | 03 CENTRAL | 527656 | CROSSROADS 7 | 345 | 10.056 | 10.0566 | 0.0006
GEN-2020-008 | 03 CENTRAL | 527666 | RSVLT_COL1 7 | 345 | 8.0122 | 8.0125 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527667 | RSVLT_COL2 7 | 345 | 8.0122 | 8.0125 | 0.0003
GEN-2020-008 | 03 CENTRAL | 527802 | EDDY_CNTY 7 | 345 | 7.2881 | 7.2882 | 0.0001
GEN-2020-008 | 03 CENTRAL | 527896 | HOBBS_INT 7 | 345 | 12.0346 | 12.0349 | 0.0003
GEN-2020-008 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 7.9905 | 7.9945 | 0.004
GEN-2020-008 | 03 CENTRAL | 531210 | BLUEJAY3 | 115 | 2.2109 | 2.2123 | 0.0014
GEN-2020-008 | 03 CENTRAL | 531211 | CHRLSTN3 | 115 | 2.1472 | 2.1485 | 0.0013
GEN-2020-008 | 03 CENTRAL | 531212 | TWNSPRG3 | 115 | 1.6704 | 1.6712 | 0.0008
GEN-2020-008 | 03 CENTRAL | 531213 | SANTAFE3 | 115 | 2.8188 | 2.821 | 0.0022
GEN-2020-008 | 03 CENTRAL | 531375 | PUCKET 3 | 115 | 5.0605 | 5.0731 | 0.0126
GEN-2020-008 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.9232 | 10.9466 | 0.0234
GEN-2020-008 | 03 CENTRAL | 531380 | HUGOTON2 | 69 | 2.9767 | 2.9869 | 0.0102
GEN-2020-008 | 03 CENTRAL | 531384 | MOSCOW 2 | 69 | 2.2384 | 2.2464 | 0.008
GEN-2020-008 | 03 CENTRAL | 531385 | MOSCOWT2 | 69 | 2.3545 | 2.3633 | 0.0088
GEN-2020-008 | 03 CENTRAL | 531388 | NORTH6 2 | 69 | 2.6481 | 2.6594 | 0.0113
GEN-2020-008 | 03 CENTRAL | 531389 | NORTH6T2 | 69 | 3.0977 | 3.1132 | 0.0155
GEN-2020-008 | 03 CENTRAL | 531392 | PIONTAP3 | 115 | 6.9694 | 6.986 | 0.0166
GEN-2020-008 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.9815 | 7.9987 | 0.0172
GEN-2020-008 | 03 CENTRAL | 531395 | ROLLA 2 | 115 | 2.6434 | 2.6571 | 0.0137
GEN-2020-008 | 03 CENTRAL | 531398 | SUBLETE3 | 115 | 6.2236 | 6.2368 | 0.0132
GEN-2020-008 | 03 CENTRAL | 531400 | PK_GOAB3 | 115 | 5.0746 | 5.0872 | 0.0126
GEN-2020-008 | 03 CENTRAL | 531404 | WALKMYR2 | 69 | 8.6584 | 8.7791 | 0.1207
GEN-2020-008 | 03 CENTRAL | 531405 | WALKMYR3 | 115 | 10.1561 | 10.4393 | 0.2832
GEN-2020-008 | 03 CENTRAL | 531406 | WOODS 2 | 69 | 6.3688 | 6.4351 | 0.0663
GEN-2020-008 | 03 CENTRAL | 531407 | INGALLS3 | 115 | 2.8173 | 2.8195 | 0.0022
GEN-2020-008 | 03 CENTRAL | 531408 | PIERCVL3 | 115 | 4.0387 | 4.0431 | 0.0044
GEN-2020-008 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 7.0203 | 7.0363 | 0.016
GEN-2020-008 | 03 CENTRAL | 531423 | GARDNCY2 | 69 | 3.7454 | 3.7468 | 0.0014
GEN-2020-008 | 03 CENTRAL | 531426 | JAMESON3 | 115 | 10.3802 | 10.4007 | 0.0205
GEN-2020-008 | 03 CENTRAL | 531429 | MINGO 3 | 115 | 12.722 | 12.7397 | 0.0177
GEN-2020-008 | 03 CENTRAL | 531433 | SCOTCTY3 | 115 | 9.0389 | 9.0565 | 0.0176
GEN-2020-008 | 03 CENTRAL | 531440 | WILLIAM3 | 115 | 3.9273 | 3.9323 | 0.005
GEN-2020-008 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.9414 | 12.9686 | 0.0272
GEN-2020-008 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.3443 | 21.4443 | 0.1
GEN-2020-008 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 9.8638 | 9.9961 | 0.1323
GEN-2020-008 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.2324 | 6.2463 | 0.0139
GEN-2020-008 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.5736 | 10.5992 | 0.0256
GEN-2020-008 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.0241 | 7.0655 | 0.0414
GEN-2020-008 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 14.0909 | 14.1268 | 0.0359
GEN-2020-008 | 03 CENTRAL | 531476 | SWNDTAP3 | 115 | 7.4951 | 7.504 | 0.0089
GEN-2020-008 | 03 CENTRAL | 531477 | S. WIND3 | 115 | 6.9057 | 6.9133 | 0.0076
GEN-2020-008 | 03 CENTRAL | 531479 | CHUGTON2 | 69 | 2.6797 | 2.688 | 0.0083
GEN-2020-008 | 03 CENTRAL | 531480 | KSAVWTP3 | 115 | 12.5755 | 12.6013 | 0.0258
GEN-2020-008 | 03 CENTRAL | 531481 | HUGOTON3 | 115 | 5.8298 | 5.8966 | 0.0668
GEN-2020-008 | 03 CENTRAL | 531483 | GRANTTP3 | 115 | 5.0218 | 5.0484 | 0.0266
GEN-2020-008 | 03 CENTRAL | 531484 | GRANT 3 | 115 | 4.7314 | 4.7551 | 0.0237
GEN-2020-008 | 03 CENTRAL | 531485 | CNTRLPL3 | 115 | 6.1506 | 6.1586 | 0.008
GEN-2020-008 | 03 CENTRAL | 531494 | ABBK 2 | 115 | 5.2473 | 5.3014 | 0.0541
GEN-2020-008 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 9.4661 | 9.5208 | 0.0547
GEN-2020-008 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 7.516 | 7.5504 | 0.0344
GEN-2020-008 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 7.6407 | 7.6756 | 0.0349
GEN-2020-008 | 03 CENTRAL | 531510 | HARBNGR3 | 115 | 10.7496 | 11.09 | 0.3404
GEN-2020-008 | 03 CENTRAL | 531512 | HARBNGR7 | 345 | 6.3414 | 6.8573 | 0.5159
GEN-2020-008 | 03 CENTRAL | 531623 | EASTFORK3 | 115 | 10.1015 | 10.1124 | 0.0109
GEN-2020-008 | 03 CENTRAL | 531632 | GEN-2015-065 | 345 | 5.5206 | 5.5312 | 0.0106
GEN-2020-008 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.707 | 12.7228 | 0.0158
GEN-2020-008 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.8161 | 10.8275 | 0.0114
GEN-2020-008 | 03 CENTRAL | 539640 | HAYNE3 | 115 | 5.6527 | 5.6758 | 0.0231
GEN-2020-008 | 03 CENTRAL | 539652 | CMRIVTP3 | 115 | 6.0692 | 6.0936 | 0.0244
GEN-2020-008 | 03 CENTRAL | 539654 | CIM-PLT3 | 115 | 6.8153 | 6.8499 | 0.0346
GEN-2020-008 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 13.0356 | 13.0523 | 0.0167
GEN-2020-008 | 03 CENTRAL | 539749 | N-CIMRN3 | 115 | 6.7365 | 6.77 | 0.0335
GEN-2020-008 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.403 | 13.414 | 0.011
GEN-2020-008 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 13.5818 | 13.6139 | 0.0321
GEN-2020-008 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.2548 | 12.2809 | 0.0261
GEN-2020-008 | 03 CENTRAL | 560071 | G16-003-TAP | 345 | 12.9253 | 12.9809 | 0.0556
GEN-2020-008 | 03 CENTRAL | 560577 | G06-44 | 115 | 6.4703 | 6.4928 | 0.0225
GEN-2020-008 | 03 CENTRAL | 576395 | GEN-2010-014 | 345 | 7.8593 | 7.9603 | 0.101
GEN-2020-008 | 03 CENTRAL | 576397 | G10014G11022 | 345 | 7.8593 | 7.9603 | 0.101
GEN-2020-008 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 13.123 | 13.1529 | 0.0299
GEN-2020-008 | 03 CENTRAL | 585190 | GEN-2015-082 | 345 | 6.0554 | 6.0858 | 0.0304
GEN-2020-008 | 03 CENTRAL | 585440 | PRSIMN_CRK2 | 345 | 9.1446 | 9.1582 | 0.0136
GEN-2020-008 | 03 CENTRAL | 588560 | GEN-2017-011 | 345 | 10.8062 | 10.8451 | 0.0389
GEN-2020-008 | 03 CENTRAL | 588860 | GEN-2017-047 | 115 | 4.1408 | 4.1463 | 0.0055
GEN-2020-008 | 03 CENTRAL | 589380 | GEN-2017-100 | 115 | 4.8047 | 4.8127 | 0.008
GEN-2020-008 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4743 | 2.4828 | 0.0085
GEN-2020-008 | 03 CENTRAL | 599955 | PNM-DC6 | 230 | 9.2888 | 9.2892 | 0.0004
GEN-2020-008 | 03 CENTRAL | 640325 | REDWILO3 | 345 | 6.3827 | 6.3869 | 0.0042
GEN-2020-008 | 03 CENTRAL | 762132 | GEN-2017-158 | 230 | 12.3173 | 12.3181 | 0.0008
GEN-2020-008 | 03 CENTRAL | 762471 | GEN-2018-009 | 115 | 3.2051 | 3.2101 | 0.005
GEN-2020-008 | 03 CENTRAL | 763186 | GEN-2018-089 | 230 | 10.3475 | 10.349 | 0.0015
GEN-2020-008 | 03 CENTRAL | 763483 | GEN-2019-003 | 230 | 8.3325 | 8.3328 | 0.0003
GEN-2020-008 | 03 CENTRAL | 763527 | GEN-2019-012 | 345 | 15.2797 | 15.3176 | 0.0379
GEN-2020-008 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.8321 | 9.8456 | 0.0135
GEN-2020-008 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 11.9686 | 11.989 | 0.0204
GEN-2020-008 | 03 CENTRAL | 764825 | GEN-2020-017 | 230 | 5.6297 | 5.6298 | 0.0001
GEN-2020-008 | 03 CENTRAL | 764980 | GEN-2020-008 | 345 | 6.359 | 6.8784 | 0.5194
GEN-2020-056 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.2307 | 3.2311 | 0.0004
GEN-2020-056 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.8012 | 8.804 | 0.0028
GEN-2020-056 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 9.1018 | 9.1111 | 0.0093
GEN-2020-056 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 7.0306 | 7.036 | 0.0054
GEN-2020-056 | 03 CENTRAL | 530571 | SUSANK 2 | 69 | 1.6718 | 1.6721 | 0.0003
GEN-2020-056 | 03 CENTRAL | 530572 | BNK HL 2 | 69 | 1.2691 | 1.2693 | 0.0002
GEN-2020-056 | 03 CENTRAL | 530573 | HITHMN 2 | 69 | 1.1504 | 1.1506 | 0.0002
GEN-2020-056 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 9.1693 | 9.1753 | 0.006
GEN-2020-056 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.1288 | 11.1342 | 0.0054
GEN-2020-056 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.7952 | 3.7966 | 0.0014
GEN-2020-056 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 6.2001 | 6.2043 | 0.0042
GEN-2020-056 | 03 CENTRAL | 530588 | WSTPRT 2 | 69 | 5.1549 | 5.1578 | 0.0029
GEN-2020-056 | 03 CENTRAL | 530589 | BKHLTAP2 | 69 | 1.5088 | 1.509 | 0.0002
GEN-2020-056 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 12.6076 | 12.6408 | 0.0332
GEN-2020-056 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 4.2792 | 4.2815 | 0.0023
GEN-2020-056 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.7079 | 3.7096 | 0.0017
GEN-2020-056 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 4.1553 | 4.1571 | 0.0018
GEN-2020-056 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 8.0937 | 8.1073 | 0.0136
GEN-2020-056 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 3.5778 | 3.5785 | 0.0007
GEN-2020-056 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 5.2578 | 5.2613 | 0.0035
GEN-2020-056 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 9.0688 | 9.0837 | 0.0149
GEN-2020-056 | 03 CENTRAL | 530681 | BUSHTON3 | 115 | 5.1228 | 5.1376 | 0.0148
GEN-2020-056 | 03 CENTRAL | 530684 | RUSLPMP3 | 115 | 2.1111 | 2.1112 | 0.0001
GEN-2020-056 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.1759 | 8.1787 | 0.0028
GEN-2020-056 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.435 | 5.4361 | 0.0011
GEN-2020-056 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.5645 | 3.565 | 0.0005
GEN-2020-056 | 03 CENTRAL | 531373 | RHOADES3 | 115 | 3.2783 | 3.2795 | 0.0012
GEN-2020-056 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.8004 | 8.8081 | 0.0077
GEN-2020-056 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.7204 | 12.7228 | 0.0024
GEN-2020-056 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.8258 | 10.8275 | 0.0017
GEN-2020-056 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 4.0958 | 4.1863 | 0.0905
GEN-2020-056 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.7538 | 3.8196 | 0.0658
GEN-2020-056 | 03 CENTRAL | 539644 | COVERT 3 | 115 | 2.7382 | 2.7697 | 0.0315
GEN-2020-056 | 03 CENTRAL | 539647 | IONIA 3 | 115 | 3.0712 | 3.0756 | 0.0044
GEN-2020-056 | 03 CENTRAL | 539650 | BELOIT 3 | 115 | 3.3072 | 3.3097 | 0.0025
GEN-2020-056 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.383 | 3.412 | 0.029
GEN-2020-056 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 8.7064 | 8.7202 | 0.0138
GEN-2020-056 | 03 CENTRAL | 539662 | ELLSWTH3 | 115 | 3.6071 | 3.6284 | 0.0213
GEN-2020-056 | 03 CENTRAL | 539663 | GLENELD3 | 115 | 2.917 | 2.92 | 0.003
GEN-2020-056 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 8.9767 | 8.9914 | 0.0147
GEN-2020-056 | 03 CENTRAL | 539669 | JEWELL 3 | 115 | 3.257 | 3.26 | 0.003
GEN-2020-056 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 12.7066 | 12.7418 | 0.0352
GEN-2020-056 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 9.128 | 9.143 | 0.015
GEN-2020-056 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 9.6032 | 9.6219 | 0.0187
GEN-2020-056 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 3.0597 | 3.0617 | 0.002
GEN-2020-056 | 03 CENTRAL | 539685 | PHLBURG3 | 115 | 3.5736 | 3.5772 | 0.0036
GEN-2020-056 | 03 CENTRAL | 539686 | PLAINVL3 | 115 | 3.769 | 3.7704 | 0.0014
GEN-2020-056 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 8.5921 | 8.6055 | 0.0134
GEN-2020-056 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.9471 | 5.9516 | 0.0045
GEN-2020-056 | 03 CENTRAL | 539693 | SMITH-C3 | 115 | 3.9148 | 3.9267 | 0.0119
GEN-2020-056 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 13.0498 | 13.0523 | 0.0025
GEN-2020-056 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 5.1929 | 5.1947 | 0.0018
GEN-2020-056 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.862 | 2.9054 | 0.0434
GEN-2020-056 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.5902 | 3.6911 | 0.1009
GEN-2020-056 | 03 CENTRAL | 763329 | GEN-2018-116 | 115 | 8.6883 | 8.702 | 0.0137
GEN-2020-056 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 7.4061 | 7.4089 | 0.0028
GEN-2020-056 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 7.4946 | 7.4976 | 0.003
GEN-2020-056 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 7.1873 | 7.1952 | 0.0079
GEN-2020-056 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 7.2698 | 7.2779 | 0.0081
GEN-2020-056 | 03 CENTRAL | 765010 | GEN-2020-056 | 115 | 3.5747 | 3.6755 | 0.1008
GEN-2020-057 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 12.933 | 12.9346 | 0.0016
GEN-2020-057 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.2765 | 16.2782 | 0.0017
GEN-2020-057 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5711 | 24.5713 | 0.0002
GEN-2020-057 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.1972 | 13.1981 | 0.0009
GEN-2020-057 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.4778 | 11.478 | 0.0002
GEN-2020-057 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.0567 | 12.0572 | 0.0005
GEN-2020-057 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.1715 | 19.1718 | 0.0003
GEN-2020-057 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.0781 | 16.0914 | 0.0133
GEN-2020-057 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 22.1764 | 22.1884 | 0.012
GEN-2020-057 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5694 | 16.5846 | 0.0152
GEN-2020-057 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3895 | 16.4043 | 0.0148
GEN-2020-057 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.7688 | 12.7759 | 0.0071
GEN-2020-057 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 27.2864 | 27.3672 | 0.0808
GEN-2020-057 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.6837 | 16.7394 | 0.0557
GEN-2020-057 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 20.8604 | 21.0589 | 0.1985
GEN-2020-057 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8788 | 13.8894 | 0.0106
GEN-2020-057 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9325 | 11.9338 | 0.0013
GEN-2020-057 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.037 | 11.0381 | 0.0011
GEN-2020-057 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7659 | 9.7665 | 0.0006
GEN-2020-057 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4949 | 9.4954 | 0.0005
GEN-2020-057 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.2252 | 18.2288 | 0.0036
GEN-2020-057 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.6777 | 23.6806 | 0.0029
GEN-2020-057 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.1986 | 18.2036 | 0.005
GEN-2020-057 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.2222 | 16.2276 | 0.0054
GEN-2020-057 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5678 | 13.5715 | 0.0037
GEN-2020-057 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.4127 | 10.415 | 0.0023
GEN-2020-057 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.5687 | 13.5784 | 0.0097
GEN-2020-057 | 03 CENTRAL | 532852 | JEC 6 | 230 | 23.4301 | 23.4384 | 0.0083
GEN-2020-057 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.0049 | 14.016 | 0.0111
GEN-2020-057 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.8752 | 13.8861 | 0.0109
GEN-2020-057 | 03 CENTRAL | 532855 | MIDLAND6 | 230 | 12.4442 | 12.4532 | 0.009
GEN-2020-057 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.6969 | 21.739 | 0.0421
GEN-2020-057 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.0167 | 11.0257 | 0.009
GEN-2020-057 | 03 CENTRAL | 532862 | MCDOWEL6 | 230 | 7.2233 | 7.2246 | 0.0013
GEN-2020-057 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0326 | 14.0386 | 0.006
GEN-2020-057 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.2671 | 8.2681 | 0.001
GEN-2020-057 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.8878 | 4.8881 | 0.0003
GEN-2020-057 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1649 | 11.1769 | 0.012
GEN-2020-057 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2089 | 8.2093 | 0.0004
GEN-2020-057 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7921 | 23.7942 | 0.0021
GEN-2020-057 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.3832 | 25.3852 | 0.002
GEN-2020-057 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4264 | 25.4284 | 0.002
GEN-2020-057 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.3076 | 25.3096 | 0.002
GEN-2020-057 | 03 CENTRAL | 533151 | AUBURN 3 | 115 | 21.7032 | 21.7148 | 0.0116
GEN-2020-057 | 03 CENTRAL | 533155 | CROOKED3 | 115 | 20.5452 | 20.5555 | 0.0103
GEN-2020-057 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 23.2328 | 23.2431 | 0.0103
GEN-2020-057 | 03 CENTRAL | 533182 | TECHILE3 | 115 | 25.1372 | 25.155 | 0.0178
GEN-2020-057 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.3976 | 8.3999 | 0.0023
GEN-2020-057 | 03 CENTRAL | 533236 | FAIRGDS3 | 115 | 18.9172 | 18.9303 | 0.0131
GEN-2020-057 | 03 CENTRAL | 533240 | EUDORA 3 | 115 | 11.8889 | 11.8962 | 0.0073
GEN-2020-057 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.1445 | 27.174 | 0.0295
GEN-2020-057 | 03 CENTRAL | 533250 | LWRNCHL3 | 115 | 26.9215 | 26.944 | 0.0225
GEN-2020-057 | 03 CENTRAL | 533254 | MOONLIT3 | 115 | 11.3104 | 11.3221 | 0.0117
GEN-2020-057 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.5412 | 17.5524 | 0.0112
GEN-2020-057 | 03 CENTRAL | 533261 | PENTAGN3 | 115 | 22.3777 | 22.4125 | 0.0348
GEN-2020-057 | 03 CENTRAL | 533265 | SOUTHTN3 | 115 | 11.3836 | 11.3949 | 0.0113
GEN-2020-057 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.238 | 37.2898 | 0.0518
GEN-2020-057 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.4746 | 16.4848 | 0.0102
GEN-2020-057 | 03 CENTRAL | 533273 | TIMBRLN3 | 115 | 13.6053 | 13.622 | 0.0167
GEN-2020-057 | 03 CENTRAL | 533278 | WAVERLY3 | 115 | 14.7557 | 14.7763 | 0.0206
GEN-2020-057 | 03 CENTRAL | 533281 | MNTCLLO3 | 115 | 23.4022 | 23.4487 | 0.0465
GEN-2020-057 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.5001 | 27.5727 | 0.0726
GEN-2020-057 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.6198 | 15.6239 | 0.0041
GEN-2020-057 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 12.9467 | 12.9492 | 0.0025
GEN-2020-057 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8781 | 3.8782 | 0.0001
GEN-2020-057 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.457 | 3.457 | 0
GEN-2020-057 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0526 | 24.0535 | 0.0009
GEN-2020-057 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.6691 | 20.748 | 0.0789
GEN-2020-057 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.8175 | 18.8625 | 0.045
GEN-2020-057 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.3808 | 21.4074 | 0.0266
GEN-2020-057 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 14.2479 | 14.2566 | 0.0087
GEN-2020-057 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 33.4841 | 33.5175 | 0.0334
GEN-2020-057 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.3938 | 19.4192 | 0.0254
GEN-2020-057 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 20.4413 | 20.4689 | 0.0276
GEN-2020-057 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 22.8105 | 22.8468 | 0.0363
GEN-2020-057 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.561 | 4.5614 | 0.0004
GEN-2020-057 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.2346 | 21.2654 | 0.0308
GEN-2020-057 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5661 | 15.573 | 0.0069
GEN-2020-057 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 18.9926 | 19.0054 | 0.0128
GEN-2020-057 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.0669 | 19.088 | 0.0211
GEN-2020-057 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6771 | 2.6772 | 0.0001
GEN-2020-057 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.2433 | 20.9429 | 0.6996
GEN-2020-057 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 34.4952 | 34.6829 | 0.1877
GEN-2020-057 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.1272 | 27.1958 | 0.0686
GEN-2020-057 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.5222 | 30.5801 | 0.0579
GEN-2020-057 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.1616 | 27.6185 | 0.4569
GEN-2020-057 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.0007 | 30.1269 | 0.1262
GEN-2020-057 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.6714 | 25.8373 | 0.1659
GEN-2020-057 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.8268 | 40.9756 | 0.1488
GEN-2020-057 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 21.865 | 22.1427 | 0.2777
GEN-2020-057 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 43.0972 | 43.3904 | 0.2932
GEN-2020-057 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 29.7314 | 29.8481 | 0.1167
GEN-2020-057 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.757 | 23.7859 | 0.0289
GEN-2020-057 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8076 | 27.8947 | 0.0871
GEN-2020-057 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.6668 | 30.7241 | 0.0573
GEN-2020-057 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.072 | 37.1574 | 0.0854
GEN-2020-057 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.9746 | 20.0023 | 0.0277
GEN-2020-057 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.1366 | 25.1791 | 0.0425
GEN-2020-057 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 36.4675 | 36.5991 | 0.1316
GEN-2020-057 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.1807 | 32.2773 | 0.0966
GEN-2020-057 | 03 CENTRAL | 543033 | BRKRIDG5 | 161 | 24.3672 | 24.4349 | 0.0677
GEN-2020-057 | 03 CENTRAL | 543034 | KNLWRTH5 | 161 | 27.2721 | 27.3486 | 0.0765
GEN-2020-057 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.3144 | 27.4113 | 0.0969
GEN-2020-057 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.1862 | 16.2208 | 0.0346
GEN-2020-057 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 36.9233 | 37.1132 | 0.1899
GEN-2020-057 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 27.5516 | 27.6161 | 0.0645
GEN-2020-057 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 17.8366 | 17.879 | 0.0424
GEN-2020-057 | 03 CENTRAL | 543045 | SWITZER5 | 161 | 19.7838 | 19.8324 | 0.0486
GEN-2020-057 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.2751 | 21.3275 | 0.0524
GEN-2020-057 | 03 CENTRAL | 543047 | OVERLPK5 | 161 | 32.4429 | 32.5602 | 0.1173
GEN-2020-057 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.3176 | 30.4527 | 0.1351
GEN-2020-057 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.7552 | 30.8912 | 0.136
GEN-2020-057 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2227 | 23.2777 | 0.055
GEN-2020-057 | 03 CENTRAL | 543052 | REEDER 5 | 161 | 21.2892 | 21.3422 | 0.053
GEN-2020-057 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.0434 | 25.092 | 0.0486
GEN-2020-057 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8366 | 10.8531 | 0.0165
GEN-2020-057 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 8.2121 | 8.2167 | 0.0046
GEN-2020-057 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.607 | 16.6436 | 0.0366
GEN-2020-057 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0077 | 21.0435 | 0.0358
GEN-2020-057 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3271 | 9.3342 | 0.0071
GEN-2020-057 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4921 | 14.5072 | 0.0151
GEN-2020-057 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.6207 | 10.6325 | 0.0118
GEN-2020-057 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.0404 | 29.1564 | 0.116
GEN-2020-057 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8459 | 13.864 | 0.0181
GEN-2020-057 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.1378 | 22.2051 | 0.0673
GEN-2020-057 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.9971 | 7.0004 | 0.0033
GEN-2020-057 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.0715 | 27.154 | 0.0825
GEN-2020-057 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.0715 | 27.154 | 0.0825
GEN-2020-057 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8161 | 2.8163 | 0.0002
GEN-2020-057 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6734 | 0.6735 | 0.0001
GEN-2020-057 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.645 | 0.6451 | 0.0001
GEN-2020-057 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.0867 | 27.1379 | 0.0512
GEN-2020-057 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.5999 | 6.6008 | 0.0009
GEN-2020-057 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.1531 | 8.1545 | 0.0014
GEN-2020-057 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 3.6326 | 3.633 | 0.0004
GEN-2020-057 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 6.1498 | 6.1519 | 0.0021
GEN-2020-057 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 5.1615 | 5.1628 | 0.0013
GEN-2020-057 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 3.4321 | 3.4324 | 0.0003
GEN-2020-057 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.523 | 6.5235 | 0.0005
GEN-2020-057 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 9.4229 | 9.4242 | 0.0013
GEN-2020-057 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.0921 | 27.5465 | 0.4544
GEN-2020-057 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.018 | 27.4699 | 0.4519
GEN-2020-057 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.3556 | 3.3567 | 0.0011
GEN-2020-057 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 12.0098 | 12.0113 | 0.0015
GEN-2020-057 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 15.44 | 15.4402 | 0.0002
GEN-2020-057 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 18.6505 | 18.6507 | 0.0002
GEN-2020-057 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.2059 | 20.9028 | 0.6969
GEN-2020-057 | 03 CENTRAL | 764390 | GEN-2020-073 | 161 | 8.357 | 8.3619 | 0.0049
GEN-2020-057 | 03 CENTRAL | 764400 | G20-073-TAP | 161 | 8.4372 | 8.4423 | 0.0051
GEN-2020-057 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.2033 | 20.9029 | 0.6996
GEN-2020-057 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 9.0328 | 9.0335 | 0.0007
GEN-2020-057 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3577 | 10.3587 | 0.001
GEN-2020-057 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.5584 | 24.6242 | 0.0658
GEN-2020-057 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 27.0345 | 27.1153 | 0.0808
GEN-2020-058 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 12.9331 | 12.9346 | 0.0015
GEN-2020-058 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.2766 | 16.2782 | 0.0016
GEN-2020-058 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5711 | 24.5713 | 0.0002
GEN-2020-058 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.1972 | 13.1981 | 0.0009
GEN-2020-058 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.4778 | 11.478 | 0.0002
GEN-2020-058 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.0568 | 12.0572 | 0.0004
GEN-2020-058 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.1715 | 19.1718 | 0.0003
GEN-2020-058 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 16.0786 | 16.0914 | 0.0128
GEN-2020-058 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 22.1769 | 22.1884 | 0.0115
GEN-2020-058 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.57 | 16.5846 | 0.0146
GEN-2020-058 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.3901 | 16.4043 | 0.0142
GEN-2020-058 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.7691 | 12.7759 | 0.0068
GEN-2020-058 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 27.2898 | 27.3672 | 0.0774
GEN-2020-058 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.686 | 16.7394 | 0.0534
GEN-2020-058 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 20.8687 | 21.0589 | 0.1902
GEN-2020-058 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8792 | 13.8894 | 0.0102
GEN-2020-058 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9326 | 11.9338 | 0.0012
GEN-2020-058 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.037 | 11.0381 | 0.0011
GEN-2020-058 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7659 | 9.7665 | 0.0006
GEN-2020-058 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4949 | 9.4954 | 0.0005
GEN-2020-058 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.2253 | 18.2288 | 0.0035
GEN-2020-058 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.6778 | 23.6806 | 0.0028
GEN-2020-058 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.1988 | 18.2036 | 0.0048
GEN-2020-058 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.2225 | 16.2276 | 0.0051
GEN-2020-058 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.568 | 13.5715 | 0.0035
GEN-2020-058 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.4128 | 10.415 | 0.0022
GEN-2020-058 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.5692 | 13.5784 | 0.0092
GEN-2020-058 | 03 CENTRAL | 532852 | JEC 6 | 230 | 23.4305 | 23.4384 | 0.0079
GEN-2020-058 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 14.0053 | 14.016 | 0.0107
GEN-2020-058 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.8756 | 13.8861 | 0.0105
GEN-2020-058 | 03 CENTRAL | 532855 | MIDLAND6 | 230 | 12.4446 | 12.4532 | 0.0086
GEN-2020-058 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.6986 | 21.739 | 0.0404
GEN-2020-058 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 11.0171 | 11.0257 | 0.0086
GEN-2020-058 | 03 CENTRAL | 532862 | MCDOWEL6 | 230 | 7.2234 | 7.2246 | 0.0012
GEN-2020-058 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 14.0329 | 14.0386 | 0.0057
GEN-2020-058 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.2672 | 8.2681 | 0.0009
GEN-2020-058 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.8878 | 4.8881 | 0.0003
GEN-2020-058 | 03 CENTRAL | 532914 | SPRGHL 5 | 161 | 11.1654 | 11.1769 | 0.0115
GEN-2020-058 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2089 | 8.2093 | 0.0004
GEN-2020-058 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7922 | 23.7942 | 0.002
GEN-2020-058 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.3833 | 25.3852 | 0.0019
GEN-2020-058 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4264 | 25.4284 | 0.002
GEN-2020-058 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.3077 | 25.3096 | 0.0019
GEN-2020-058 | 03 CENTRAL | 533151 | AUBURN 3 | 115 | 21.7037 | 21.7148 | 0.0111
GEN-2020-058 | 03 CENTRAL | 533155 | CROOKED3 | 115 | 20.5456 | 20.5555 | 0.0099
GEN-2020-058 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 23.2333 | 23.2431 | 0.0098
GEN-2020-058 | 03 CENTRAL | 533182 | TECHILE3 | 115 | 25.138 | 25.155 | 0.017
GEN-2020-058 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.3977 | 8.3999 | 0.0022
GEN-2020-058 | 03 CENTRAL | 533236 | FAIRGDS3 | 115 | 18.9178 | 18.9303 | 0.0125
GEN-2020-058 | 03 CENTRAL | 533240 | EUDORA 3 | 115 | 11.8893 | 11.8962 | 0.0069
GEN-2020-058 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 27.1457 | 27.174 | 0.0283
GEN-2020-058 | 03 CENTRAL | 533250 | LWRNCHL3 | 115 | 26.9225 | 26.944 | 0.0215
GEN-2020-058 | 03 CENTRAL | 533254 | MOONLIT3 | 115 | 11.3109 | 11.3221 | 0.0112
GEN-2020-058 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 17.5416 | 17.5524 | 0.0108
GEN-2020-058 | 03 CENTRAL | 533261 | PENTAGN3 | 115 | 22.3792 | 22.4125 | 0.0333
GEN-2020-058 | 03 CENTRAL | 533265 | SOUTHTN3 | 115 | 11.3841 | 11.3949 | 0.0108
GEN-2020-058 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 37.2402 | 37.2898 | 0.0496
GEN-2020-058 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 16.4751 | 16.4848 | 0.0097
GEN-2020-058 | 03 CENTRAL | 533273 | TIMBRLN3 | 115 | 13.606 | 13.622 | 0.016
GEN-2020-058 | 03 CENTRAL | 533278 | WAVERLY3 | 115 | 14.7566 | 14.7763 | 0.0197
GEN-2020-058 | 03 CENTRAL | 533281 | MNTCLLO3 | 115 | 23.4041 | 23.4487 | 0.0446
GEN-2020-058 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 27.5031 | 27.5727 | 0.0696
GEN-2020-058 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.62 | 15.6239 | 0.0039
GEN-2020-058 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 12.9468 | 12.9492 | 0.0024
GEN-2020-058 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.8781 | 3.8782 | 0.0001
GEN-2020-058 | 03 CENTRAL | 533360 | TCHOPE 3 | 115 | 3.457 | 3.457 | 0
GEN-2020-058 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0526 | 24.0535 | 0.0009
GEN-2020-058 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.6724 | 20.748 | 0.0756
GEN-2020-058 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.8194 | 18.8625 | 0.0431
GEN-2020-058 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 21.382 | 21.4074 | 0.0254
GEN-2020-058 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 14.2483 | 14.2566 | 0.0083
GEN-2020-058 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 33.4855 | 33.5175 | 0.032
GEN-2020-058 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 19.3949 | 19.4192 | 0.0243
GEN-2020-058 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 20.4424 | 20.4689 | 0.0265
GEN-2020-058 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 22.812 | 22.8468 | 0.0348
GEN-2020-058 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.561 | 4.5614 | 0.0004
GEN-2020-058 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 21.2359 | 21.2654 | 0.0295
GEN-2020-058 | 03 CENTRAL | 541350 | IATAN5 | 161 | 15.5664 | 15.573 | 0.0066
GEN-2020-058 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 18.9931 | 19.0054 | 0.0123
GEN-2020-058 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 19.0678 | 19.088 | 0.0202
GEN-2020-058 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6771 | 2.6772 | 0.0001
GEN-2020-058 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.2718 | 20.9429 | 0.6711
GEN-2020-058 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 34.5031 | 34.6829 | 0.1798
GEN-2020-058 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.1301 | 27.1958 | 0.0657
GEN-2020-058 | 03 CENTRAL | 542950 | STHTOWN_CAP5 | 161 | 30.5246 | 30.5801 | 0.0555
GEN-2020-058 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.1805 | 27.6185 | 0.438
GEN-2020-058 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.006 | 30.1269 | 0.1209
GEN-2020-058 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.6784 | 25.8373 | 0.1589
GEN-2020-058 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.833 | 40.9756 | 0.1426
GEN-2020-058 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 21.8766 | 22.1427 | 0.2661
GEN-2020-058 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 43.1095 | 43.3904 | 0.2809
GEN-2020-058 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 29.7363 | 29.8481 | 0.1118
GEN-2020-058 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.7582 | 23.7859 | 0.0277
GEN-2020-058 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8113 | 27.8947 | 0.0834
GEN-2020-058 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.6692 | 30.7241 | 0.0549
GEN-2020-058 | 03 CENTRAL | 542993 | STHTOWN5 | 161 | 37.0756 | 37.1574 | 0.0818
GEN-2020-058 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.9758 | 20.0023 | 0.0265
GEN-2020-058 | 03 CENTRAL | 543002 | MARTCIT5 | 161 | 25.1384 | 25.1791 | 0.0407
GEN-2020-058 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 36.4731 | 36.5991 | 0.126
GEN-2020-058 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.1848 | 32.2773 | 0.0925
GEN-2020-058 | 03 CENTRAL | 543033 | BRKRIDG5 | 161 | 24.3701 | 24.4349 | 0.0648
GEN-2020-058 | 03 CENTRAL | 543034 | KNLWRTH5 | 161 | 27.2753 | 27.3486 | 0.0733
GEN-2020-058 | 03 CENTRAL | 543036 | OLATHE 5 | 161 | 27.3185 | 27.4113 | 0.0928
GEN-2020-058 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.1877 | 16.2208 | 0.0331
GEN-2020-058 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 36.9312 | 37.1132 | 0.182
GEN-2020-058 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 27.5543 | 27.6161 | 0.0618
GEN-2020-058 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 17.8384 | 17.879 | 0.0406
GEN-2020-058 | 03 CENTRAL | 543045 | SWITZER5 | 161 | 19.7859 | 19.8324 | 0.0465
GEN-2020-058 | 03 CENTRAL | 543046 | OXFORD 5 | 161 | 21.2773 | 21.3275 | 0.0502
GEN-2020-058 | 03 CENTRAL | 543047 | OVERLPK5 | 161 | 32.4478 | 32.5602 | 0.1124
GEN-2020-058 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.3233 | 30.4527 | 0.1294
GEN-2020-058 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.7609 | 30.8912 | 0.1303
GEN-2020-058 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.225 | 23.2777 | 0.0527
GEN-2020-058 | 03 CENTRAL | 543052 | REEDER 5 | 161 | 21.2914 | 21.3422 | 0.0508
GEN-2020-058 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.0455 | 25.092 | 0.0465
GEN-2020-058 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8373 | 10.8531 | 0.0158
GEN-2020-058 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 8.2123 | 8.2167 | 0.0044
GEN-2020-058 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.6085 | 16.6436 | 0.0351
GEN-2020-058 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0092 | 21.0435 | 0.0343
GEN-2020-058 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3274 | 9.3342 | 0.0068
GEN-2020-058 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4927 | 14.5072 | 0.0145
GEN-2020-058 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.6212 | 10.6325 | 0.0113
GEN-2020-058 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.0452 | 29.1564 | 0.1112
GEN-2020-058 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8467 | 13.864 | 0.0173
GEN-2020-058 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.1406 | 22.2051 | 0.0645
GEN-2020-058 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.9972 | 7.0004 | 0.0032
GEN-2020-058 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.075 | 27.154 | 0.079
GEN-2020-058 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.075 | 27.154 | 0.079
GEN-2020-058 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8161 | 2.8163 | 0.0002
GEN-2020-058 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6734 | 0.6735 | 0.0001
GEN-2020-058 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.645 | 0.6451 | 0.0001
GEN-2020-058 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.0889 | 27.1379 | 0.049
GEN-2020-058 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.6 | 6.6008 | 0.0008
GEN-2020-058 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.1532 | 8.1545 | 0.0013
GEN-2020-058 | 03 CENTRAL | 588240 | GEN-2016-149 | 345 | 3.6326 | 3.633 | 0.0004
GEN-2020-058 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 6.1499 | 6.1519 | 0.002
GEN-2020-058 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 5.1616 | 5.1628 | 0.0012
GEN-2020-058 | 03 CENTRAL | 588270 | GEN-2016-150 | 345 | 3.4321 | 3.4324 | 0.0003
GEN-2020-058 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.5231 | 6.5235 | 0.0004
GEN-2020-058 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 9.4229 | 9.4242 | 0.0013
GEN-2020-058 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.1109 | 27.5465 | 0.4356
GEN-2020-058 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.0367 | 27.4699 | 0.4332
GEN-2020-058 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.3556 | 3.3567 | 0.0011
GEN-2020-058 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 12.0099 | 12.0113 | 0.0014
GEN-2020-058 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 15.44 | 15.4402 | 0.0002
GEN-2020-058 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 18.6505 | 18.6507 | 0.0002
GEN-2020-058 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.2317 | 20.9028 | 0.6711
GEN-2020-058 | 03 CENTRAL | 764390 | GEN-2020-073 | 161 | 8.3572 | 8.3619 | 0.0047
GEN-2020-058 | 03 CENTRAL | 764400 | G20-073-TAP | 161 | 8.4375 | 8.4423 | 0.0048
GEN-2020-058 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.2344 | 20.9029 | 0.6685
GEN-2020-058 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 9.0328 | 9.0335 | 0.0007
GEN-2020-058 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3577 | 10.3587 | 0.001
GEN-2020-058 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.5612 | 24.6242 | 0.063
GEN-2020-058 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 27.0379 | 27.1153 | 0.0774
GEN-2020-061 | 03 CENTRAL | 41453 | J1145 SUB | 345 | 25.7239 | 25.7364 | 0.0125
GEN-2020-061 | 03 CENTRAL | 44882 | J1488_INV | 345 | 24.1263 | 24.1372 | 0.0109
GEN-2020-061 | 03 CENTRAL | 44887 | J1490_INV | 345 | 24.2793 | 24.2903 | 0.011
GEN-2020-061 | 03 CENTRAL | 44888 | J1490_POI | 345 | 25.7239 | 25.7364 | 0.0125
GEN-2020-061 | 03 CENTRAL | 300043 | 7KINGDM | 345 | 20.5841 | 20.595 | 0.0109
GEN-2020-061 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 25.951 | 25.9684 | 0.0174
GEN-2020-061 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 15.6391 | 15.6431 | 0.004
GEN-2020-061 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 12.8964 | 12.9346 | 0.0382
GEN-2020-061 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.7969 | 7.8151 | 0.0182
GEN-2020-061 | 03 CENTRAL | 300500 | 5HUNTSDL | 161 | 11.0769 | 11.0815 | 0.0046
GEN-2020-061 | 03 CENTRAL | 300688 | 2AUSTIN | 69 | 4.3383 | 4.3575 | 0.0192
GEN-2020-061 | 03 CENTRAL | 300689 | 2BUTLER | 69 | 6.0005 | 6.0231 | 0.0226
GEN-2020-061 | 03 CENTRAL | 300692 | 2CLINTN | 69 | 13.7439 | 13.7673 | 0.0234
GEN-2020-061 | 03 CENTRAL | 300698 | 2ELYNNE | 69 | 3.2961 | 3.3122 | 0.0161
GEN-2020-061 | 03 CENTRAL | 300699 | 2ELYNTP | 69 | 6.0667 | 6.1189 | 0.0522
GEN-2020-061 | 03 CENTRAL | 300705 | 2PECULR | 69 | 3.3468 | 3.3601 | 0.0133
GEN-2020-061 | 03 CENTRAL | 300709 | 2SHARSNV | 69 | 6.3477 | 6.4077 | 0.06
GEN-2020-061 | 03 CENTRAL | 301342 | 5BUTLER | 161 | 6.6361 | 6.7225 | 0.0864
GEN-2020-061 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.5978 | 6.6042 | 0.0064
GEN-2020-061 | 03 CENTRAL | 301503 | 7THOMHLGSU3 | 345 | 15.5099 | 15.5138 | 0.0039
GEN-2020-061 | 03 CENTRAL | 301515 | 5SHARSNV | 161 | 13.3112 | 14.2567 | 0.9455
GEN-2020-061 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.5906 | 6.5969 | 0.0063
GEN-2020-061 | 03 CENTRAL | 345221 | 5MOBERLY | 161 | 16.1763 | 16.1816 | 0.0053
GEN-2020-061 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 14.7782 | 14.8047 | 0.0265
GEN-2020-061 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.5211 | 22.5433 | 0.0222
GEN-2020-061 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 22.5211 | 22.5433 | 0.0222
GEN-2020-061 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.7013 | 3.7015 | 0.0002
GEN-2020-061 | 03 CENTRAL | 505502 | TRUMAN 5 | 161 | 7.4665 | 7.4712 | 0.0047
GEN-2020-061 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.6843 | 16.7394 | 0.0551
GEN-2020-061 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.2162 | 18.2288 | 0.0126
GEN-2020-061 | 03 CENTRAL | 541149 | WSTELEC_CAP5 | 161 | 14.3268 | 15.4784 | 1.1516
GEN-2020-061 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 8.0045 | 8.0195 | 0.015
GEN-2020-061 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 19.7602 | 20.748 | 0.9878
GEN-2020-061 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 17.6321 | 18.8625 | 1.2304
GEN-2020-061 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.8323 | 21.4074 | 0.5751
GEN-2020-061 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.8857 | 27.4504 | 0.5647
GEN-2020-061 | 03 CENTRAL | 541206 | PRALEE 5 | 161 | 19.0159 | 20.7888 | 1.7729
GEN-2020-061 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 13.5634 | 14.2566 | 0.6932
GEN-2020-061 | 03 CENTRAL | 541208 | NEVADA 5 | 161 | 6.2104 | 6.2357 | 0.0253
GEN-2020-061 | 03 CENTRAL | 541210 | MARTCTY5 | 161 | 26.8521 | 28.1197 | 1.2676
GEN-2020-061 | 03 CENTRAL | 541211 | BLSPS 5 | 161 | 18.812 | 19.997 | 1.185
GEN-2020-061 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 14.1 | 14.1845 | 0.0845
GEN-2020-061 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 8.351 | 8.366 | 0.015
GEN-2020-061 | 03 CENTRAL | 541218 | GRNWD 5 | 161 | 20.5232 | 24.1532 | 3.63
GEN-2020-061 | 03 CENTRAL | 541222 | WSTELEC5 | 161 | 15.6223 | 17.0017 | 1.3794
GEN-2020-061 | 03 CENTRAL | 541223 | GRDVWE 5 | 161 | 19.1518 | 20.3647 | 1.2129
GEN-2020-061 | 03 CENTRAL | 541224 | LNGVW 5 | 161 | 20.3568 | 22.8586 | 2.5018
GEN-2020-061 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 24.7352 | 33.5175 | 8.7823
GEN-2020-061 | 03 CENTRAL | 541231 | NRAYMORETP 5 | 161 | 5.8576 | 5.9456 | 0.088
GEN-2020-061 | 03 CENTRAL | 541233 | LEESUM 5 | 161 | 18.3619 | 20.4749 | 2.113
GEN-2020-061 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.1431 | 19.8403 | 0.6972
GEN-2020-061 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 13.4157 | 14.3772 | 0.9615
GEN-2020-061 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 7.9004 | 8.0685 | 0.1681
GEN-2020-061 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 12.8505 | 12.8884 | 0.0379
GEN-2020-061 | 03 CENTRAL | 541243 | LKWINBG5 | 161 | 20.668 | 24.9957 | 4.3277
GEN-2020-061 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 13.9812 | 14.1484 | 0.1672
GEN-2020-061 | 03 CENTRAL | 541245 | KCSOUTH5 | 161 | 13.1814 | 14.1147 | 0.9333
GEN-2020-061 | 03 CENTRAL | 541246 | STROTHR5 | 161 | 13.7166 | 14.7001 | 0.9835
GEN-2020-061 | 03 CENTRAL | 541249 | HOOKRD 5 | 161 | 19.7636 | 22.8608 | 3.0972
GEN-2020-061 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.4118 | 29.0585 | 0.6467
GEN-2020-061 | 03 CENTRAL | 541259 | TURNER_RD5 | 161 | 17.8091 | 18.3617 | 0.5526
GEN-2020-061 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.8369 | 11.8793 | 0.0424
GEN-2020-061 | 03 CENTRAL | 541278 | HOLDEN 2 | 69 | 3.9951 | 4.0115 | 0.0164
GEN-2020-061 | 03 CENTRAL | 541279 | RGREEN 2 | 69 | 9.3414 | 9.5319 | 0.1905
GEN-2020-061 | 03 CENTRAL | 541280 | PHILL 2 | 69 | 10.1234 | 10.3587 | 0.2353
GEN-2020-061 | 03 CENTRAL | 541282 | LNGVW 2 | 69 | 10.5202 | 10.6518 | 0.1316
GEN-2020-061 | 03 CENTRAL | 541283 | BRMALL 2 | 69 | 15.3813 | 15.4469 | 0.0656
GEN-2020-061 | 03 CENTRAL | 541284 | GRDVWTP2 | 69 | 9.3646 | 9.4665 | 0.1019
GEN-2020-061 | 03 CENTRAL | 541289 | BELTON 2 | 69 | 9.2288 | 9.3358 | 0.107
GEN-2020-061 | 03 CENTRAL | 541290 | BELTONS2 | 69 | 9.9774 | 10.1059 | 0.1285
GEN-2020-061 | 03 CENTRAL | 541291 | FREEMAN2 | 69 | 4.4809 | 4.5091 | 0.0282
GEN-2020-061 | 03 CENTRAL | 541292 | ANCONDA2 | 69 | 6.3081 | 6.3804 | 0.0723
GEN-2020-061 | 03 CENTRAL | 541293 | HSNVLW 2 | 69 | 6.409 | 6.4841 | 0.0751
GEN-2020-061 | 03 CENTRAL | 541294 | HSNVLS 2 | 69 | 7.0616 | 7.1556 | 0.094
GEN-2020-061 | 03 CENTRAL | 541295 | HSNVL 2 | 69 | 8.2835 | 8.4179 | 0.1344
GEN-2020-061 | 03 CENTRAL | 541296 | HSNVLSW2 | 69 | 7.5943 | 7.7085 | 0.1142
GEN-2020-061 | 03 CENTRAL | 541297 | HSNVLN 2 | 69 | 6.9674 | 7.0651 | 0.0977
GEN-2020-061 | 03 CENTRAL | 541298 | GRDNCTY2 | 69 | 4.0981 | 4.1308 | 0.0327
GEN-2020-061 | 03 CENTRAL | 541299 | GUNNPS2 | 69 | 3.9236 | 3.9535 | 0.0299
GEN-2020-061 | 03 CENTRAL | 541313 | HARRIS | 161 | 21.2823 | 25.929 | 4.6467
GEN-2020-061 | 03 CENTRAL | 541340 | BELTONS5 | 161 | 18.8003 | 19.4192 | 0.6189
GEN-2020-061 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 19.7261 | 20.4689 | 0.7428
GEN-2020-061 | 03 CENTRAL | 541342 | PECULR 5 | 161 | 22.0182 | 22.8468 | 0.8286
GEN-2020-061 | 03 CENTRAL | 541343 | S.HARP 2 | 69 | 4.5353 | 4.5614 | 0.0261
GEN-2020-061 | 03 CENTRAL | 541344 | PECULRS5 | 161 | 20.5151 | 21.2654 | 0.7503
GEN-2020-061 | 03 CENTRAL | 541347 | RAYMORE | 69 | 8.3423 | 8.4491 | 0.1068
GEN-2020-061 | 03 CENTRAL | 541348 | RAYTAP | 69 | 9.0656 | 9.1799 | 0.1143
GEN-2020-061 | 03 CENTRAL | 541386 | HLDENTP2 | 69 | 4.1377 | 4.1552 | 0.0175
GEN-2020-061 | 03 CENTRAL | 541387 | KNGSVIL 2 | 69 | 4.2859 | 4.3096 | 0.0237
GEN-2020-061 | 03 CENTRAL | 541388 | KNGSVRL2 | 69 | 4.7053 | 4.739 | 0.0337
GEN-2020-061 | 03 CENTRAL | 541411 | MC REAC1 | 345 | 7.6564 | 7.6701 | 0.0137
GEN-2020-061 | 03 CENTRAL | 541412 | MC REAC2 | 345 | 7.6564 | 7.6701 | 0.0137
GEN-2020-061 | 03 CENTRAL | 541413 | MC REAC3 | 345 | 7.6564 | 7.6701 | 0.0137
GEN-2020-061 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.6296 | 19.088 | 0.4584
GEN-2020-061 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.8904 | 7.9216 | 0.0312
GEN-2020-061 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 7.034 | 7.0585 | 0.0245
GEN-2020-061 | 03 CENTRAL | 541510 | HOLT 7 | 345 | 9.2582 | 9.2699 | 0.0117
GEN-2020-061 | 03 CENTRAL | 541511 | ROCKCK7 | 345 | 7.137 | 7.1434 | 0.0064
GEN-2020-061 | 03 CENTRAL | 541517 | HOLT_REACT7 | 345 | 9.2095 | 9.2211 | 0.0116
GEN-2020-061 | 03 CENTRAL | 541540 | FREEMAN_SP2 | 69 | 4.1813 | 4.205 | 0.0237
GEN-2020-061 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6768 | 2.6772 | 0.0004
GEN-2020-061 | 03 CENTRAL | 541543 | OUTLAW | 345 | 5.8745 | 5.8787 | 0.0042
GEN-2020-061 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.7302 | 20.9429 | 0.2127
GEN-2020-061 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.1998 | 27.6185 | 0.4187
GEN-2020-061 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.946 | 30.1269 | 0.1809
GEN-2020-061 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 24.9585 | 25.8373 | 0.8788
GEN-2020-061 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 39.7238 | 40.9756 | 1.2518
GEN-2020-061 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.9791 | 23.375 | 0.3959
GEN-2020-061 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 56.6981 | 57.7268 | 1.0287
GEN-2020-061 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 51.3302 | 52.1481 | 0.8179
GEN-2020-061 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 23.5573 | 23.7859 | 0.2286
GEN-2020-061 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.6726 | 27.8947 | 0.2221
GEN-2020-061 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.5704 | 30.7241 | 0.1537
GEN-2020-061 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.7154 | 20.0023 | 0.2869
GEN-2020-061 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 38.6188 | 39.0971 | 0.4783
GEN-2020-061 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 36.1647 | 36.5563 | 0.3916
GEN-2020-061 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 33.2754 | 33.6126 | 0.3372
GEN-2020-061 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 34.2705 | 34.5513 | 0.2808
GEN-2020-061 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 22.9469 | 23.2777 | 0.3308
GEN-2020-061 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 24.4051 | 25.092 | 0.6869
GEN-2020-061 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8295 | 10.8531 | 0.0236
GEN-2020-061 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 20.7529 | 21.0435 | 0.2906
GEN-2020-061 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.2766 | 9.3342 | 0.0576
GEN-2020-061 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.9901 | 29.1564 | 0.1663
GEN-2020-061 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.7358 | 13.864 | 0.1282
GEN-2020-061 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 55.9229 | 56.9223 | 0.9994
GEN-2020-061 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 26.9435 | 27.154 | 0.2105
GEN-2020-061 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 26.9435 | 27.154 | 0.2105
GEN-2020-061 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8158 | 2.8163 | 0.0005
GEN-2020-061 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 57.331 | 58.3729 | 1.0419
GEN-2020-061 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6734 | 0.6735 | 0.0001
GEN-2020-061 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.645 | 0.6451 | 0.0001
GEN-2020-061 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.2802 | 25.6684 | 0.3882
GEN-2020-061 | 03 CENTRAL | 760746 | GEN-2017-115 | 345 | 8.3838 | 8.3934 | 0.0096
GEN-2020-061 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.5147 | 6.5235 | 0.0088
GEN-2020-061 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 9.4013 | 9.4242 | 0.0229
GEN-2020-061 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.9565 | 8.9748 | 0.0183
GEN-2020-061 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.752 | 17.8391 | 0.0871
GEN-2020-061 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.1301 | 27.5465 | 0.4164
GEN-2020-061 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.0558 | 27.4699 | 0.4141
GEN-2020-061 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 12.0059 | 12.0113 | 0.0054
GEN-2020-061 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.6909 | 20.9028 | 0.2119
GEN-2020-061 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.691 | 20.9029 | 0.2119
GEN-2020-061 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.4563 | 24.6242 | 0.1679
GEN-2020-061 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 26.9091 | 27.1153 | 0.2062
GEN-2020-061 | 03 CENTRAL | 999101 | GI083 | 345 | 16.8191 | 16.8213 | 0.0022
GEN-2020-064 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.578 | 6.5983 | 0.0203
GEN-2020-064 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.2435 | 16.2782 | 0.0347
GEN-2020-064 | 03 CENTRAL | 300748 | 2NEOSAC | 69 | 10.1071 | 10.2059 | 0.0988
GEN-2020-064 | 03 CENTRAL | 300763 | 2WASHBRN | 69 | 6.7833 | 6.8007 | 0.0174
GEN-2020-064 | 03 CENTRAL | 505480 | BEAVER 5 | 161 | 11.266 | 11.3056 | 0.0396
GEN-2020-064 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 8.3007 | 8.3523 | 0.0516
GEN-2020-064 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.1006 | 15.8465 | 0.7459
GEN-2020-064 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.2369 | 16.9483 | 0.7114
GEN-2020-064 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 13.9322 | 14.1051 | 0.1729
GEN-2020-064 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 27.4707 | 27.533 | 0.0623
GEN-2020-064 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.0447 | 12.0572 | 0.0125
GEN-2020-064 | 03 CENTRAL | 510417 | VINTAJC4 | 138 | 5.2127 | 5.2311 | 0.0184
GEN-2020-064 | 03 CENTRAL | 512630 | MIAMI 2 | 69 | 12.3812 | 12.505 | 0.1238
GEN-2020-064 | 03 CENTRAL | 512631 | MIAMI 5 | 161 | 9.4979 | 9.6878 | 0.1899
GEN-2020-064 | 03 CENTRAL | 512632 | AFTON 5 | 161 | 8.4996 | 8.5788 | 0.0792
GEN-2020-064 | 03 CENTRAL | 513020 | MIAMI1 2 | 69 | 10.6108 | 10.7015 | 0.0907
GEN-2020-064 | 03 CENTRAL | 513022 | MIAMI4 2 | 69 | 9.0373 | 9.1031 | 0.0658
GEN-2020-064 | 03 CENTRAL | 513026 | COMMTP 2 | 69 | 9.4772 | 9.5496 | 0.0724
GEN-2020-064 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9098 | 11.9338 | 0.024
GEN-2020-064 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.0177 | 11.0381 | 0.0204
GEN-2020-064 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1526 | 18.2288 | 0.0762
GEN-2020-064 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.184 | 8.2126 | 0.0286
GEN-2020-064 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.1808 | 8.2093 | 0.0285
GEN-2020-064 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.5766 | 23.7942 | 0.2176
GEN-2020-064 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2505 | 7.2579 | 0.0074
GEN-2020-064 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.216 | 25.3852 | 0.1692
GEN-2020-064 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.2588 | 25.4284 | 0.1696
GEN-2020-064 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.1416 | 25.3096 | 0.168
GEN-2020-064 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.9613 | 8.9742 | 0.0129
GEN-2020-064 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 23.9626 | 24.0535 | 0.0909
GEN-2020-064 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6772 | 2.6772 | 0
GEN-2020-064 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8868 | 27.8947 | 0.0079
GEN-2020-064 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.1466 | 27.154 | 0.0074
GEN-2020-064 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.1466 | 27.154 | 0.0074
GEN-2020-064 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8163 | 2.8163 | 0
GEN-2020-064 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6735 | 0.6735 | 0
GEN-2020-064 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6451 | 0.6451 | 0
GEN-2020-064 | 03 CENTRAL | 547400 | MON376J2 | 69 | 4.1214 | 4.131 | 0.0096
GEN-2020-064 | 03 CENTRAL | 547401 | MON376 2 | 69 | 6.6801 | 6.7053 | 0.0252
GEN-2020-064 | 03 CENTRAL | 547402 | MON416J2 | 69 | 3.6305 | 3.6378 | 0.0073
GEN-2020-064 | 03 CENTRAL | 547403 | MON416 2 | 69 | 3.5363 | 3.5432 | 0.0069
GEN-2020-064 | 03 CENTRAL | 547404 | PUR390 2 | 69 | 1.7985 | 1.8001 | 0.0016
GEN-2020-064 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.8997 | 7.9351 | 0.0354
GEN-2020-064 | 03 CENTRAL | 547406 | MON352 2 | 69 | 7.5895 | 7.6222 | 0.0327
GEN-2020-064 | 03 CENTRAL | 547407 | MON311J2 | 69 | 6.7646 | 6.7905 | 0.0259
GEN-2020-064 | 03 CENTRAL | 547408 | MON311 2 | 69 | 6.6801 | 6.7053 | 0.0252
GEN-2020-064 | 03 CENTRAL | 547409 | SCAM66 2 | 69 | 2.5415 | 2.5519 | 0.0104
GEN-2020-064 | 03 CENTRAL | 547411 | COL282 2 | 69 | 4.6627 | 4.7 | 0.0373
GEN-2020-064 | 03 CENTRAL | 547412 | SEK225T2 | 69 | 3.599 | 3.6205 | 0.0215
GEN-2020-064 | 03 CENTRAL | 547413 | SEK225 2 | 69 | 3.5525 | 3.5733 | 0.0208
GEN-2020-064 | 03 CENTRAL | 547414 | SMN425 2 | 69 | 2.0298 | 2.0365 | 0.0067
GEN-2020-064 | 03 CENTRAL | 547415 | SHR444 2 | 69 | 2.796 | 2.8085 | 0.0125
GEN-2020-064 | 03 CENTRAL | 547416 | CHE299T2 | 69 | 1.9034 | 1.9085 | 0.0051
GEN-2020-064 | 03 CENTRAL | 547417 | CHE299 2 | 69 | 1.8232 | 1.8279 | 0.0047
GEN-2020-064 | 03 CENTRAL | 547418 | CHE300 2 | 69 | 1.8645 | 1.8694 | 0.0049
GEN-2020-064 | 03 CENTRAL | 547419 | TWN388 2 | 69 | 1.8115 | 1.8161 | 0.0046
GEN-2020-064 | 03 CENTRAL | 547420 | WEL186 2 | 69 | 1.1659 | 1.1678 | 0.0019
GEN-2020-064 | 03 CENTRAL | 547426 | SEN375 2 | 69 | 3.0605 | 3.0779 | 0.0174
GEN-2020-064 | 03 CENTRAL | 547431 | WEB105 2 | 69 | 8.0117 | 8.1362 | 0.1245
GEN-2020-064 | 03 CENTRAL | 547438 | EXP449T2 | 69 | 8.9269 | 9.1178 | 0.1909
GEN-2020-064 | 03 CENTRAL | 547439 | EXP4492 | 69 | 7.4304 | 7.5613 | 0.1309
GEN-2020-064 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.7354 | 5.7606 | 0.0252
GEN-2020-064 | 03 CENTRAL | 547455 | SCM66T 2 | 69 | 4.4896 | 4.5228 | 0.0332
GEN-2020-064 | 03 CENTRAL | 547459 | WWR477 | 161 | 18.6706 | 22.5477 | 3.8771
GEN-2020-064 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 13.219 | 14.5045 | 1.2855
GEN-2020-064 | 03 CENTRAL | 547463 | KOD471 2 | 69 | 11.9751 | 12.2616 | 0.2865
GEN-2020-064 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 15.5921 | 16.6218 | 1.0297
GEN-2020-064 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 18.403 | 20.1817 | 1.7787
GEN-2020-064 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.7413 | 10.8322 | 0.0909
GEN-2020-064 | 03 CENTRAL | 547469 | RIV4525 | 161 | 22.4442 | 24.955 | 2.5108
GEN-2020-064 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 16.97 | 19.2966 | 2.3266
GEN-2020-064 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.0135 | 14.6078 | 0.5943
GEN-2020-064 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 16.3417 | 17.8729 | 1.5312
GEN-2020-064 | 03 CENTRAL | 547476 | ASB349 5 | 161 | 11.0297 | 11.3223 | 0.2926
GEN-2020-064 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.1402 | 12.7408 | 0.6006
GEN-2020-064 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 15.4126 | 15.696 | 0.2834
GEN-2020-064 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.0139 | 12.2264 | 0.2125
GEN-2020-064 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 17.6386 | 20.2614 | 2.6228
GEN-2020-064 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 12.1744 | 12.5634 | 0.389
GEN-2020-064 | 03 CENTRAL | 547486 | HOC404 4 | 138 | 6.6743 | 6.7646 | 0.0903
GEN-2020-064 | 03 CENTRAL | 547487 | HOC404 5 | 161 | 13.0614 | 13.6178 | 0.5564
GEN-2020-064 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 13.8277 | 14.6931 | 0.8654
GEN-2020-064 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 16.8781 | 18.2669 | 1.3888
GEN-2020-064 | 03 CENTRAL | 547496 | NOL435 5 | 161 | 10.1223 | 10.2153 | 0.093
GEN-2020-064 | 03 CENTRAL | 547498 | STL439 5 | 161 | 20.1026 | 24.6682 | 4.5656
GEN-2020-064 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.7491 | 8.7839 | 0.0348
GEN-2020-064 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 13.4495 | 14.5565 | 1.107
GEN-2020-064 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 21.3371 | 23.5252 | 2.1881
GEN-2020-064 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 20.9433 | 23.0916 | 2.1483
GEN-2020-064 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 22.0738 | 24.4738 | 2.4
GEN-2020-064 | 03 CENTRAL | 547524 | NEO 56 2 | 69 | 7.88 | 7.9729 | 0.0929
GEN-2020-064 | 03 CENTRAL | 547525 | JOP 59 2 | 69 | 19.1606 | 20.0155 | 0.8549
GEN-2020-064 | 03 CENTRAL | 547526 | JOP 64 2 | 69 | 18.8275 | 19.6517 | 0.8242
GEN-2020-064 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.5408 | 9.7134 | 0.1726
GEN-2020-064 | 03 CENTRAL | 547530 | COL 94 2 | 69 | 6.5217 | 6.5932 | 0.0715
GEN-2020-064 | 03 CENTRAL | 547531 | JOP100 2 | 69 | 15.8215 | 16.3881 | 0.5666
GEN-2020-064 | 03 CENTRAL | 547532 | CAR108 2 | 69 | 8.4099 | 8.5166 | 0.1067
GEN-2020-064 | 03 CENTRAL | 547533 | ATL109 2 | 69 | 20.3767 | 21.2225 | 0.8458
GEN-2020-064 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 17.6377 | 18.3049 | 0.6672
GEN-2020-064 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.5684 | 12.6214 | 0.053
GEN-2020-064 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 20.3179 | 21.321 | 1.0031
GEN-2020-064 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.948 | 11.0131 | 0.0651
GEN-2020-064 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 17.4011 | 18.0208 | 0.6197
GEN-2020-064 | 03 CENTRAL | 547543 | NEO184 2 | 69 | 11.8941 | 12.0898 | 0.1957
GEN-2020-064 | 03 CENTRAL | 547551 | GAT258 2 | 69 | 14.2552 | 14.7041 | 0.4489
GEN-2020-064 | 03 CENTRAL | 547554 | BAX271 2 | 69 | 9.5662 | 9.7155 | 0.1493
GEN-2020-064 | 03 CENTRAL | 547555 | GAL278 2 | 69 | 12.9637 | 13.3508 | 0.3871
GEN-2020-064 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 15.6932 | 16.209 | 0.5158
GEN-2020-064 | 03 CENTRAL | 547557 | JOP284 2 | 69 | 16.3926 | 17.0048 | 0.6122
GEN-2020-064 | 03 CENTRAL | 547559 | TIP292 2 | 69 | 9.9195 | 10.1069 | 0.1874
GEN-2020-064 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 17.7268 | 18.4638 | 0.737
GEN-2020-064 | 03 CENTRAL | 547589 | RAC375 2 | 69 | 6.2182 | 6.2969 | 0.0787
GEN-2020-064 | 03 CENTRAL | 547590 | QUA377 2 | 69 | 7.2806 | 7.3542 | 0.0736
GEN-2020-064 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.6158 | 12.707 | 0.0912
GEN-2020-064 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.0134 | 15.6115 | 0.5981
GEN-2020-064 | 03 CENTRAL | 547593 | JOP391 5 | 161 | 12.6406 | 13.666 | 1.0254
GEN-2020-064 | 03 CENTRAL | 547595 | RNM393 2 | 69 | 18.9758 | 19.7394 | 0.7636
GEN-2020-064 | 03 CENTRAL | 547601 | HOC404 2 | 69 | 9.6926 | 9.8337 | 0.1411
GEN-2020-064 | 03 CENTRAL | 547602 | RIV406 2 | 69 | 15.5062 | 15.991 | 0.4848
GEN-2020-064 | 03 CENTRAL | 547607 | JOP422 5 | 161 | 12.4355 | 13.4873 | 1.0518
GEN-2020-064 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 15.5394 | 16.1243 | 0.5849
GEN-2020-064 | 03 CENTRAL | 547685 | PLB447 2 | 69 | 14.2151 | 14.6583 | 0.4432
GEN-2020-064 | 03 CENTRAL | 547690 | GLF339 2 | 69 | 11.8402 | 12.1398 | 0.2996
GEN-2020-064 | 03 CENTRAL | 547728 | GAL278T | 69 | 13.2414 | 13.6455 | 0.4041
GEN-2020-064 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 14.5267 | 15.3177 | 0.791
GEN-2020-064 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 6.2057 | 6.2462 | 0.0405
GEN-2020-064 | 03 CENTRAL | 589200 | GEN-2017-082 | 161 | 7.5545 | 7.6839 | 0.1294
GEN-2020-064 | 03 CENTRAL | 760242 | GEN-2017-188 | 161 | 2.0244 | 2.03 | 0.0056
GEN-2020-064 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9782 | 12.0113 | 0.0331
GEN-2020-064 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.8472 | 7.8775 | 0.0303
GEN-2020-064 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.8647 | 7.8951 | 0.0304
GEN-2020-064 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.756 | 15.4402 | 0.6842
GEN-2020-064 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.6261 | 18.6507 | 1.0246
GEN-2020-064 | 03 CENTRAL | 764315 | GEN-2020-088 | 161 | 14.9545 | 15.2206 | 0.2661
GEN-2020-072 | 03 CENTRAL | 99911 | GI91POI | 69 | 2.9464 | 2.9509 | 0.0045
GEN-2020-072 | 03 CENTRAL | 300034 | 5EDMONS | 161 | 6.5599 | 6.5876 | 0.0277
GEN-2020-072 | 03 CENTRAL | 300071 | 5CLINTN | 161 | 12.5138 | 12.9346 | 0.4208
GEN-2020-072 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.3344 | 8.5198 | 0.1854
GEN-2020-072 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.8019 | 6.8375 | 0.0356
GEN-2020-072 | 03 CENTRAL | 300108 | 5OSCEOLTP | 161 | 6.5627 | 6.6058 | 0.0431
GEN-2020-072 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.7879 | 8.8042 | 0.0163
GEN-2020-072 | 03 CENTRAL | 300117 | 5SEDALA | 161 | 8.9439 | 9.2818 | 0.3379
GEN-2020-072 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.7816 | 7.8151 | 0.0335
GEN-2020-072 | 03 CENTRAL | 300323 | 2CENTRV | 69 | 4.4796 | 4.4838 | 0.0042
GEN-2020-072 | 03 CENTRAL | 300327 | 2ELM | 69 | 4.4508 | 4.4542 | 0.0034
GEN-2020-072 | 03 CENTRAL | 300328 | 2MAGNOL | 69 | 2.2762 | 2.2773 | 0.0011
GEN-2020-072 | 03 CENTRAL | 300336 | 2HOLDEN | 69 | 6.5627 | 6.5715 | 0.0088
GEN-2020-072 | 03 CENTRAL | 300527 | 2BEAMAN | 69 | 3.8494 | 3.8608 | 0.0114
GEN-2020-072 | 03 CENTRAL | 300528 | 2DRESDN | 69 | 5.9345 | 5.9709 | 0.0364
GEN-2020-072 | 03 CENTRAL | 300529 | 2GEOGT1 | 69 | 7.3939 | 7.4483 | 0.0544
GEN-2020-072 | 03 CENTRAL | 300530 | 2GEOGT2 | 69 | 7.9761 | 8.0412 | 0.0651
GEN-2020-072 | 03 CENTRAL | 300531 | 2GEORGE | 69 | 8.0675 | 8.1333 | 0.0658
GEN-2020-072 | 03 CENTRAL | 300534 | 2LINCLN | 69 | 4.9465 | 4.9669 | 0.0204
GEN-2020-072 | 03 CENTRAL | 300541 | 2SEDALI | 69 | 10.2842 | 10.3986 | 0.1144
GEN-2020-072 | 03 CENTRAL | 300542 | 2SMTHTN | 69 | 4.4959 | 4.5115 | 0.0156
GEN-2020-072 | 03 CENTRAL | 300553 | 2FLORNC | 69 | 3.8012 | 3.8075 | 0.0063
GEN-2020-072 | 03 CENTRAL | 300557 | 2IVYBND | 69 | 2.7884 | 2.7918 | 0.0034
GEN-2020-072 | 03 CENTRAL | 300558 | 2MTHULD | 69 | 2.9724 | 2.9778 | 0.0054
GEN-2020-072 | 03 CENTRAL | 300562 | 2STOVER | 69 | 1.961 | 1.9633 | 0.0023
GEN-2020-072 | 03 CENTRAL | 300690 | 2BUTLERE | 69 | 4.8276 | 4.8304 | 0.0028
GEN-2020-072 | 03 CENTRAL | 300692 | 2CLINTN | 69 | 13.6124 | 13.7673 | 0.1549
GEN-2020-072 | 03 CENTRAL | 300696 | 2CREIGH | 69 | 4.1525 | 4.1561 | 0.0036
GEN-2020-072 | 03 CENTRAL | 300701 | 2GAINES | 69 | 4.6425 | 4.6571 | 0.0146
GEN-2020-072 | 03 CENTRAL | 300702 | 2LADUE | 69 | 4.0636 | 4.0737 | 0.0101
GEN-2020-072 | 03 CENTRAL | 300703 | 2LEETON | 69 | 4.0191 | 4.0284 | 0.0093
GEN-2020-072 | 03 CENTRAL | 300706 | 2PIPER | 69 | 3.7487 | 3.7549 | 0.0062
GEN-2020-072 | 03 CENTRAL | 300789 | 2TRUMAN | 69 | 1.9231 | 1.9251 | 0.002
GEN-2020-072 | 03 CENTRAL | 300810 | 2MTZION | 69 | 3.9762 | 3.9847 | 0.0085
GEN-2020-072 | 03 CENTRAL | 300816 | 5COLLINS | 161 | 6.717 | 6.7425 | 0.0255
GEN-2020-072 | 03 CENTRAL | 301040 | 5OSCEOL | 161 | 6.5472 | 6.5901 | 0.0429
GEN-2020-072 | 03 CENTRAL | 301370 | 5TURKEYCRK | 161 | 5.3461 | 5.3677 | 0.0216
GEN-2020-072 | 03 CENTRAL | 301402 | 5LOSTVALY | 161 | 7.2328 | 7.2735 | 0.0407
GEN-2020-072 | 03 CENTRAL | 301477 | 5OSCEOKCTP | 161 | 6.561 | 6.6042 | 0.0432
GEN-2020-072 | 03 CENTRAL | 301522 | 5OSCEOKC | 161 | 6.5539 | 6.5969 | 0.043
GEN-2020-072 | 03 CENTRAL | 301561 | 5HOLDENB1 | 161 | 7.7778 | 7.8112 | 0.0334
GEN-2020-072 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.294 | 6.3341 | 0.0401
GEN-2020-072 | 03 CENTRAL | 301626 | 2CLINTNLD | 69 | 13.4365 | 13.5874 | 0.1509
GEN-2020-072 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 10.9414 | 10.953 | 0.0116
GEN-2020-072 | 03 CENTRAL | 345071 | 5MCBAIN T | 161 | 15.038 | 15.047 | 0.009
GEN-2020-072 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 22.5014 | 22.5433 | 0.0419
GEN-2020-072 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 22.5014 | 22.5433 | 0.0419
GEN-2020-072 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.701 | 3.7015 | 0.0005
GEN-2020-072 | 03 CENTRAL | 503507 | 2BUTLEREGEN | 69 | 4.8251 | 4.8278 | 0.0027
GEN-2020-072 | 03 CENTRAL | 505502 | TRUMAN 5 | 161 | 7.425 | 7.4712 | 0.0462
GEN-2020-072 | 03 CENTRAL | 541138 | CLNTPLT_CAP2 | 69 | 8.3301 | 8.3917 | 0.0616
GEN-2020-072 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 9.2115 | 9.469 | 0.2575
GEN-2020-072 | 03 CENTRAL | 541148 | WBURGE_CAP5 | 161 | 6.3689 | 6.4234 | 0.0545
GEN-2020-072 | 03 CENTRAL | 541207 | ARCHIE 5 | 161 | 14.2493 | 14.2566 | 0.0073
GEN-2020-072 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.7293 | 10.0172 | 0.2879
GEN-2020-072 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 7.5201 | 8.366 | 0.8459
GEN-2020-072 | 03 CENTRAL | 541228 | WBURGE 5 | 161 | 6.6124 | 6.6712 | 0.0588
GEN-2020-072 | 03 CENTRAL | 541239 | HSNVL 5 | 161 | 14.37 | 14.3772 | 0.0072
GEN-2020-072 | 03 CENTRAL | 541240 | ADRIAN 5 | 161 | 8.0649 | 8.0685 | 0.0036
GEN-2020-072 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.7184 | 7.8478 | 0.1294
GEN-2020-072 | 03 CENTRAL | 541242 | CLINTON5 | 161 | 12.4705 | 12.8884 | 0.4179
GEN-2020-072 | 03 CENTRAL | 541270 | KNOSTER2 | 69 | 4.8987 | 4.9148 | 0.0161
GEN-2020-072 | 03 CENTRAL | 541271 | SEDN 2 | 69 | 7.4273 | 7.483 | 0.0557
GEN-2020-072 | 03 CENTRAL | 541272 | SEDS 2 | 69 | 6.615 | 6.6622 | 0.0472
GEN-2020-072 | 03 CENTRAL | 541273 | KELHYS 2 | 69 | 7.0483 | 7.0987 | 0.0504
GEN-2020-072 | 03 CENTRAL | 541274 | PITTCRN2 | 69 | 6.5569 | 6.6025 | 0.0456
GEN-2020-072 | 03 CENTRAL | 541275 | SEDPLT 2 | 69 | 6.7313 | 6.7777 | 0.0464
GEN-2020-072 | 03 CENTRAL | 541301 | CLNTPLT2 | 69 | 8.5056 | 8.5698 | 0.0642
GEN-2020-072 | 03 CENTRAL | 541302 | CLNTGRN2 | 69 | 8.2419 | 8.3033 | 0.0614
GEN-2020-072 | 03 CENTRAL | 541303 | CLNTN N2 | 69 | 8.0299 | 8.0898 | 0.0599
GEN-2020-072 | 03 CENTRAL | 541314 | NWARSAW5 | 161 | 7.2176 | 7.2582 | 0.0406
GEN-2020-072 | 03 CENTRAL | 541320 | CLNTN S2 | 69 | 8.2945 | 8.3567 | 0.0622
GEN-2020-072 | 03 CENTRAL | 541335 | WAFBW_SW5 | 161 | 6.6896 | 6.7694 | 0.0798
GEN-2020-072 | 03 CENTRAL | 541336 | WAFBW5 | 161 | 6.087 | 6.1532 | 0.0662
GEN-2020-072 | 03 CENTRAL | 541337 | WAFBE_SW5 | 161 | 6.717 | 6.7991 | 0.0821
GEN-2020-072 | 03 CENTRAL | 541338 | WAFBE5 | 161 | 6.1134 | 6.1814 | 0.068
GEN-2020-072 | 03 CENTRAL | 541341 | S.HARP 5 | 161 | 20.4592 | 20.4689 | 0.0097
GEN-2020-072 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.2392 | 7.3529 | 0.1137
GEN-2020-072 | 03 CENTRAL | 541534 | KNOSTERTP | 69 | 4.9529 | 4.9693 | 0.0164
GEN-2020-072 | 03 CENTRAL | 541535 | LAMONTETP | 69 | 5.078 | 5.0996 | 0.0216
GEN-2020-072 | 03 CENTRAL | 541536 | LAMONTE | 69 | 4.9238 | 4.944 | 0.0202
GEN-2020-072 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.8232 | 25.8373 | 0.0141
GEN-2020-072 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9399 | 40.9756 | 0.0357
GEN-2020-072 | 03 CENTRAL | 542994 | HICKMAN5 | 161 | 19.9963 | 20.0023 | 0.006
GEN-2020-072 | 03 CENTRAL | 543050 | ANTIOCH5 | 161 | 23.2688 | 23.2777 | 0.0089
GEN-2020-072 | 03 CENTRAL | 543053 | REDEL 5 | 161 | 25.0795 | 25.092 | 0.0125
GEN-2020-072 | 03 CENTRAL | 543057 | BUCYRUS5 | 161 | 21.0353 | 21.0435 | 0.0082
GEN-2020-072 | 03 CENTRAL | 543058 | NLOUISB5 | 161 | 9.3326 | 9.3342 | 0.0016
GEN-2020-072 | 03 CENTRAL | 543126 | LACKMAN5 | 161 | 13.8604 | 13.864 | 0.0036
GEN-2020-072 | 03 CENTRAL | 761271 | GEN-2017-108 | 161 | 6.4718 | 6.5235 | 0.0517
GEN-2020-072 | 03 CENTRAL | 761278 | G17-108-TAP | 161 | 9.2917 | 9.4242 | 0.1325
GEN-2020-072 | 03 CENTRAL | 764345 | GEN-2020-072 | 161 | 7.4085 | 8.2806 | 0.8721
GEN-2020-072 | 03 CENTRAL | 764355 | G20-072-TAP | 161 | 7.4894 | 8.3603 | 0.8709
GEN-2020-073 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5814 | 16.5846 | 0.0032
GEN-2020-073 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.7281 | 16.7394 | 0.0113
GEN-2020-073 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8872 | 13.8894 | 0.0022
GEN-2020-073 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.226 | 18.2288 | 0.0028
GEN-2020-073 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.7305 | 21.739 | 0.0085
GEN-2020-073 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.714 | 20.748 | 0.034
GEN-2020-073 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6772 | 2.6772 | 0
GEN-2020-073 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.8983 | 20.9429 | 0.0446
GEN-2020-073 | 03 CENTRAL | 542945 | CRAIG_CAP 5 | 161 | 34.612 | 34.6829 | 0.0709
GEN-2020-073 | 03 CENTRAL | 542947 | MERRIAM_CAP5 | 161 | 27.1643 | 27.1958 | 0.0315
GEN-2020-073 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.5257 | 27.6185 | 0.0928
GEN-2020-073 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.7674 | 30.1269 | 0.3595
GEN-2020-073 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.7708 | 25.8373 | 0.0665
GEN-2020-073 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.8266 | 40.9756 | 0.149
GEN-2020-073 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.1006 | 22.1427 | 0.0421
GEN-2020-073 | 03 CENTRAL | 542978 | CRAIG 5 | 161 | 43.2796 | 43.3904 | 0.1108
GEN-2020-073 | 03 CENTRAL | 542979 | PFLUMM 5 | 161 | 29.7994 | 29.8481 | 0.0487
GEN-2020-073 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8686 | 27.8947 | 0.0261
GEN-2020-073 | 03 CENTRAL | 543031 | SHWNMSN5 | 161 | 36.5412 | 36.5991 | 0.0579
GEN-2020-073 | 03 CENTRAL | 543032 | MERRIAM5 | 161 | 32.2329 | 32.2773 | 0.0444
GEN-2020-073 | 03 CENTRAL | 543037 | QUARRY 5 | 161 | 16.1665 | 16.2208 | 0.0543
GEN-2020-073 | 03 CENTRAL | 543038 | LENEXA 5 | 161 | 37.0383 | 37.1132 | 0.0749
GEN-2020-073 | 03 CENTRAL | 543041 | SHAWNEE5 | 161 | 27.5878 | 27.6161 | 0.0283
GEN-2020-073 | 03 CENTRAL | 543044 | MOONLT 5 | 161 | 17.7906 | 17.879 | 0.0884
GEN-2020-073 | 03 CENTRAL | 543048 | COLLEGE5 | 161 | 30.3877 | 30.4527 | 0.065
GEN-2020-073 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.8146 | 30.8912 | 0.0766
GEN-2020-073 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.806 | 10.8531 | 0.0471
GEN-2020-073 | 03 CENTRAL | 543055 | SEOTTWA5 | 161 | 7.4197 | 8.2167 | 0.797
GEN-2020-073 | 03 CENTRAL | 543056 | GARDNER5 | 161 | 16.5673 | 16.6436 | 0.0763
GEN-2020-073 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.1367 | 6.1695 | 0.0328
GEN-2020-073 | 03 CENTRAL | 543066 | S.OTTWA5 | 161 | 7.3835 | 8.0533 | 0.6698
GEN-2020-073 | 03 CENTRAL | 543067 | CENTENL5 | 161 | 10.6237 | 10.8095 | 0.1858
GEN-2020-073 | 03 CENTRAL | 543068 | WAGSTAF5 | 161 | 14.4011 | 14.5072 | 0.1061
GEN-2020-073 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.664 | 10.897 | 0.233
GEN-2020-073 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.1412 | 10.6325 | 0.4913
GEN-2020-073 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.826 | 29.1564 | 0.3304
GEN-2020-073 | 03 CENTRAL | 543112 | OSAWAT 5 | 161 | 10.5734 | 10.8018 | 0.2284
GEN-2020-073 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 22.0351 | 22.2051 | 0.17
GEN-2020-073 | 03 CENTRAL | 543135 | OSAWTM_CAP5 | 161 | 9.9636 | 10.1661 | 0.2025
GEN-2020-073 | 03 CENTRAL | 543166 | NEASTOTTW5 | 161 | 6.4134 | 7.0004 | 0.587
GEN-2020-073 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.1293 | 27.154 | 0.0247
GEN-2020-073 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.1293 | 27.154 | 0.0247
GEN-2020-073 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 6.8837 | 6.8995 | 0.0158
GEN-2020-073 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 5.4292 | 5.4384 | 0.0092
GEN-2020-073 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8162 | 2.8163 | 0.0001
GEN-2020-073 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6735 | 0.6735 | 0
GEN-2020-073 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6451 | 0.6451 | 0
GEN-2020-073 | 03 CENTRAL | 546742 | METRO 5 | 161 | 27.1167 | 27.1379 | 0.0212
GEN-2020-073 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.4543 | 27.5465 | 0.0922
GEN-2020-073 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.3782 | 27.4699 | 0.0917
GEN-2020-073 | 03 CENTRAL | 762405 | ASG-2018-010 | 161 | 3.3082 | 3.3567 | 0.0485
GEN-2020-073 | 03 CENTRAL | 762416 | ASG-2018-011 | 161 | 2.961 | 3.0608 | 0.0998
GEN-2020-073 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 12.0101 | 12.0113 | 0.0012
GEN-2020-073 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.8584 | 20.9028 | 0.0444
GEN-2020-073 | 03 CENTRAL | 764390 | GEN-2020-073 | 161 | 7.4337 | 8.3619 | 0.9282
GEN-2020-073 | 03 CENTRAL | 764400 | G20-073-TAP | 161 | 7.5153 | 8.4423 | 0.927
GEN-2020-073 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.8585 | 20.9029 | 0.0444
GEN-2020-073 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.6045 | 24.6242 | 0.0197
GEN-2020-073 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 27.091 | 27.1153 | 0.0243
GEN-2020-079 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.2572 | 16.2782 | 0.021
GEN-2020-079 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5616 | 24.5713 | 0.0097
GEN-2020-079 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 40.8822 | 40.8915 | 0.0093
GEN-2020-079 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.1864 | 13.1981 | 0.0117
GEN-2020-079 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.1564 | 13.1619 | 0.0055
GEN-2020-079 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.7529 | 15.8465 | 0.0936
GEN-2020-079 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.8262 | 16.9483 | 0.1221
GEN-2020-079 | 03 CENTRAL | 509807 | ONETA--7 | 345 | 29.0046 | 29.0084 | 0.0038
GEN-2020-079 | 03 CENTRAL | 509836 | OEC 7 | 345 | 28.7444 | 28.7481 | 0.0037
GEN-2020-079 | 03 CENTRAL | 509852 | T.NO.--7 | 345 | 23.5839 | 23.5895 | 0.0056
GEN-2020-079 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.4741 | 11.478 | 0.0039
GEN-2020-079 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.0473 | 12.0572 | 0.0099
GEN-2020-079 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.1648 | 19.1718 | 0.007
GEN-2020-079 | 03 CENTRAL | 510417 | VINTAJC4 | 138 | 5.2246 | 5.2311 | 0.0065
GEN-2020-079 | 03 CENTRAL | 512630 | MIAMI 2 | 69 | 12.4649 | 12.505 | 0.0401
GEN-2020-079 | 03 CENTRAL | 512631 | MIAMI 5 | 161 | 9.6216 | 9.6878 | 0.0662
GEN-2020-079 | 03 CENTRAL | 512632 | AFTON 5 | 161 | 8.5518 | 8.5788 | 0.027
GEN-2020-079 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.9026 | 26.9139 | 0.0113
GEN-2020-079 | 03 CENTRAL | 513020 | MIAMI1 2 | 69 | 10.6721 | 10.7015 | 0.0294
GEN-2020-079 | 03 CENTRAL | 513022 | MIAMI4 2 | 69 | 9.0818 | 9.1031 | 0.0213
GEN-2020-079 | 03 CENTRAL | 513024 | MIAMI3 2 | 69 | 9.9112 | 9.9366 | 0.0254
GEN-2020-079 | 03 CENTRAL | 513026 | COMMTP 2 | 69 | 9.5262 | 9.5496 | 0.0234
GEN-2020-079 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.7391 | 16.7394 | 0.0003
GEN-2020-079 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9127 | 11.9338 | 0.0211
GEN-2020-079 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.0201 | 11.0381 | 0.018
GEN-2020-079 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7623 | 9.7665 | 0.0042
GEN-2020-079 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4915 | 9.4954 | 0.0039
GEN-2020-079 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1615 | 18.2288 | 0.0673
GEN-2020-079 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.2001 | 18.2036 | 0.0035
GEN-2020-079 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.2248 | 16.2276 | 0.0028
GEN-2020-079 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3764 | 10.3802 | 0.0038
GEN-2020-079 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2167 | 9.2196 | 0.0029
GEN-2020-079 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5696 | 13.5715 | 0.0019
GEN-2020-079 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1346 | 5.1385 | 0.0039
GEN-2020-079 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.2008 | 8.2126 | 0.0118
GEN-2020-079 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.1976 | 8.2093 | 0.0117
GEN-2020-079 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.5687 | 23.7942 | 0.2255
GEN-2020-079 | 03 CENTRAL | 532938 | FRANKLIN5 | 161 | 8.0948 | 8.118 | 0.0232
GEN-2020-079 | 03 CENTRAL | 533001 | ALTOONA4 | 138 | 9.3593 | 9.3677 | 0.0084
GEN-2020-079 | 03 CENTRAL | 533002 | DEARING4 | 138 | 9.6046 | 9.6105 | 0.0059
GEN-2020-079 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.6043 | 7.6098 | 0.0055
GEN-2020-079 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 13.0972 | 13.1323 | 0.0351
GEN-2020-079 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2511 | 7.2579 | 0.0068
GEN-2020-079 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.2215 | 25.3852 | 0.1637
GEN-2020-079 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.2644 | 25.4284 | 0.164
GEN-2020-079 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.1473 | 25.3096 | 0.1623
GEN-2020-079 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.969 | 8.9742 | 0.0052
GEN-2020-079 | 03 CENTRAL | 533640 | MCKEE 2 | 69 | 4.3674 | 4.3689 | 0.0015
GEN-2020-079 | 03 CENTRAL | 533645 | SE9HIAT2 | 69 | 3.8904 | 3.8917 | 0.0013
GEN-2020-079 | 03 CENTRAL | 533647 | UN1ELSM2 | 69 | 8.0798 | 8.0836 | 0.0038
GEN-2020-079 | 03 CENTRAL | 533650 | UN8HUMB2 | 69 | 4.5544 | 4.5552 | 0.0008
GEN-2020-079 | 03 CENTRAL | 533654 | ZILAJCT2 | 69 | 6.4697 | 6.4713 | 0.0016
GEN-2020-079 | 03 CENTRAL | 533673 | ALTOO E2 | 69 | 4.3704 | 4.3713 | 0.0009
GEN-2020-079 | 03 CENTRAL | 533674 | ALTOO W2 | 69 | 3.1733 | 3.1738 | 0.0005
GEN-2020-079 | 03 CENTRAL | 533675 | ARGO 2 | 69 | 3.0979 | 3.0984 | 0.0005
GEN-2020-079 | 03 CENTRAL | 533692 | YELLOWJ2 | 69 | 1.4668 | 1.4669 | 0.0001
GEN-2020-079 | 03 CENTRAL | 533695 | LABETTE2 | 69 | 4.2176 | 4.2198 | 0.0022
GEN-2020-079 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.3928 | 6.3978 | 0.005
GEN-2020-079 | 03 CENTRAL | 533697 | LIBERT-2 | 69 | 8.7116 | 8.7148 | 0.0032
GEN-2020-079 | 03 CENTRAL | 533699 | NEODESH2 | 69 | 2.7827 | 2.7831 | 0.0004
GEN-2020-079 | 03 CENTRAL | 533700 | NEODJCT2 | 69 | 3.7618 | 3.7625 | 0.0007
GEN-2020-079 | 03 CENTRAL | 533701 | NEW ALB2 | 69 | 1.5565 | 1.5566 | 0.0001
GEN-2020-079 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.3268 | 6.3318 | 0.005
GEN-2020-079 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.7611 | 8.7709 | 0.0098
GEN-2020-079 | 03 CENTRAL | 533704 | PARSONS2 | 69 | 5.0866 | 5.0898 | 0.0032
GEN-2020-079 | 03 CENTRAL | 533705 | STUDBKR2 | 69 | 1.8869 | 1.8871 | 0.0002
GEN-2020-079 | 03 CENTRAL | 533706 | RA5HIPR2 | 69 | 4.3682 | 4.3691 | 0.0009
GEN-2020-079 | 03 CENTRAL | 533707 | RA6BROO2 | 69 | 2.6707 | 2.6711 | 0.0004
GEN-2020-079 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.6293 | 7.637 | 0.0077
GEN-2020-079 | 03 CENTRAL | 533763 | HUDSON-2 | 69 | 4.8136 | 4.8172 | 0.0036
GEN-2020-079 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 23.9539 | 24.0283 | 0.0744
GEN-2020-079 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.3985 | 6.4041 | 0.0056
GEN-2020-079 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.7594 | 5.7645 | 0.0051
GEN-2020-079 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 23.9789 | 24.0535 | 0.0746
GEN-2020-079 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.747 | 20.748 | 0.001
GEN-2020-079 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6772 | 2.6772 | 0
GEN-2020-079 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.9422 | 20.9429 | 0.0007
GEN-2020-079 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6167 | 27.6185 | 0.0018
GEN-2020-079 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.1262 | 30.1269 | 0.0007
GEN-2020-079 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.8353 | 25.8373 | 0.002
GEN-2020-079 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9733 | 40.9756 | 0.0023
GEN-2020-079 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8887 | 27.8947 | 0.006
GEN-2020-079 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.853 | 10.8531 | 0.0001
GEN-2020-079 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.1674 | 6.1695 | 0.0021
GEN-2020-079 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.1557 | 29.1564 | 0.0007
GEN-2020-079 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.1484 | 27.154 | 0.0056
GEN-2020-079 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.1484 | 27.154 | 0.0056
GEN-2020-079 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 6.894 | 6.8995 | 0.0055
GEN-2020-079 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 5.4352 | 5.4384 | 0.0032
GEN-2020-079 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8163 | 2.8163 | 0
GEN-2020-079 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6735 | 0.6735 | 0
GEN-2020-079 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6451 | 0.6451 | 0
GEN-2020-079 | 03 CENTRAL | 547409 | SCAM66 2 | 69 | 2.5491 | 2.5519 | 0.0028
GEN-2020-079 | 03 CENTRAL | 547411 | COL282 2 | 69 | 4.6898 | 4.7 | 0.0102
GEN-2020-079 | 03 CENTRAL | 547412 | SEK225T2 | 69 | 3.6145 | 3.6205 | 0.006
GEN-2020-079 | 03 CENTRAL | 547413 | SEK225 2 | 69 | 3.5675 | 3.5733 | 0.0058
GEN-2020-079 | 03 CENTRAL | 547414 | SMN425 2 | 69 | 2.0347 | 2.0365 | 0.0018
GEN-2020-079 | 03 CENTRAL | 547415 | SHR444 2 | 69 | 2.805 | 2.8085 | 0.0035
GEN-2020-079 | 03 CENTRAL | 547416 | CHE299T2 | 69 | 1.907 | 1.9085 | 0.0015
GEN-2020-079 | 03 CENTRAL | 547417 | CHE299 2 | 69 | 1.8266 | 1.8279 | 0.0013
GEN-2020-079 | 03 CENTRAL | 547418 | CHE300 2 | 69 | 1.868 | 1.8694 | 0.0014
GEN-2020-079 | 03 CENTRAL | 547419 | TWN388 2 | 69 | 1.8148 | 1.8161 | 0.0013
GEN-2020-079 | 03 CENTRAL | 547420 | WEL186 2 | 69 | 1.1673 | 1.1678 | 0.0005
GEN-2020-079 | 03 CENTRAL | 547431 | WEB105 2 | 69 | 8.1164 | 8.1362 | 0.0198
GEN-2020-079 | 03 CENTRAL | 547438 | EXP449T2 | 69 | 9.0942 | 9.1178 | 0.0236
GEN-2020-079 | 03 CENTRAL | 547439 | EXP4492 | 69 | 7.5452 | 7.5613 | 0.0161
GEN-2020-079 | 03 CENTRAL | 547455 | SCM66T 2 | 69 | 4.5136 | 4.5228 | 0.0092
GEN-2020-079 | 03 CENTRAL | 547459 | WWR477 | 161 | 22.1293 | 22.5477 | 0.4184
GEN-2020-079 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.3642 | 14.5045 | 0.1403
GEN-2020-079 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 16.4307 | 16.6218 | 0.1911
GEN-2020-079 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 19.8295 | 20.1817 | 0.3522
GEN-2020-079 | 03 CENTRAL | 547469 | RIV4525 | 161 | 23.9586 | 24.955 | 0.9964
GEN-2020-079 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 18.9837 | 19.2966 | 0.3129
GEN-2020-079 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 17.6976 | 17.8729 | 0.1753
GEN-2020-079 | 03 CENTRAL | 547476 | ASB349 5 | 161 | 11.2627 | 11.3223 | 0.0596
GEN-2020-079 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.6235 | 12.7408 | 0.1173
GEN-2020-079 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.198 | 12.2264 | 0.0284
GEN-2020-079 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 19.9715 | 20.2614 | 0.2899
GEN-2020-079 | 03 CENTRAL | 547486 | HOC404 4 | 138 | 6.7322 | 6.7646 | 0.0324
GEN-2020-079 | 03 CENTRAL | 547487 | HOC404 5 | 161 | 13.414 | 13.6178 | 0.2038
GEN-2020-079 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.5241 | 14.6931 | 0.169
GEN-2020-079 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 17.9984 | 18.2669 | 0.2685
GEN-2020-079 | 03 CENTRAL | 547498 | STL439 5 | 161 | 24.1684 | 24.6682 | 0.4998
GEN-2020-079 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.4304 | 14.5565 | 0.1261
GEN-2020-079 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 22.6612 | 23.5252 | 0.864
GEN-2020-079 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 22.2435 | 23.0916 | 0.8481
GEN-2020-079 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 23.5231 | 24.4738 | 0.9507
GEN-2020-079 | 03 CENTRAL | 547525 | JOP 59 2 | 69 | 19.8775 | 20.0155 | 0.138
GEN-2020-079 | 03 CENTRAL | 547526 | JOP 64 2 | 69 | 19.5188 | 19.6517 | 0.1329
GEN-2020-079 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.6854 | 9.7134 | 0.028
GEN-2020-079 | 03 CENTRAL | 547530 | COL 94 2 | 69 | 6.5734 | 6.5932 | 0.0198
GEN-2020-079 | 03 CENTRAL | 547532 | CAR108 2 | 69 | 8.4995 | 8.5166 | 0.0171
GEN-2020-079 | 03 CENTRAL | 547533 | ATL109 2 | 69 | 21.0862 | 21.2225 | 0.1363
GEN-2020-079 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 18.194 | 18.3049 | 0.1109
GEN-2020-079 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 21.1584 | 21.321 | 0.1626
GEN-2020-079 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 17.8613 | 18.0208 | 0.1595
GEN-2020-079 | 03 CENTRAL | 547551 | GAT258 2 | 69 | 14.6366 | 14.7041 | 0.0675
GEN-2020-079 | 03 CENTRAL | 547554 | BAX271 2 | 69 | 9.6726 | 9.7155 | 0.0429
GEN-2020-079 | 03 CENTRAL | 547555 | GAL278 2 | 69 | 13.282 | 13.3508 | 0.0688
GEN-2020-079 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 16.1246 | 16.209 | 0.0844
GEN-2020-079 | 03 CENTRAL | 547557 | JOP284 2 | 69 | 16.9067 | 17.0048 | 0.0981
GEN-2020-079 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 18.3442 | 18.4638 | 0.1196
GEN-2020-079 | 03 CENTRAL | 547590 | QUA377 2 | 69 | 7.3319 | 7.3542 | 0.0223
GEN-2020-079 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.5353 | 15.6115 | 0.0762
GEN-2020-079 | 03 CENTRAL | 547601 | HOC404 2 | 69 | 9.7911 | 9.8337 | 0.0426
GEN-2020-079 | 03 CENTRAL | 547602 | RIV406 2 | 69 | 15.8657 | 15.991 | 0.1253
GEN-2020-079 | 03 CENTRAL | 547607 | JOP422 5 | 161 | 13.3712 | 13.4873 | 0.1161
GEN-2020-079 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 16.0375 | 16.1243 | 0.0868
GEN-2020-079 | 03 CENTRAL | 547685 | PLB447 2 | 69 | 14.5924 | 14.6583 | 0.0659
GEN-2020-079 | 03 CENTRAL | 547690 | GLF339 2 | 69 | 12.0738 | 12.1398 | 0.066
GEN-2020-079 | 03 CENTRAL | 547728 | GAL278T | 69 | 13.5736 | 13.6455 | 0.0719
GEN-2020-079 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 15.0213 | 15.3177 | 0.2964
GEN-2020-079 | 03 CENTRAL | 588500 | GEN-2017-005 | 161 | 6.9089 | 6.9194 | 0.0105
GEN-2020-079 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.9926 | 7.0033 | 0.0107
GEN-2020-079 | 03 CENTRAL | 588660 | GEN-2017-022 | 138 | 8.9846 | 8.9923 | 0.0077
GEN-2020-079 | 03 CENTRAL | 589200 | GEN-2017-082 | 161 | 7.6577 | 7.6839 | 0.0262
GEN-2020-079 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.9602 | 11.9669 | 0.0067
GEN-2020-079 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.9602 | 11.9669 | 0.0067
GEN-2020-079 | 03 CENTRAL | 760242 | GEN-2017-188 | 161 | 2.0289 | 2.03 | 0.0011
GEN-2020-079 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5448 | 27.5465 | 0.0017
GEN-2020-079 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4682 | 27.4699 | 0.0017
GEN-2020-079 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9821 | 12.0113 | 0.0292
GEN-2020-079 | 03 CENTRAL | 763109 | GEN-2018-079 | 138 | 6.6027 | 6.604 | 0.0013
GEN-2020-079 | 03 CENTRAL | 763113 | G18-079-TAP | 138 | 9.3908 | 9.3935 | 0.0027
GEN-2020-079 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.0199 | 15.4402 | 1.4203
GEN-2020-079 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.2564 | 18.6507 | 1.3943
GEN-2020-079 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.9021 | 20.9028 | 0.0007
GEN-2020-079 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.9022 | 20.9029 | 0.0007
GEN-2020-079 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 9.0304 | 9.0335 | 0.0031
GEN-2020-079 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3545 | 10.3587 | 0.0042
GEN-2020-079 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.6196 | 24.6242 | 0.0046
GEN-2020-079 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 27.1097 | 27.1153 | 0.0056
GEN-2020-088 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.5879 | 10.5898 | 0.0019
GEN-2020-088 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.8591 | 13.8663 | 0.0072
GEN-2020-088 | 03 CENTRAL | 300081 | 5GAINES | 161 | 5.9486 | 5.949 | 0.0004
GEN-2020-088 | 03 CENTRAL | 300089 | 5JAMESV | 161 | 16.1603 | 16.1716 | 0.0113
GEN-2020-088 | 03 CENTRAL | 300095 | 5MANSFDMN | 161 | 9.1554 | 9.1564 | 0.001
GEN-2020-088 | 03 CENTRAL | 300101 | 5MORGAN | 161 | 19.7135 | 19.7268 | 0.0133
GEN-2020-088 | 03 CENTRAL | 300118 | 5STKAEC | 161 | 9.3305 | 9.3322 | 0.0017
GEN-2020-088 | 03 CENTRAL | 300348 | 5BTLFD | 161 | 22.0025 | 22.0209 | 0.0184
GEN-2020-088 | 03 CENTRAL | 300646 | 2BELLAMY | 69 | 2.6489 | 2.649 | 0.0001
GEN-2020-088 | 03 CENTRAL | 300647 | 2BLLMYTP | 69 | 5.3234 | 5.3237 | 0.0003
GEN-2020-088 | 03 CENTRAL | 300649 | 2JASPER | 69 | 4.9496 | 4.9511 | 0.0015
GEN-2020-088 | 03 CENTRAL | 300651 | 2LAMR | 69 | 10.1554 | 10.1573 | 0.0019
GEN-2020-088 | 03 CENTRAL | 300652 | 2LAMRCTS | 69 | 3.9493 | 3.9495 | 0.0002
GEN-2020-088 | 03 CENTRAL | 300653 | 2MEDOC | 69 | 2.4931 | 2.4935 | 0.0004
GEN-2020-088 | 03 CENTRAL | 300656 | 2JACK ST | 69 | 7.5957 | 7.597 | 0.0013
GEN-2020-088 | 03 CENTRAL | 300657 | 2ASHGRV | 69 | 4.0526 | 4.0529 | 0.0003
GEN-2020-088 | 03 CENTRAL | 300658 | 2BILLNG | 69 | 8.4418 | 8.4461 | 0.0043
GEN-2020-088 | 03 CENTRAL | 300659 | 2BOWRML | 69 | 6.1664 | 6.1696 | 0.0032
GEN-2020-088 | 03 CENTRAL | 300660 | 2BRNSPG | 69 | 3.8413 | 3.8424 | 0.0011
GEN-2020-088 | 03 CENTRAL | 300663 | 2CASSIDY | 69 | 6.957 | 6.9578 | 0.0008
GEN-2020-088 | 03 CENTRAL | 300664 | 2CAVESP | 69 | 2.4073 | 2.4074 | 0.0001
GEN-2020-088 | 03 CENTRAL | 300666 | 2CLRKSN | 69 | 2.8515 | 2.8522 | 0.0007
GEN-2020-088 | 03 CENTRAL | 300667 | 2CRANE | 69 | 3.3457 | 3.3468 | 0.0011
GEN-2020-088 | 03 CENTRAL | 300668 | 2DADEVL | 69 | 5.859 | 5.8596 | 0.0006
GEN-2020-088 | 03 CENTRAL | 300669 | 2ELWOOD | 69 | 5.4294 | 5.4299 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300670 | 2EPURDY | 69 | 3.634 | 3.6354 | 0.0014
GEN-2020-088 | 03 CENTRAL | 300673 | 2JAMESV | 69 | 12.2334 | 12.2361 | 0.0027
GEN-2020-088 | 03 CENTRAL | 300677 | 2MTVRN | 69 | 9.1049 | 9.1108 | 0.0059
GEN-2020-088 | 03 CENTRAL | 300678 | 5NIXA-1 | 161 | 19.4469 | 19.4643 | 0.0174
GEN-2020-088 | 03 CENTRAL | 300679 | 2PRDYTP | 69 | 5.1713 | 5.1742 | 0.0029
GEN-2020-088 | 03 CENTRAL | 300680 | 2VERONA | 69 | 6.5924 | 6.5983 | 0.0059
GEN-2020-088 | 03 CENTRAL | 300681 | 2BUTRFLD | 69 | 5.1752 | 5.1773 | 0.0021
GEN-2020-088 | 03 CENTRAL | 300685 | 2LAMARPT | 69 | 8.5719 | 8.5732 | 0.0013
GEN-2020-088 | 03 CENTRAL | 300718 | 5CLEVCOV | 161 | 12.1615 | 12.1665 | 0.005
GEN-2020-088 | 03 CENTRAL | 300719 | 5COMPTN | 161 | 11.545 | 11.55 | 0.005
GEN-2020-088 | 03 CENTRAL | 300723 | 2PARDIS | 69 | 5.1152 | 5.1157 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300726 | 5RIVRDL | 161 | 11.6955 | 11.7013 | 0.0058
GEN-2020-088 | 03 CENTRAL | 300727 | 5ROARK | 161 | 10.1792 | 10.1831 | 0.0039
GEN-2020-088 | 03 CENTRAL | 300735 | 2T.ROCK | 69 | 12.4328 | 12.4357 | 0.0029
GEN-2020-088 | 03 CENTRAL | 300744 | 2DMNDGR | 69 | 2.6049 | 2.6058 | 0.0009
GEN-2020-088 | 03 CENTRAL | 300745 | 2DMNDTP | 69 | 5.5961 | 5.6005 | 0.0044
GEN-2020-088 | 03 CENTRAL | 300748 | 2NEOSAC | 69 | 10.1994 | 10.2059 | 0.0065
GEN-2020-088 | 03 CENTRAL | 300750 | 2NEOSHO | 69 | 8.6783 | 8.6827 | 0.0044
GEN-2020-088 | 03 CENTRAL | 300751 | 2REEDS | 69 | 6.5657 | 6.5717 | 0.006
GEN-2020-088 | 03 CENTRAL | 300753 | 2SIMS | 69 | 3.7058 | 3.7063 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300754 | 2SPGCTP | 69 | 5.653 | 5.6553 | 0.0023
GEN-2020-088 | 03 CENTRAL | 300755 | 2SPGCTY | 69 | 2.7585 | 2.759 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300758 | 2SWTWT | 69 | 4.2778 | 4.2789 | 0.0011
GEN-2020-088 | 03 CENTRAL | 300762 | 2WNTWRT | 69 | 4.771 | 4.7738 | 0.0028
GEN-2020-088 | 03 CENTRAL | 300763 | 2WASHBRN | 69 | 6.7989 | 6.8007 | 0.0018
GEN-2020-088 | 03 CENTRAL | 300764 | 2SPURGNTP | 69 | 3.1953 | 3.1961 | 0.0008
GEN-2020-088 | 03 CENTRAL | 300765 | 2SPURGN | 69 | 2.9219 | 2.9225 | 0.0006
GEN-2020-088 | 03 CENTRAL | 300774 | 2EUDORA | 69 | 6.1733 | 6.174 | 0.0007
GEN-2020-088 | 03 CENTRAL | 300782 | 2MORGAN | 69 | 7.1199 | 7.1207 | 0.0008
GEN-2020-088 | 03 CENTRAL | 300788 | 2SLAGLE | 69 | 6.238 | 6.2385 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.9592 | 8.9605 | 0.0013
GEN-2020-088 | 03 CENTRAL | 300800 | 2BONA | 69 | 3.4956 | 3.4958 | 0.0002
GEN-2020-088 | 03 CENTRAL | 300805 | 5RIVERSIDE | 161 | 11.0917 | 11.0969 | 0.0052
GEN-2020-088 | 03 CENTRAL | 300816 | 5COLLINS | 161 | 6.742 | 6.7425 | 0.0005
GEN-2020-088 | 03 CENTRAL | 300824 | 2SELIGM | 69 | 6.1882 | 6.1898 | 0.0016
GEN-2020-088 | 03 CENTRAL | 301057 | 5GRVSPG | 161 | 7.0445 | 7.0449 | 0.0004
GEN-2020-088 | 03 CENTRAL | 301058 | 2HARTVL | 69 | 3.3814 | 3.3815 | 0.0001
GEN-2020-088 | 03 CENTRAL | 301128 | 5MTNGRV | 161 | 6.1412 | 6.1415 | 0.0003
GEN-2020-088 | 03 CENTRAL | 301161 | 5LOGAN | 161 | 13.7264 | 13.7325 | 0.0061
GEN-2020-088 | 03 CENTRAL | 301168 | 2MANSFL | 69 | 10.6688 | 10.6694 | 0.0006
GEN-2020-088 | 03 CENTRAL | 301360 | 2T.ROCKSW | 69 | 12.7107 | 12.7137 | 0.003
GEN-2020-088 | 03 CENTRAL | 301393 | 2ROUNDGROVE | 69 | 4.3116 | 4.3126 | 0.001
GEN-2020-088 | 03 CENTRAL | 301395 | 2ROUNDGRVETP | 69 | 4.4846 | 4.4856 | 0.001
GEN-2020-088 | 03 CENTRAL | 301521 | 5REEDSP | 161 | 8.6396 | 8.6465 | 0.0069
GEN-2020-088 | 03 CENTRAL | 301547 | 5MANSFDTF | 161 | 9.1332 | 9.1342 | 0.001
GEN-2020-088 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 19.712 | 19.7253 | 0.0133
GEN-2020-088 | 03 CENTRAL | 338099 | 5GRANDVIEW% | 161 | 9.7518 | 9.7545 | 0.0027
GEN-2020-088 | 03 CENTRAL | 338120 | 5S.LEAD HILL | 161 | 6.6087 | 6.6094 | 0.0007
GEN-2020-088 | 03 CENTRAL | 338554 | 2OSAGE CRK-1 | 69 | 4.6807 | 4.6809 | 0.0002
GEN-2020-088 | 03 CENTRAL | 338556 | 2OSAGE CRK-2 | 69 | 4.2166 | 4.2168 | 0.0002
GEN-2020-088 | 03 CENTRAL | 338682 | 5OSAGE CRK#! | 161 | 9.8107 | 9.8132 | 0.0025
GEN-2020-088 | 03 CENTRAL | 503508 | 2LAMRLNDFL | 69 | 3.3636 | 3.3638 | 0.0002
GEN-2020-088 | 03 CENTRAL | 504000 | AVOCA 5 | 161 | 9.4226 | 9.4243 | 0.0017
GEN-2020-088 | 03 CENTRAL | 504001 | AVOCA_1 2 | 69 | 6.735 | 6.7354 | 0.0004
GEN-2020-088 | 03 CENTRAL | 505472 | TABLE R5 | 161 | 15.119 | 15.1273 | 0.0083
GEN-2020-088 | 03 CENTRAL | 505474 | TABLE R2 | 69 | 13.7137 | 13.7172 | 0.0035
GEN-2020-088 | 03 CENTRAL | 505480 | BEAVER 5 | 161 | 11.3018 | 11.3056 | 0.0038
GEN-2020-088 | 03 CENTRAL | 505485 | WASHBURN5 | 161 | 8.3482 | 8.3523 | 0.0041
GEN-2020-088 | 03 CENTRAL | 505486 | NEO SPA5 | 161 | 15.8038 | 15.8465 | 0.0427
GEN-2020-088 | 03 CENTRAL | 505488 | CARTHAG5 | 161 | 16.7936 | 16.9483 | 0.1547
GEN-2020-088 | 03 CENTRAL | 505490 | CARTHG 2 | 69 | 14.0708 | 14.1051 | 0.0343
GEN-2020-088 | 03 CENTRAL | 505492 | SPRGFLD5 | 161 | 27.4969 | 27.533 | 0.0361
GEN-2020-088 | 03 CENTRAL | 505494 | SPRGFLD2 | 69 | 16.2019 | 16.2072 | 0.0053
GEN-2020-088 | 03 CENTRAL | 505496 | NIXA 5 | 161 | 12.7432 | 12.7504 | 0.0072
GEN-2020-088 | 03 CENTRAL | 505498 | STOCKTN5 | 161 | 10.0558 | 10.0577 | 0.0019
GEN-2020-088 | 03 CENTRAL | 505501 | NIXA 2 | 69 | 12.4998 | 12.5026 | 0.0028
GEN-2020-088 | 03 CENTRAL | 505541 | NIXA DT2 | 69 | 10.9384 | 10.9406 | 0.0022
GEN-2020-088 | 03 CENTRAL | 505543 | NX ESPY2 | 69 | 11.376 | 11.3783 | 0.0023
GEN-2020-088 | 03 CENTRAL | 505545 | NIX_SLR_U1_2 | 69 | 8.8139 | 8.8153 | 0.0014
GEN-2020-088 | 03 CENTRAL | 506932 | EUREKA 5 | 161 | 10.5019 | 10.505 | 0.0031
GEN-2020-088 | 03 CENTRAL | 506934 | FLINTCR5 | 161 | 34.4494 | 34.4556 | 0.0062
GEN-2020-088 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.7047 | 15.7075 | 0.0028
GEN-2020-088 | 03 CENTRAL | 506979 | SHIPERD7 | 345 | 10.563 | 10.5643 | 0.0013
GEN-2020-088 | 03 CENTRAL | 510411 | GROVE 5 | 161 | 5.9745 | 5.9759 | 0.0014
GEN-2020-088 | 03 CENTRAL | 512750 | TONECE7 | 345 | 15.4768 | 15.4793 | 0.0025
GEN-2020-088 | 03 CENTRAL | 532932 | LITCH 5 | 161 | 9.1878 | 9.1997 | 0.0119
GEN-2020-088 | 03 CENTRAL | 547400 | MON376J2 | 69 | 4.1277 | 4.131 | 0.0033
GEN-2020-088 | 03 CENTRAL | 547401 | MON376 2 | 69 | 6.6967 | 6.7053 | 0.0086
GEN-2020-088 | 03 CENTRAL | 547402 | MON416J2 | 69 | 3.6352 | 3.6378 | 0.0026
GEN-2020-088 | 03 CENTRAL | 547403 | MON416 2 | 69 | 3.5408 | 3.5432 | 0.0024
GEN-2020-088 | 03 CENTRAL | 547404 | PUR390 2 | 69 | 1.7995 | 1.8001 | 0.0006
GEN-2020-088 | 03 CENTRAL | 547405 | MON352J2 | 69 | 7.923 | 7.9351 | 0.0121
GEN-2020-088 | 03 CENTRAL | 547406 | MON352 2 | 69 | 7.6111 | 7.6222 | 0.0111
GEN-2020-088 | 03 CENTRAL | 547407 | MON311J2 | 69 | 6.7816 | 6.7905 | 0.0089
GEN-2020-088 | 03 CENTRAL | 547408 | MON311 2 | 69 | 6.6967 | 6.7053 | 0.0086
GEN-2020-088 | 03 CENTRAL | 547424 | RES364 2 | 69 | 4.0711 | 4.0724 | 0.0013
GEN-2020-088 | 03 CENTRAL | 547428 | SWC414 2 | 69 | 3.8237 | 3.8241 | 0.0004
GEN-2020-088 | 03 CENTRAL | 547430 | SAR362 2 | 69 | 2.0304 | 2.031 | 0.0006
GEN-2020-088 | 03 CENTRAL | 547431 | WEB105 2 | 69 | 8.1317 | 8.1362 | 0.0045
GEN-2020-088 | 03 CENTRAL | 547438 | EXP449T2 | 69 | 9.1131 | 9.1178 | 0.0047
GEN-2020-088 | 03 CENTRAL | 547439 | EXP4492 | 69 | 7.558 | 7.5613 | 0.0033
GEN-2020-088 | 03 CENTRAL | 547449 | PRC460 2 | 69 | 5.7552 | 5.7606 | 0.0054
GEN-2020-088 | 03 CENTRAL | 547450 | JAS344T2 | 69 | 5.1109 | 5.112 | 0.0011
GEN-2020-088 | 03 CENTRAL | 547451 | JAS344 | 69 | 4.4463 | 4.4472 | 0.0009
GEN-2020-088 | 03 CENTRAL | 547459 | WWR477 | 161 | 22.4948 | 22.5477 | 0.0529
GEN-2020-088 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 14.475 | 14.5045 | 0.0295
GEN-2020-088 | 03 CENTRAL | 547463 | KOD471 2 | 69 | 12.2499 | 12.2616 | 0.0117
GEN-2020-088 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 16.5463 | 16.6218 | 0.0755
GEN-2020-088 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 20.111 | 20.1817 | 0.0707
GEN-2020-088 | 03 CENTRAL | 547468 | AUR124 5 | 161 | 10.7939 | 10.8322 | 0.0383
GEN-2020-088 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.9037 | 24.955 | 0.0513
GEN-2020-088 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 19.2478 | 19.2966 | 0.0488
GEN-2020-088 | 03 CENTRAL | 547471 | NEO184 5 | 161 | 14.5741 | 14.6078 | 0.0337
GEN-2020-088 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 17.8188 | 17.8729 | 0.0541
GEN-2020-088 | 03 CENTRAL | 547473 | RDS295 5 | 161 | 8.0668 | 8.074 | 0.0072
GEN-2020-088 | 03 CENTRAL | 547476 | ASB349 5 | 161 | 11.2984 | 11.3223 | 0.0239
GEN-2020-088 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.7119 | 12.7408 | 0.0289
GEN-2020-088 | 03 CENTRAL | 547478 | DAD368 5 | 161 | 18.6302 | 18.6429 | 0.0127
GEN-2020-088 | 03 CENTRAL | 547479 | LAR382 5 | 161 | 15.2133 | 15.696 | 0.4827
GEN-2020-088 | 03 CENTRAL | 547480 | MON383 5 | 161 | 12.1297 | 12.2264 | 0.0967
GEN-2020-088 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 20.2082 | 20.2614 | 0.0532
GEN-2020-088 | 03 CENTRAL | 547484 | DEC392 5 | 161 | 15.7703 | 15.7737 | 0.0034
GEN-2020-088 | 03 CENTRAL | 547485 | CAR395 5 | 161 | 12.4896 | 12.5634 | 0.0738
GEN-2020-088 | 03 CENTRAL | 547489 | BRN413 5 | 161 | 10.7344 | 10.7399 | 0.0055
GEN-2020-088 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.6551 | 14.6931 | 0.038
GEN-2020-088 | 03 CENTRAL | 547491 | PUR421 5 | 161 | 9.7504 | 9.7817 | 0.0313
GEN-2020-088 | 03 CENTRAL | 547493 | BOL431 5 | 161 | 6.1398 | 6.1412 | 0.0014
GEN-2020-088 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 18.1985 | 18.2669 | 0.0684
GEN-2020-088 | 03 CENTRAL | 547496 | NOL435 5 | 161 | 10.21 | 10.2153 | 0.0053
GEN-2020-088 | 03 CENTRAL | 547497 | RVS438 5 | 161 | 12.3892 | 12.3959 | 0.0067
GEN-2020-088 | 03 CENTRAL | 547498 | STL439 5 | 161 | 24.6049 | 24.6682 | 0.0633
GEN-2020-088 | 03 CENTRAL | 547499 | CPK446 5 | 161 | 8.77 | 8.7839 | 0.0139
GEN-2020-088 | 03 CENTRAL | 547500 | RNM393 5 | 161 | 14.5226 | 14.5565 | 0.0339
GEN-2020-088 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.4809 | 23.5252 | 0.0443
GEN-2020-088 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.0481 | 23.0916 | 0.0435
GEN-2020-088 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.4249 | 24.4738 | 0.0489
GEN-2020-088 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.7072 | 9.7134 | 0.0062
GEN-2020-088 | 03 CENTRAL | 547532 | CAR108 2 | 69 | 8.5123 | 8.5166 | 0.0043
GEN-2020-088 | 03 CENTRAL | 547533 | ATL109 2 | 69 | 21.187 | 21.2225 | 0.0355
GEN-2020-088 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 18.2816 | 18.3049 | 0.0233
GEN-2020-088 | 03 CENTRAL | 547537 | AUR124 2 | 69 | 12.601 | 12.6214 | 0.0204
GEN-2020-088 | 03 CENTRAL | 547540 | MON152 2 | 69 | 10.9907 | 11.0131 | 0.0224
GEN-2020-088 | 03 CENTRAL | 547543 | NEO184 2 | 69 | 12.081 | 12.0898 | 0.0088
GEN-2020-088 | 03 CENTRAL | 547544 | WEN205 2 | 69 | 4.5485 | 4.5514 | 0.0029
GEN-2020-088 | 03 CENTRAL | 547546 | BIL221 2 | 69 | 10.1103 | 10.1159 | 0.0056
GEN-2020-088 | 03 CENTRAL | 547553 | ALB262 2 | 69 | 8.7646 | 8.7705 | 0.0059
GEN-2020-088 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 16.1899 | 16.209 | 0.0191
GEN-2020-088 | 03 CENTRAL | 547559 | TIP292 2 | 69 | 10.0997 | 10.1069 | 0.0072
GEN-2020-088 | 03 CENTRAL | 547560 | ROC296 2 | 69 | 9.039 | 9.0441 | 0.0051
GEN-2020-088 | 03 CENTRAL | 547563 | LIN314 2 | 69 | 10.2677 | 10.274 | 0.0063
GEN-2020-088 | 03 CENTRAL | 547566 | AND322 2 | 69 | 5.7966 | 5.7979 | 0.0013
GEN-2020-088 | 03 CENTRAL | 547578 | AUR355 2 | 69 | 9.576 | 9.5871 | 0.0111
GEN-2020-088 | 03 CENTRAL | 547581 | JOP360 2 | 69 | 14.3703 | 14.3851 | 0.0148
GEN-2020-088 | 03 CENTRAL | 547582 | SAR362T2 | 69 | 4.417 | 4.4194 | 0.0024
GEN-2020-088 | 03 CENTRAL | 547585 | DAD368 2 | 69 | 9.8909 | 9.8929 | 0.002
GEN-2020-088 | 03 CENTRAL | 547588 | JOP372 2 | 69 | 15.5424 | 15.5584 | 0.016
GEN-2020-088 | 03 CENTRAL | 547591 | MON383 2 | 69 | 12.6761 | 12.707 | 0.0309
GEN-2020-088 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 15.5971 | 15.6115 | 0.0144
GEN-2020-088 | 03 CENTRAL | 547593 | JOP391 5 | 161 | 13.6372 | 13.666 | 0.0288
GEN-2020-088 | 03 CENTRAL | 547595 | RNM393 2 | 69 | 19.7109 | 19.7394 | 0.0285
GEN-2020-088 | 03 CENTRAL | 547604 | BHJ415 2 | 69 | 11.2335 | 11.2358 | 0.0023
GEN-2020-088 | 03 CENTRAL | 547606 | MTV420 2 | 69 | 7.1302 | 7.135 | 0.0048
GEN-2020-088 | 03 CENTRAL | 547607 | JOP422 5 | 161 | 13.4603 | 13.4873 | 0.027
GEN-2020-088 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 16.1086 | 16.1243 | 0.0157
GEN-2020-088 | 03 CENTRAL | 547610 | NOL435 2 | 69 | 8.552 | 8.5537 | 0.0017
GEN-2020-088 | 03 CENTRAL | 547611 | MAR437 2 | 69 | 6.0244 | 6.0277 | 0.0033
GEN-2020-088 | 03 CENTRAL | 547618 | CPK446 2 | 69 | 10.5103 | 10.5182 | 0.0079
GEN-2020-088 | 03 CENTRAL | 547626 | HOL478_5 | 161 | 10.4528 | 10.4576 | 0.0048
GEN-2020-088 | 03 CENTRAL | 547685 | PLB447 2 | 69 | 14.6438 | 14.6583 | 0.0145
GEN-2020-088 | 03 CENTRAL | 549903 | JRPS 69B-2 2 | 69 | 19.5817 | 19.5881 | 0.0064
GEN-2020-088 | 03 CENTRAL | 549904 | JAMES RIVER2 | 69 | 16.1316 | 16.1356 | 0.004
GEN-2020-088 | 03 CENTRAL | 549905 | PLAINVIEW 2 | 69 | 14.3753 | 14.3789 | 0.0036
GEN-2020-088 | 03 CENTRAL | 549910 | COX 2 | 69 | 14.2063 | 14.21 | 0.0037
GEN-2020-088 | 03 CENTRAL | 549911 | GOLDEN 2 | 69 | 20.6876 | 20.6959 | 0.0083
GEN-2020-088 | 03 CENTRAL | 549913 | DAYTON 2 | 69 | 19.5791 | 19.5863 | 0.0072
GEN-2020-088 | 03 CENTRAL | 549914 | FORT 2 | 69 | 17.7859 | 17.7916 | 0.0057
GEN-2020-088 | 03 CENTRAL | 549916 | BLACKMAN 2 | 69 | 18.3735 | 18.3788 | 0.0053
GEN-2020-088 | 03 CENTRAL | 549917 | INGRAM 2 | 69 | 17.1034 | 17.1079 | 0.0045
GEN-2020-088 | 03 CENTRAL | 549918 | MILL 2 | 69 | 22.58 | 22.5879 | 0.0079
GEN-2020-088 | 03 CENTRAL | 549919 | CHAD 2 | 69 | 16.0157 | 16.02 | 0.0043
GEN-2020-088 | 03 CENTRAL | 549920 | HARGISS 2 | 69 | 18.2083 | 18.2139 | 0.0056
GEN-2020-088 | 03 CENTRAL | 549921 | MAIN STREET2 | 69 | 26.0731 | 26.0851 | 0.012
GEN-2020-088 | 03 CENTRAL | 549922 | GRAND 2 | 69 | 19.1695 | 19.1758 | 0.0063
GEN-2020-088 | 03 CENTRAL | 549924 | LAUREL 2 | 69 | 18.4414 | 18.4485 | 0.0071
GEN-2020-088 | 03 CENTRAL | 549925 | NICHOLS 2 | 69 | 24.6129 | 24.6267 | 0.0138
GEN-2020-088 | 03 CENTRAL | 549929 | WASHINGTON 2 | 69 | 19.6035 | 19.6103 | 0.0068
GEN-2020-088 | 03 CENTRAL | 549932 | PACKER 2 | 69 | 14.8542 | 14.8577 | 0.0035
GEN-2020-088 | 03 CENTRAL | 549954 | JTEC 5 | 161 | 27.0656 | 27.0932 | 0.0276
GEN-2020-088 | 03 CENTRAL | 549955 | JUNCTION 5 | 161 | 21.0748 | 21.0927 | 0.0179
GEN-2020-088 | 03 CENTRAL | 549956 | NICHOLS 5 | 161 | 19.2344 | 19.2501 | 0.0157
GEN-2020-088 | 03 CENTRAL | 549957 | WEST BELT 5 | 161 | 18.9571 | 18.9725 | 0.0154
GEN-2020-088 | 03 CENTRAL | 549958 | MAIN STREET5 | 161 | 19.1814 | 19.1973 | 0.0159
GEN-2020-088 | 03 CENTRAL | 549959 | BATTLEFIELD5 | 161 | 26.8418 | 26.8753 | 0.0335
GEN-2020-088 | 03 CENTRAL | 549960 | SW DISP PLT5 | 161 | 25.7798 | 25.8056 | 0.0258
GEN-2020-088 | 03 CENTRAL | 549961 | JAMES RIVER5 | 161 | 15.8875 | 15.8954 | 0.0079
GEN-2020-088 | 03 CENTRAL | 549962 | MILL 5 | 161 | 16.0627 | 16.0712 | 0.0085
GEN-2020-088 | 03 CENTRAL | 549963 | MENTOR 5 | 161 | 15.0699 | 15.0775 | 0.0076
GEN-2020-088 | 03 CENTRAL | 549966 | SUMMIT 5 | 161 | 13.4226 | 13.4288 | 0.0062
GEN-2020-088 | 03 CENTRAL | 549968 | MC CARTNEY 5 | 161 | 15.2398 | 15.2464 | 0.0066
GEN-2020-088 | 03 CENTRAL | 549969 | BROOKLINE 5 | 161 | 28.5442 | 28.5765 | 0.0323
GEN-2020-088 | 03 CENTRAL | 549970 | CLAY 5 | 161 | 18.8397 | 18.8522 | 0.0125
GEN-2020-088 | 03 CENTRAL | 549971 | PIC WEST 5 | 161 | 17.3382 | 17.35 | 0.0118
GEN-2020-088 | 03 CENTRAL | 549979 | BATTLEFIELD2 | 69 | 20.9712 | 20.9796 | 0.0084
GEN-2020-088 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.9268 | 11.9339 | 0.0071
GEN-2020-088 | 03 CENTRAL | 588980 | GEN-2017-060 | 161 | 6.1767 | 6.2462 | 0.0695
GEN-2020-088 | 03 CENTRAL | 589200 | GEN-2017-082 | 161 | 7.6734 | 7.6839 | 0.0105
GEN-2020-088 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.9629 | 11.9669 | 0.004
GEN-2020-088 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.9629 | 11.9669 | 0.004
GEN-2020-088 | 03 CENTRAL | 760242 | GEN-2017-188 | 161 | 2.0296 | 2.03 | 0.0004
GEN-2020-088 | 03 CENTRAL | 763560 | GEN-2019-016 | 161 | 18.3213 | 18.3336 | 0.0123
GEN-2020-088 | 03 CENTRAL | 763692 | GEN-2019-035 | 161 | 7.8653 | 7.8775 | 0.0122
GEN-2020-088 | 03 CENTRAL | 763696 | G19-035-TAP | 161 | 7.8828 | 7.8951 | 0.0123
GEN-2020-088 | 03 CENTRAL | 764315 | GEN-2020-088 | 161 | 14.7379 | 15.2206 | 0.4827
GEN-2020-090 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.5868 | 10.5898 | 0.003
GEN-2020-090 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.8511 | 13.8663 | 0.0152
GEN-2020-090 | 03 CENTRAL | 300069 | 5CHOTEAU1 | 161 | 42.5123 | 42.5188 | 0.0065
GEN-2020-090 | 03 CENTRAL | 300070 | 5CLARK | 161 | 8.1878 | 8.1903 | 0.0025
GEN-2020-090 | 03 CENTRAL | 300651 | 2LAMR | 69 | 10.1553 | 10.1573 | 0.002
GEN-2020-090 | 03 CENTRAL | 300652 | 2LAMRCTS | 69 | 3.9492 | 3.9495 | 0.0003
GEN-2020-090 | 03 CENTRAL | 300685 | 2LAMARPT | 69 | 8.5718 | 8.5732 | 0.0014
GEN-2020-090 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 16.1375 | 16.2782 | 0.1407
GEN-2020-090 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 24.5608 | 24.5713 | 0.0105
GEN-2020-090 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 40.884 | 40.8915 | 0.0075
GEN-2020-090 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.9541 | 8.9605 | 0.0064
GEN-2020-090 | 03 CENTRAL | 300949 | 7JASPER | 345 | 13.1365 | 13.1981 | 0.0616
GEN-2020-090 | 03 CENTRAL | 300950 | 5JASPER | 161 | 13.1395 | 13.1619 | 0.0224
GEN-2020-090 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 42.5123 | 42.5188 | 0.0065
GEN-2020-090 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 19.7167 | 19.7253 | 0.0086
GEN-2020-090 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.7052 | 15.7075 | 0.0023
GEN-2020-090 | 03 CENTRAL | 509807 | ONETA--7 | 345 | 29.0066 | 29.0084 | 0.0018
GEN-2020-090 | 03 CENTRAL | 509836 | OEC 7 | 345 | 28.7464 | 28.7481 | 0.0017
GEN-2020-090 | 03 CENTRAL | 509852 | T.NO.--7 | 345 | 23.5862 | 23.5895 | 0.0033
GEN-2020-090 | 03 CENTRAL | 510379 | DELWARE4 | 138 | 11.476 | 11.478 | 0.002
GEN-2020-090 | 03 CENTRAL | 510380 | DELWARE7 | 345 | 12.051 | 12.0572 | 0.0062
GEN-2020-090 | 03 CENTRAL | 510406 | N.E.S.-7 | 345 | 19.1676 | 19.1718 | 0.0042
GEN-2020-090 | 03 CENTRAL | 512648 | MAID 5 | 161 | 44.7099 | 44.7169 | 0.007
GEN-2020-090 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.9039 | 26.9139 | 0.01
GEN-2020-090 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 44.2374 | 44.2445 | 0.0071
GEN-2020-090 | 03 CENTRAL | 512700 | WAGNOR 5 | 161 | 9.9622 | 9.9624 | 0.0002
GEN-2020-090 | 03 CENTRAL | 512727 | GRDA1 2 | 69 | 12.5499 | 12.5501 | 0.0002
GEN-2020-090 | 03 CENTRAL | 512728 | ARKLIN2 | 69 | 3.8368 | 3.8368 | 0
GEN-2020-090 | 03 CENTRAL | 512742 | WMAIN ST5 | 161 | 28.1533 | 28.1561 | 0.0028
GEN-2020-090 | 03 CENTRAL | 512745 | SSLINC2 | 69 | 2.8861 | 2.8861 | 0
GEN-2020-090 | 03 CENTRAL | 512746 | SSNORT2 | 69 | 2.9422 | 2.9422 | 0
GEN-2020-090 | 03 CENTRAL | 512747 | SSNEWN2 | 69 | 3.1913 | 3.1913 | 0
GEN-2020-090 | 03 CENTRAL | 512750 | TONECE7 | 345 | 15.477 | 15.4793 | 0.0023
GEN-2020-090 | 03 CENTRAL | 512751 | TONECE5 | 161 | 15.5409 | 15.5417 | 0.0008
GEN-2020-090 | 03 CENTRAL | 512753 | TONNEC2 | 69 | 4.9587 | 4.9587 | 0
GEN-2020-090 | 03 CENTRAL | 512756 | TONECESTR2 | 69 | 3.9506 | 3.9507 | 0.0001
GEN-2020-090 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 25.7215 | 25.7303 | 0.0088
GEN-2020-090 | 03 CENTRAL | 513570 | CHOUTEAUCRK5 | 161 | 20.6761 | 20.6776 | 0.0015
GEN-2020-090 | 03 CENTRAL | 513590 | CUSTDAY1 5 | 161 | 16.8176 | 16.8192 | 0.0016
GEN-2020-090 | 03 CENTRAL | 513591 | HERRON 5 | 161 | 17.2337 | 17.2354 | 0.0017
GEN-2020-090 | 03 CENTRAL | 513593 | IGLOOV1 5 | 161 | 17.4301 | 17.4318 | 0.0017
GEN-2020-090 | 03 CENTRAL | 513595 | IGLOOV2 5 | 161 | 17.4301 | 17.4318 | 0.0017
GEN-2020-090 | 03 CENTRAL | 513596 | IGLOOV 7 | 345 | 20.4425 | 20.4477 | 0.0052
GEN-2020-090 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 12 | 12.0021 | 0.0021
GEN-2020-090 | 03 CENTRAL | 515576 | RANCHRD7 | 345 | 12.9183 | 12.92 | 0.0017
GEN-2020-090 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 12.0299 | 12.032 | 0.0021
GEN-2020-090 | 03 CENTRAL | 515688 | FRNTWND7 | 345 | 10.3431 | 10.3442 | 0.0011
GEN-2020-090 | 03 CENTRAL | 516066 | FRNT2WD7 | 345 | 10.1334 | 10.1345 | 0.0011
GEN-2020-090 | 03 CENTRAL | 529200 | OMCDLEC7 | 345 | 12.8999 | 12.9016 | 0.0017
GEN-2020-090 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.5838 | 16.5846 | 0.0008
GEN-2020-090 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.4596 | 11.4605 | 0.0009
GEN-2020-090 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.7385 | 16.7394 | 0.0009
GEN-2020-090 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.8888 | 13.8894 | 0.0006
GEN-2020-090 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 11.9171 | 11.9338 | 0.0167
GEN-2020-090 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 11.0239 | 11.0381 | 0.0142
GEN-2020-090 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.7599 | 9.7665 | 0.0066
GEN-2020-090 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 9.4892 | 9.4954 | 0.0062
GEN-2020-090 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.74 | 20.7452 | 0.0052
GEN-2020-090 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.4746 | 7.4751 | 0.0005
GEN-2020-090 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 6.2006 | 6.2009 | 0.0003
GEN-2020-090 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 5.1526 | 5.1528 | 0.0002
GEN-2020-090 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.9331 | 18.9486 | 0.0155
GEN-2020-090 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 7.0715 | 7.0718 | 0.0003
GEN-2020-090 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 18.1815 | 18.2288 | 0.0473
GEN-2020-090 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 18.5096 | 18.527 | 0.0174
GEN-2020-090 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.6969 | 5.6971 | 0.0002
GEN-2020-090 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.6724 | 23.6806 | 0.0082
GEN-2020-090 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.0881 | 18.2036 | 0.1155
GEN-2020-090 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.1487 | 14.1504 | 0.0017
GEN-2020-090 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.1483 | 16.2276 | 0.0793
GEN-2020-090 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 10.3732 | 10.3802 | 0.007
GEN-2020-090 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 9.2142 | 9.2196 | 0.0054
GEN-2020-090 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5164 | 13.5715 | 0.0551
GEN-2020-090 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.4142 | 10.415 | 0.0008
GEN-2020-090 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 5.1383 | 5.1385 | 0.0002
GEN-2020-090 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.2118 | 8.2126 | 0.0008
GEN-2020-090 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.2085 | 8.2093 | 0.0008
GEN-2020-090 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 23.7712 | 23.7942 | 0.023
GEN-2020-090 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 28.274 | 28.2854 | 0.0114
GEN-2020-090 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 11.2436 | 11.2453 | 0.0017
GEN-2020-090 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 19.2449 | 19.2501 | 0.0052
GEN-2020-090 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 11.2938 | 11.2955 | 0.0017
GEN-2020-090 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 22.4871 | 22.4942 | 0.0071
GEN-2020-090 | 03 CENTRAL | 532993 | TALLGRS4 | 138 | 10.7087 | 10.7102 | 0.0015
GEN-2020-090 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 4.139 | 4.1393 | 0.0003
GEN-2020-090 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 13.1271 | 13.1323 | 0.0052
GEN-2020-090 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 7.2568 | 7.2579 | 0.0011
GEN-2020-090 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 25.3625 | 25.3852 | 0.0227
GEN-2020-090 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 25.4056 | 25.4284 | 0.0228
GEN-2020-090 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 25.287 | 25.3096 | 0.0226
GEN-2020-090 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.8834 | 19.889 | 0.0056
GEN-2020-090 | 03 CENTRAL | 533026 | ANDOVER4 | 138 | 18.1993 | 18.2038 | 0.0045
GEN-2020-090 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.6906 | 17.6936 | 0.003
GEN-2020-090 | 03 CENTRAL | 533030 | BOEINGE4 | 138 | 17.2277 | 17.2313 | 0.0036
GEN-2020-090 | 03 CENTRAL | 533032 | BU11PON4 | 138 | 15.4307 | 15.4338 | 0.0031
GEN-2020-090 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 21.7628 | 21.7679 | 0.0051
GEN-2020-090 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.959 | 18.9641 | 0.0051
GEN-2020-090 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 25.2741 | 25.2817 | 0.0076
GEN-2020-090 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 32.3825 | 32.3893 | 0.0068
GEN-2020-090 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 32.306 | 32.3128 | 0.0068
GEN-2020-090 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 20.5738 | 20.5787 | 0.0049
GEN-2020-090 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 21.2358 | 21.2394 | 0.0036
GEN-2020-090 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 25.2324 | 25.24 | 0.0076
GEN-2020-090 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 20.8264 | 20.8324 | 0.006
GEN-2020-090 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 31.219 | 31.2348 | 0.0158
GEN-2020-090 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 19.7609 | 19.7633 | 0.0024
GEN-2020-090 | 03 CENTRAL | 533067 | SPRNGDL4 | 138 | 14.8076 | 14.8105 | 0.0029
GEN-2020-090 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.8478 | 19.8528 | 0.005
GEN-2020-090 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.6888 | 24.6915 | 0.0027
GEN-2020-090 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.9952 | 22.9962 | 0.001
GEN-2020-090 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 14.6136 | 14.615 | 0.0014
GEN-2020-090 | 03 CENTRAL | 533604 | WEAVER 2 | 69 | 12.3352 | 12.3361 | 0.0009
GEN-2020-090 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.5466 | 3.5471 | 0.0005
GEN-2020-090 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.1619 | 3.1623 | 0.0004
GEN-2020-090 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 5.1538 | 5.1549 | 0.0011
GEN-2020-090 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.5452 | 3.5457 | 0.0005
GEN-2020-090 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.817 | 4.8182 | 0.0012
GEN-2020-090 | 03 CENTRAL | 533630 | CC3WEST2 | 69 | 4.7611 | 4.762 | 0.0009
GEN-2020-090 | 03 CENTRAL | 533636 | GREEN 2 | 69 | 4.2299 | 4.2304 | 0.0005
GEN-2020-090 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.9738 | 8.9742 | 0.0004
GEN-2020-090 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 6.2267 | 6.2285 | 0.0018
GEN-2020-090 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.3311 | 6.3318 | 0.0007
GEN-2020-090 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.7696 | 8.7709 | 0.0013
GEN-2020-090 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.6363 | 7.637 | 0.0007
GEN-2020-090 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 24.019 | 24.0283 | 0.0093
GEN-2020-090 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 24.0441 | 24.0535 | 0.0094
GEN-2020-090 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.6372 | 16.6383 | 0.0011
GEN-2020-090 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.7455 | 20.748 | 0.0025
GEN-2020-090 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.6772 | 2.6772 | 0
GEN-2020-090 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 20.941 | 20.9429 | 0.0019
GEN-2020-090 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6136 | 27.6185 | 0.0049
GEN-2020-090 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 30.1256 | 30.1269 | 0.0013
GEN-2020-090 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.832 | 25.8373 | 0.0053
GEN-2020-090 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.9716 | 40.9756 | 0.004
GEN-2020-090 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 27.8728 | 27.8947 | 0.0219
GEN-2020-090 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.8529 | 10.8531 | 0.0002
GEN-2020-090 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 29.1551 | 29.1564 | 0.0013
GEN-2020-090 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 27.1333 | 27.154 | 0.0207
GEN-2020-090 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 27.1333 | 27.154 | 0.0207
GEN-2020-090 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.8162 | 2.8163 | 0.0001
GEN-2020-090 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.6735 | 0.6735 | 0
GEN-2020-090 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.6451 | 0.6451 | 0
GEN-2020-090 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.9517 | 24.955 | 0.0033
GEN-2020-090 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 23.5224 | 23.5252 | 0.0028
GEN-2020-090 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 23.0889 | 23.0916 | 0.0027
GEN-2020-090 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 24.4707 | 24.4738 | 0.0031
GEN-2020-090 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.9282 | 11.9339 | 0.0057
GEN-2020-090 | 03 CENTRAL | 560053 | G15-052T | 345 | 12.4324 | 12.4369 | 0.0045
GEN-2020-090 | 03 CENTRAL | 578530 | FR3HV | 345 | 5.2327 | 5.2329 | 0.0002
GEN-2020-090 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.6005 | 6.6008 | 0.0003
GEN-2020-090 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.154 | 8.1545 | 0.0005
GEN-2020-090 | 03 CENTRAL | 584900 | GEN-2015-052 | 345 | 12.3842 | 12.3887 | 0.0045
GEN-2020-090 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.7592 | 6.7594 | 0.0002
GEN-2020-090 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 10.1084 | 10.1089 | 0.0005
GEN-2020-090 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 7.4333 | 7.4336 | 0.0003
GEN-2020-090 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 7.7917 | 7.7921 | 0.0004
GEN-2020-090 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.6372 | 16.6383 | 0.0011
GEN-2020-090 | 03 CENTRAL | 588990 | GEN-2017-061 | 161 | 17.5115 | 17.5125 | 0.001
GEN-2020-090 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 29.456 | 29.4616 | 0.0056
GEN-2020-090 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 6.5211 | 6.5213 | 0.0002
GEN-2020-090 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.9432 | 11.9669 | 0.0237
GEN-2020-090 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.9432 | 11.9669 | 0.0237
GEN-2020-090 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.6324 | 20.6376 | 0.0052
GEN-2020-090 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 32.2111 | 32.2178 | 0.0067
GEN-2020-090 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5417 | 27.5465 | 0.0048
GEN-2020-090 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4651 | 27.4699 | 0.0048
GEN-2020-090 | 03 CENTRAL | 762680 | GEN-2018-032 | 345 | 11.9908 | 12.0113 | 0.0205
GEN-2020-090 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 7.1557 | 7.1559 | 0.0002
GEN-2020-090 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 17.674 | 17.6759 | 0.0019
GEN-2020-090 | 03 CENTRAL | 762999 | GEN-2018-064 | 69 | 3.6736 | 3.6736 | 0
GEN-2020-090 | 03 CENTRAL | 763065 | GEN-2018-071 | 345 | 12.5103 | 12.5119 | 0.0016
GEN-2020-090 | 03 CENTRAL | 763069 | G18-071-TAP | 345 | 12.5552 | 12.5568 | 0.0016
GEN-2020-090 | 03 CENTRAL | 763109 | GEN-2018-079 | 138 | 6.6034 | 6.604 | 0.0006
GEN-2020-090 | 03 CENTRAL | 763113 | G18-079-TAP | 138 | 9.3923 | 9.3935 | 0.0012
GEN-2020-090 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 10.97 | 10.9707 | 0.0007
GEN-2020-090 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.0536 | 12.0544 | 0.0008
GEN-2020-090 | 03 CENTRAL | 763472 | GEN-2019-002 | 161 | 41.5279 | 41.5339 | 0.006
GEN-2020-090 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 15.4381 | 15.4402 | 0.0021
GEN-2020-090 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 18.6477 | 18.6507 | 0.003
GEN-2020-090 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 20.9009 | 20.9028 | 0.0019
GEN-2020-090 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 20.901 | 20.9029 | 0.0019
GEN-2020-090 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 8.7041 | 9.0335 | 0.3294
GEN-2020-090 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.0308 | 10.3587 | 0.3279
GEN-2020-090 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 24.6066 | 24.6242 | 0.0176
GEN-2020-090 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 27.0937 | 27.1153 | 0.0216
GEN-2020-010 | 04 SOUTHEAST | 514777 | CLEOCOR2 | 69 | 8.4592 | 8.4786 | 0.0194
GEN-2020-010 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.4751 | 6.4893 | 0.0142
GEN-2020-010 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 11.8784 | 11.9535 | 0.0751
GEN-2020-010 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 19.5178 | 19.6614 | 0.1436
GEN-2020-010 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 7.6111 | 8.1223 | 0.5112
GEN-2020-010 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.2492 | 5.2722 | 0.023
GEN-2020-010 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.0777 | 9.0909 | 0.0132
GEN-2020-010 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.1727 | 10.1887 | 0.016
GEN-2020-010 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.6046 | 7.7777 | 0.1731
GEN-2020-010 | 04 SOUTHEAST | 514822 | SOUTHRD4 | 138 | 4.758 | 4.86 | 0.102
GEN-2020-010 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 6.1815 | 6.2396 | 0.0581
GEN-2020-010 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4518 | 3.4628 | 0.011
GEN-2020-010 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 20.5382 | 20.603 | 0.0648
GEN-2020-010 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.0169 | 26.2082 | 0.1913
GEN-2020-010 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 3.7419 | 3.8775 | 0.1356
GEN-2020-010 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.5277 | 19.6714 | 0.1437
GEN-2020-010 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 6.8595 | 7.08 | 0.2205
GEN-2020-010 | 04 SOUTHEAST | 515562 | CLEOPLT4 | 138 | 6.4724 | 6.4866 | 0.0142
GEN-2020-010 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 20.6404 | 20.9111 | 0.2707
GEN-2020-010 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 6.4117 | 6.4554 | 0.0437
GEN-2020-010 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.5885 | 14.6152 | 0.0267
GEN-2020-010 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.8444 | 15.8742 | 0.0298
GEN-2020-010 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 6.8449 | 7.0647 | 0.2198
GEN-2020-010 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 4.9113 | 5.0583 | 0.147
GEN-2020-010 | 04 SOUTHEAST | 516025 | SUNDANC4 | 138 | 4.5677 | 4.5766 | 0.0089
GEN-2020-010 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.2601 | 8.3198 | 0.0597
GEN-2020-010 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.238 | 10.2541 | 0.0161
GEN-2020-010 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.9238 | 11.9438 | 0.02
GEN-2020-010 | 04 SOUTHEAST | 520454 | STALOGA2 | 69 | 4.566 | 4.6901 | 0.1241
GEN-2020-010 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 20.3171 | 20.5819 | 0.2648
GEN-2020-010 | 04 SOUTHEAST | 520480 | CURTIS 2 | 69 | 3.9844 | 4.0075 | 0.0231
GEN-2020-010 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 14.8856 | 15.0399 | 0.1543
GEN-2020-010 | 04 SOUTHEAST | 520507 | CEDRDAL4 | 138 | 4.7375 | 4.7627 | 0.0252
GEN-2020-010 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 6.8105 | 7.4358 | 0.6253
GEN-2020-010 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8682 | 6.8782 | 0.01
GEN-2020-010 | 04 SOUTHEAST | 520843 | CANTON-2 | 69 | 4.8702 | 4.9772 | 0.107
GEN-2020-010 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 5.8953 | 5.9287 | 0.0334
GEN-2020-010 | 04 SOUTHEAST | 520909 | FAIRVEW2 | 69 | 4.6712 | 4.6895 | 0.0183
GEN-2020-010 | 04 SOUTHEAST | 520919 | FTSUPLY2 | 69 | 6.6134 | 6.6552 | 0.0418
GEN-2020-010 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 4.4121 | 4.444 | 0.0319
GEN-2020-010 | 04 SOUTHEAST | 520922 | SLEEPBR4 | 138 | 3.1505 | 3.1735 | 0.023
GEN-2020-010 | 04 SOUTHEAST | 520942 | HM-BTTP2 | 69 | 2.3921 | 2.4292 | 0.0371
GEN-2020-010 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 7.2971 | 7.355 | 0.0579
GEN-2020-010 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 8.791 | 8.8509 | 0.0599
GEN-2020-010 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 21.0761 | 21.3585 | 0.2824
GEN-2020-010 | 04 SOUTHEAST | 521015 | OKEENE 2 | 69 | 6.5978 | 6.6438 | 0.046
GEN-2020-010 | 04 SOUTHEAST | 521016 | OKEENE 4 | 138 | 7.2951 | 7.3231 | 0.028
GEN-2020-010 | 04 SOUTHEAST | 521033 | PUTNAM 2 | 69 | 2.7203 | 2.7702 | 0.0499
GEN-2020-010 | 04 SOUTHEAST | 521064 | TALOGA 2 | 69 | 8.3907 | 8.7246 | 0.3339
GEN-2020-010 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 7.3928 | 8.056 | 0.6632
GEN-2020-010 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 3.8934 | 3.9638 | 0.0704
GEN-2020-010 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.2056 | 10.2841 | 0.0785
GEN-2020-010 | 04 SOUTHEAST | 521128 | NINMLTP4 | 138 | 4.9356 | 4.9526 | 0.017
GEN-2020-010 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 7.5162 | 7.5685 | 0.0523
GEN-2020-010 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.3663 | 8.4231 | 0.0568
GEN-2020-010 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.4002 | 15.4135 | 0.0133
GEN-2020-010 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 7.7091 | 7.7643 | 0.0552
GEN-2020-010 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.8444 | 15.8742 | 0.0298
GEN-2020-010 | 04 SOUTHEAST | 765205 | GEN-2020-010 | 138 | 6.9808 | 7.7639 | 0.7831
GEN-2020-010 | 04 SOUTHEAST | 765212 | G20-010-SS1 | 138 | 6.9649 | 7.7482 | 0.7833
GEN-2020-010 | 04 SOUTHEAST | 765213 | G20-010-SS2 | 138 | 6.7799 | 7.5451 | 0.7652
GEN-2020-010 | 04 SOUTHEAST | 765215 | G20-010-TAP | 138 | 6.9991 | 7.782 | 0.7829
GEN-2020-012 | 04 SOUTHEAST | 511429 | L AIRGS4 | 138 | 12.4449 | 12.556 | 0.1111
GEN-2020-012 | 04 SOUTHEAST | 511432 | R-AMOCO2 | 69 | 3.9062 | 3.9405 | 0.0343
GEN-2020-012 | 04 SOUTHEAST | 511435 | SNYDER-4 | 138 | 7.2898 | 7.744 | 0.4542
GEN-2020-012 | 04 SOUTHEAST | 511438 | DUKE---2 | 69 | 4.2833 | 4.3539 | 0.0706
GEN-2020-012 | 04 SOUTHEAST | 511440 | ALTUSJT4 | 138 | 5.2709 | 5.5122 | 0.2413
GEN-2020-012 | 04 SOUTHEAST | 511441 | ALTUSJT2 | 69 | 5.8064 | 5.9602 | 0.1538
GEN-2020-012 | 04 SOUTHEAST | 511444 | ROSVTAP2 | 69 | 4.1304 | 4.1681 | 0.0377
GEN-2020-012 | 04 SOUTHEAST | 511460 | FREDJC-2 | 69 | 2.9635 | 3.007 | 0.0435
GEN-2020-012 | 04 SOUTHEAST | 511462 | HEADRIK2 | 69 | 4.749 | 4.8541 | 0.1051
GEN-2020-012 | 04 SOUTHEAST | 511465 | HOBART-2 | 69 | 5.7641 | 5.8064 | 0.0423
GEN-2020-012 | 04 SOUTHEAST | 511472 | TIPTE T2 | 69 | 3.86 | 3.9278 | 0.0678
GEN-2020-012 | 04 SOUTHEAST | 511475 | SNYDER-2 | 69 | 7.7426 | 7.9825 | 0.2399
GEN-2020-012 | 04 SOUTHEAST | 511479 | TIPTCTY2 | 69 | 2.4988 | 2.532 | 0.0332
GEN-2020-012 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 13.7794 | 13.9045 | 0.1251
GEN-2020-012 | 04 SOUTHEAST | 511495 | TOMSTEED2 | 69 | 4.3721 | 4.4366 | 0.0645
GEN-2020-012 | 04 SOUTHEAST | 511500 | CACHE4 | 138 | 8.9464 | 9.0979 | 0.1515
GEN-2020-012 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 13.3308 | 13.4565 | 0.1257
GEN-2020-012 | 04 SOUTHEAST | 511520 | DAV TAP2 | 69 | 2.3517 | 2.3798 | 0.0281
GEN-2020-012 | 04 SOUTHEAST | 511543 | TIPTN T2 | 69 | 4.7471 | 4.8522 | 0.1051
GEN-2020-012 | 04 SOUTHEAST | 511545 | TIPTON 2 | 69 | 2.6625 | 2.6993 | 0.0368
GEN-2020-012 | 04 SOUTHEAST | 511564 | MARTHA 4 | 138 | 4.5554 | 4.674 | 0.1186
GEN-2020-012 | 04 SOUTHEAST | 512100 | CHLDR2WT | 69 | 2.372 | 2.3912 | 0.0192
GEN-2020-012 | 04 SOUTHEAST | 512101 | CHILD4WT | 138 | 1.7935 | 1.8115 | 0.018
GEN-2020-012 | 04 SOUTHEAST | 512103 | HOLTP4WT | 138 | 1.6177 | 1.6319 | 0.0142
GEN-2020-012 | 04 SOUTHEAST | 512110 | LAKEP4WT | 138 | 2.2936 | 2.3287 | 0.0351
GEN-2020-012 | 04 SOUTHEAST | 512111 | LAKEP2WT | 69 | 3.2747 | 3.3152 | 0.0405
GEN-2020-012 | 04 SOUTHEAST | 512113 | VRNMTAP2 | 69 | 2.5732 | 2.6038 | 0.0306
GEN-2020-012 | 04 SOUTHEAST | 520404 | MDCPRK4 | 138 | 5.3936 | 5.4545 | 0.0609
GEN-2020-012 | 04 SOUTHEAST | 520410 | CACHE4 | 138 | 4.8951 | 4.9934 | 0.0983
GEN-2020-012 | 04 SOUTHEAST | 520499 | WHTECTY2 | 69 | 1.9899 | 2.0107 | 0.0208
GEN-2020-012 | 04 SOUTHEAST | 520528 | ROSEVLT2 | 69 | 4.0226 | 4.0784 | 0.0558
GEN-2020-012 | 04 SOUTHEAST | 520534 | DUKE 2 | 69 | 5.5674 | 5.674 | 0.1066
GEN-2020-012 | 04 SOUTHEAST | 520541 | SNYDRSB2 | 69 | 7.3484 | 7.5403 | 0.1919
GEN-2020-012 | 04 SOUTHEAST | 520803 | ALTUS_ 2 | 69 | 3.8081 | 3.8675 | 0.0594
GEN-2020-012 | 04 SOUTHEAST | 520805 | ALTUSSW2 | 69 | 3.8049 | 3.8644 | 0.0595
GEN-2020-012 | 04 SOUTHEAST | 520896 | ELDORDO2 | 69 | 2.2211 | 2.245 | 0.0239
GEN-2020-012 | 04 SOUTHEAST | 520914 | FREDRIK2 | 69 | 3.6419 | 3.6875 | 0.0456
GEN-2020-012 | 04 SOUTHEAST | 520927 | GRANITE2 | 69 | 3.3884 | 3.4131 | 0.0247
GEN-2020-012 | 04 SOUTHEAST | 520929 | GYPSUM 2 | 69 | 3.8181 | 3.8773 | 0.0592
GEN-2020-012 | 04 SOUTHEAST | 520954 | INDHOMA4 | 138 | 4.2518 | 4.3266 | 0.0748
GEN-2020-012 | 04 SOUTHEAST | 520980 | LOCKETT2 | 69 | 2.0266 | 2.0471 | 0.0205
GEN-2020-012 | 04 SOUTHEAST | 521009 | NAVJOTP2 | 69 | 3.8514 | 3.9125 | 0.0611
GEN-2020-012 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 5.6585 | 5.7148 | 0.0563
GEN-2020-012 | 04 SOUTHEAST | 521042 | RUSSELL2 | 69 | 5.5674 | 5.674 | 0.1066
GEN-2020-012 | 04 SOUTHEAST | 521043 | RUSSELL4 | 138 | 4.0671 | 4.194 | 0.1269
GEN-2020-012 | 04 SOUTHEAST | 521051 | SNYDER 2 | 69 | 7.3484 | 7.5403 | 0.1919
GEN-2020-012 | 04 SOUTHEAST | 521052 | SNYDER 4 | 138 | 6.8467 | 7.1903 | 0.3436
GEN-2020-012 | 04 SOUTHEAST | 521069 | TIPTON-2 | 69 | 2.1911 | 2.2142 | 0.0231
GEN-2020-012 | 04 SOUTHEAST | 521070 | TIPTONJ2 | 69 | 4.168 | 4.2314 | 0.0634
GEN-2020-012 | 04 SOUTHEAST | 521081 | VERNON 2 | 69 | 2.5748 | 2.6055 | 0.0307
GEN-2020-012 | 04 SOUTHEAST | 521190 | CACHEJ4 | 138 | 5.2975 | 5.412 | 0.1145
GEN-2020-012 | 04 SOUTHEAST | 529298 | OMPVET-4 | 138 | 4.8409 | 5.0157 | 0.1748
GEN-2020-012 | 04 SOUTHEAST | 529302 | OMALTUS4 | 138 | 4.7241 | 4.88 | 0.1559
GEN-2020-012 | 04 SOUTHEAST | 529342 | OMMANGM2 | 69 | 3.3252 | 3.3537 | 0.0285
GEN-2020-012 | 04 SOUTHEAST | 529345 | OMPARK-4 | 138 | 5.0557 | 5.2638 | 0.2081
GEN-2020-012 | 04 SOUTHEAST | 562683 | GEN-2015-013 | 138 | 6.8306 | 7.1726 | 0.342
GEN-2020-012 | 04 SOUTHEAST | 588779 | G17-036_TAP | 138 | 7.2495 | 7.6868 | 0.4373
GEN-2020-012 | 04 SOUTHEAST | 588780 | GEN-2017-036 | 138 | 7.009 | 7.4183 | 0.4093
GEN-2020-012 | 04 SOUTHEAST | 765220 | GEN-2020-012 | 138 | 5.8373 | 6.3765 | 0.5392
GEN-2020-012 | 04 SOUTHEAST | 765230 | G20-012-TAP | 138 | 5.8806 | 6.4196 | 0.539
GEN-2020-012 | 04 SOUTHEAST | 765231 | G20-012-SS1 | 138 | 5.8373 | 6.3765 | 0.5392
GEN-2020-012 | 04 SOUTHEAST | 765232 | G20-012-SS2 | 138 | 5.5632 | 6.0766 | 0.5134
GEN-2020-020 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 5.0973 | 5.0973 | 0
GEN-2020-020 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.2908 | 10.2966 | 0.0058
GEN-2020-020 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 3.085 | 3.0903 | 0.0053
GEN-2020-020 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.8145 | 12.82 | 0.0055
GEN-2020-020 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.9525 | 8.9861 | 0.0336
GEN-2020-020 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 3.0208 | 3.0293 | 0.0085
GEN-2020-020 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 15.3807 | 15.4247 | 0.044
GEN-2020-020 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.1774 | 6.2006 | 0.0232
GEN-2020-020 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.4609 | 10.5086 | 0.0477
GEN-2020-020 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.5802 | 5.5975 | 0.0173
GEN-2020-020 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.6938 | 10.7388 | 0.045
GEN-2020-020 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.8999 | 3.914 | 0.0141
GEN-2020-020 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.6818 | 7.7053 | 0.0235
GEN-2020-020 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.4679 | 10.5069 | 0.039
GEN-2020-020 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.7742 | 14.8336 | 0.0594
GEN-2020-020 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.8743 | 13.9413 | 0.067
GEN-2020-020 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.9212 | 3.9308 | 0.0096
GEN-2020-020 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.4518 | 25.568 | 0.1162
GEN-2020-020 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.4261 | 9.4878 | 0.0617
GEN-2020-020 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 19.7919 | 19.86 | 0.0681
GEN-2020-020 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.7977 | 3.8106 | 0.0129
GEN-2020-020 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.972 | 30.9985 | 0.0265
GEN-2020-020 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0411 | 16.0584 | 0.0173
GEN-2020-020 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.5928 | 20.731 | 0.1382
GEN-2020-020 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 12.4194 | 12.4675 | 0.0481
GEN-2020-020 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 20.3749 | 20.4712 | 0.0963
GEN-2020-020 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.5508 | 21.6969 | 0.1461
GEN-2020-020 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.5035 | 7.5225 | 0.019
GEN-2020-020 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.7153 | 6.7385 | 0.0232
GEN-2020-020 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 11.4629 | 11.5053 | 0.0424
GEN-2020-020 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.4752 | 25.6741 | 0.1989
GEN-2020-020 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.524 | 26.738 | 0.214
GEN-2020-020 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.0641 | 14.2267 | 0.1626
GEN-2020-020 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.6495 | 14.729 | 0.0795
GEN-2020-020 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.2898 | 11.3409 | 0.0511
GEN-2020-020 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.9814 | 18.0596 | 0.0782
GEN-2020-020 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6843 | 12.7458 | 0.0615
GEN-2020-020 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 17.2527 | 17.3267 | 0.074
GEN-2020-020 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 17.2251 | 17.2995 | 0.0744
GEN-2020-020 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.6946 | 7.7169 | 0.0223
GEN-2020-020 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.1822 | 18.2975 | 0.1153
GEN-2020-020 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.7789 | 9.8168 | 0.0379
GEN-2020-020 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.764 | 17.7976 | 0.0336
GEN-2020-020 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.8126 | 14.0135 | 0.2009
GEN-2020-020 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.9575 | 10.9738 | 0.0163
GEN-2020-020 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.6215 | 7.634 | 0.0125
GEN-2020-020 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.6046 | 21.7302 | 0.1256
GEN-2020-020 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.5472 | 42.6022 | 0.055
GEN-2020-020 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.6532 | 17.6816 | 0.0284
GEN-2020-020 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6396 | 8.6533 | 0.0137
GEN-2020-020 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.5179 | 16.5425 | 0.0246
GEN-2020-020 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.5575 | 24.5789 | 0.0214
GEN-2020-020 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 15.9945 | 16.0133 | 0.0188
GEN-2020-020 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.8349 | 29.9045 | 0.0696
GEN-2020-020 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.4957 | 19.5591 | 0.0634
GEN-2020-020 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.6943 | 13.7122 | 0.0179
GEN-2020-020 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.8054 | 13.8281 | 0.0227
GEN-2020-020 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.7269 | 30.7878 | 0.0609
GEN-2020-020 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.608 | 15.6461 | 0.0381
GEN-2020-020 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4404 | 12.4639 | 0.0235
GEN-2020-020 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.5331 | 6.575 | 0.0419
GEN-2020-020 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 10.1201 | 10.2632 | 0.1431
GEN-2020-020 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.6816 | 2.7035 | 0.0219
GEN-2020-020 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 4.1635 | 4.1995 | 0.036
GEN-2020-020 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.9018 | 6.9674 | 0.0656
GEN-2020-020 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.7186 | 3.75 | 0.0314
GEN-2020-020 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 5.2612 | 5.308 | 0.0468
GEN-2020-020 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.2329 | 7.2947 | 0.0618
GEN-2020-020 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.5998 | 7.6509 | 0.0511
GEN-2020-020 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 9.1741 | 9.2296 | 0.0555
GEN-2020-020 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.4897 | 5.5368 | 0.0471
GEN-2020-020 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.9085 | 2.9274 | 0.0189
GEN-2020-020 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.7637 | 3.7991 | 0.0354
GEN-2020-020 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.5435 | 15.6553 | 0.1118
GEN-2020-020 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.9399 | 8.0179 | 0.078
GEN-2020-020 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.1698 | 14.7908 | 0.621
GEN-2020-020 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 4.0906 | 4.125 | 0.0344
GEN-2020-020 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.6758 | 15.9566 | 0.2808
GEN-2020-020 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 4.1948 | 4.2297 | 0.0349
GEN-2020-020 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.2562 | 15.3648 | 0.1086
GEN-2020-020 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.3295 | 14.364 | 0.0345
GEN-2020-020 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.2977 | 10.3181 | 0.0204
GEN-2020-020 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.862 | 16.9193 | 0.0573
GEN-2020-020 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.3795 | 11.4317 | 0.0522
GEN-2020-020 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2109 | 34.2233 | 0.0124
GEN-2020-020 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 44.2765 | 44.2917 | 0.0152
GEN-2020-020 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.4111 | 28.4217 | 0.0106
GEN-2020-020 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.4528 | 27.4624 | 0.0096
GEN-2020-020 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 44.0185 | 44.0491 | 0.0306
GEN-2020-020 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.7972 | 26.8205 | 0.0233
GEN-2020-020 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 50.1606 | 50.2265 | 0.0659
GEN-2020-020 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.4762 | 30.5244 | 0.0482
GEN-2020-020 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.9964 | 22.0168 | 0.0204
GEN-2020-020 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 11.0287 | 11.043 | 0.0143
GEN-2020-020 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.363 | 12.4028 | 0.0398
GEN-2020-020 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.0934 | 12.127 | 0.0336
GEN-2020-020 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 21.0063 | 21.0802 | 0.0739
GEN-2020-020 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.9703 | 13.0334 | 0.0631
GEN-2020-020 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.9104 | 9.9407 | 0.0303
GEN-2020-020 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.9316 | 27.9483 | 0.0167
GEN-2020-020 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.844 | 11.8831 | 0.0391
GEN-2020-020 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.5449 | 14.5674 | 0.0225
GEN-2020-020 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 48.8055 | 48.8694 | 0.0639
GEN-2020-020 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.8816 | 7.9125 | 0.0309
GEN-2020-020 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 17.0248 | 17.0416 | 0.0168
GEN-2020-020 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.7082 | 27.7283 | 0.0201
GEN-2020-020 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 11.0381 | 11.142 | 0.1039
GEN-2020-020 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 6.2986 | 6.34 | 0.0414
GEN-2020-020 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 22.9792 | 23.336 | 0.3568
GEN-2020-020 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 11.1762 | 11.2826 | 0.1064
GEN-2020-020 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.2326 | 23.5803 | 0.3477
GEN-2020-020 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 7.2101 | 7.2624 | 0.0523
GEN-2020-020 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 9.0352 | 9.1132 | 0.078
GEN-2020-020 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.9665 | 7.0165 | 0.05
GEN-2020-020 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8336 | 12.1638 | 0.3302
GEN-2020-020 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.9409 | 8.0108 | 0.0699
GEN-2020-020 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 19.295 | 19.5552 | 0.2602
GEN-2020-020 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 19.0612 | 19.0843 | 0.0231
GEN-2020-020 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0612 | 19.0843 | 0.0231
GEN-2020-020 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.9309 | 8.0006 | 0.0697
GEN-2020-020 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.2501 | 5.2514 | 0.0013
GEN-2020-020 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1782 | 4.1909 | 0.0127
GEN-2020-020 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.3456 | 11.3869 | 0.0413
GEN-2020-020 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.3456 | 11.3869 | 0.0413
GEN-2020-020 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 15.6595 | 15.6777 | 0.0182
GEN-2020-020 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1004 | 10.1569 | 0.0565
GEN-2020-020 | 04 SOUTHEAST | 764075 | GEN-2020-054 | 345 | 12.4125 | 12.5791 | 0.1666
GEN-2020-020 | 04 SOUTHEAST | 764115 | G20-074-TAP | 345 | 12.2116 | 12.2561 | 0.0445
GEN-2020-020 | 04 SOUTHEAST | 764510 | GEN-2020-020 | 345 | 14.0268 | 14.6505 | 0.6237
GEN-2020-020 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 14.0545 | 14.6781 | 0.6236
GEN-2020-054 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 5.0973 | 5.0973 | 0
GEN-2020-054 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 5925 | ERCOTMAINBUS | 345 | 5.0973 | 5.0973 | 0
GEN-2020-054 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.7337 | 20.751 | 0.0173
GEN-2020-054 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.2861 | 10.2966 | 0.0105
GEN-2020-054 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.8507 | 14.8551 | 0.0044
GEN-2020-054 | 04 SOUTHEAST | 337672 | 4MURFBORO | 138 | 3.0844 | 3.0903 | 0.0059
GEN-2020-054 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.8098 | 12.82 | 0.0102
GEN-2020-054 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.7665 | 15.7763 | 0.0098
GEN-2020-054 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 8.9433 | 8.9861 | 0.0428
GEN-2020-054 | 04 SOUTHEAST | 504030 | SFORE_1 2 | 69 | 3.0192 | 3.0293 | 0.0101
GEN-2020-054 | 04 SOUTHEAST | 504122 | MCNAB 3 | 115 | 15.3639 | 15.4247 | 0.0608
GEN-2020-054 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.1737 | 6.2006 | 0.0269
GEN-2020-054 | 04 SOUTHEAST | 504124 | ASHDWN_W 4 | 138 | 10.4546 | 10.5086 | 0.054
GEN-2020-054 | 04 SOUTHEAST | 504363 | NE-TEXARK2 | 69 | 5.5748 | 5.5975 | 0.0227
GEN-2020-054 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.6836 | 10.7388 | 0.0552
GEN-2020-054 | 04 SOUTHEAST | 507421 | FOREMAN2 | 69 | 3.9 | 3.914 | 0.014
GEN-2020-054 | 04 SOUTHEAST | 507427 | OKAY 2 | 69 | 7.6773 | 7.7053 | 0.028
GEN-2020-054 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.4571 | 10.5069 | 0.0498
GEN-2020-054 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.762 | 14.8336 | 0.0716
GEN-2020-054 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.8593 | 13.9413 | 0.082
GEN-2020-054 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.9198 | 3.9308 | 0.011
GEN-2020-054 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.3986 | 25.568 | 0.1694
GEN-2020-054 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.3947 | 9.4878 | 0.0931
GEN-2020-054 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 19.7641 | 19.86 | 0.0959
GEN-2020-054 | 04 SOUTHEAST | 507463 | BARITERDTP 4 | 138 | 3.7964 | 3.8106 | 0.0142
GEN-2020-054 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 17.6512 | 17.6757 | 0.0245
GEN-2020-054 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 19.1635 | 19.1857 | 0.0222
GEN-2020-054 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 22.7782 | 22.8052 | 0.027
GEN-2020-054 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.1948 | 11.2093 | 0.0145
GEN-2020-054 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.9465 | 30.9985 | 0.052
GEN-2020-054 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0225 | 16.0584 | 0.0359
GEN-2020-054 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 16.8919 | 16.9133 | 0.0214
GEN-2020-054 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 22.2256 | 22.2562 | 0.0306
GEN-2020-054 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.5257 | 20.731 | 0.2053
GEN-2020-054 | 04 SOUTHEAST | 508051 | ASHDOWN2 | 69 | 12.409 | 12.4675 | 0.0585
GEN-2020-054 | 04 SOUTHEAST | 508053 | BANN 2 | 69 | 20.3357 | 20.4712 | 0.1355
GEN-2020-054 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.4792 | 21.6969 | 0.2177
GEN-2020-054 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.3892 | 7.4164 | 0.0272
GEN-2020-054 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.4953 | 7.5225 | 0.0272
GEN-2020-054 | 04 SOUTHEAST | 508065 | NEKOOSA2 | 69 | 6.7111 | 6.7385 | 0.0274
GEN-2020-054 | 04 SOUTHEAST | 508069 | NNBOSTN4 | 138 | 11.4479 | 11.5053 | 0.0574
GEN-2020-054 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.3741 | 25.6741 | 0.3
GEN-2020-054 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 26.4142 | 26.738 | 0.3238
GEN-2020-054 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 13.9683 | 14.2267 | 0.2584
GEN-2020-054 | 04 SOUTHEAST | 508075 | REDSPRG4 | 138 | 14.6132 | 14.729 | 0.1158
GEN-2020-054 | 04 SOUTHEAST | 508078 | SETEXAR4 | 138 | 11.2689 | 11.3409 | 0.072
GEN-2020-054 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.9524 | 18.0596 | 0.1072
GEN-2020-054 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.6587 | 12.7458 | 0.0871
GEN-2020-054 | 04 SOUTHEAST | 508081 | SUGHLET2 | 69 | 17.2258 | 17.3267 | 0.1009
GEN-2020-054 | 04 SOUTHEAST | 508082 | SUGHLWT2 | 69 | 17.1974 | 17.2995 | 0.1021
GEN-2020-054 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.34 | 8.3701 | 0.0301
GEN-2020-054 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.6842 | 7.7169 | 0.0327
GEN-2020-054 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.1276 | 18.2975 | 0.1699
GEN-2020-054 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.7643 | 9.8168 | 0.0525
GEN-2020-054 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.6657 | 7.6991 | 0.0334
GEN-2020-054 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 10.1189 | 10.1473 | 0.0284
GEN-2020-054 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.7354 | 17.7976 | 0.0622
GEN-2020-054 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.3629 | 14.0135 | 0.6506
GEN-2020-054 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.1317 | 9.1579 | 0.0262
GEN-2020-054 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.6302 | 7.6514 | 0.0212
GEN-2020-054 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.7513 | 13.7849 | 0.0336
GEN-2020-054 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.9442 | 10.9738 | 0.0296
GEN-2020-054 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.6131 | 7.634 | 0.0209
GEN-2020-054 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.4102 | 21.7302 | 0.32
GEN-2020-054 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.8417 | 6.8591 | 0.0174
GEN-2020-054 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.2919 | 7.3112 | 0.0193
GEN-2020-054 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 16.9944 | 17.0306 | 0.0362
GEN-2020-054 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.7701 | 9.794 | 0.0239
GEN-2020-054 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.4896 | 42.6022 | 0.1126
GEN-2020-054 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.6208 | 17.6816 | 0.0608
GEN-2020-054 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.5274 | 12.5617 | 0.0343
GEN-2020-054 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 34.6126 | 34.6976 | 0.085
GEN-2020-054 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.1313 | 12.1515 | 0.0202
GEN-2020-054 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6281 | 8.6533 | 0.0252
GEN-2020-054 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.4907 | 16.5425 | 0.0518
GEN-2020-054 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.3768 | 8.3925 | 0.0157
GEN-2020-054 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.0357 | 19.0767 | 0.041
GEN-2020-054 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 16.4609 | 16.4836 | 0.0227
GEN-2020-054 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 24.5382 | 24.5789 | 0.0407
GEN-2020-054 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 15.9743 | 16.0133 | 0.039
GEN-2020-054 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 19.2495 | 19.2788 | 0.0293
GEN-2020-054 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 10.4054 | 10.436 | 0.0306
GEN-2020-054 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.7562 | 29.9045 | 0.1483
GEN-2020-054 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.409 | 19.5591 | 0.1501
GEN-2020-054 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.3802 | 12.4079 | 0.0277
GEN-2020-054 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.6804 | 13.7122 | 0.0318
GEN-2020-054 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.7849 | 13.8281 | 0.0432
GEN-2020-054 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 30.6723 | 30.7878 | 0.1155
GEN-2020-054 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.5624 | 15.6461 | 0.0837
GEN-2020-054 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.0602 | 25.1074 | 0.0472
GEN-2020-054 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.3796 | 7.3983 | 0.0187
GEN-2020-054 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 11.9312 | 11.974 | 0.0428
GEN-2020-054 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.5365 | 7.5523 | 0.0158
GEN-2020-054 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.0169 | 6.0357 | 0.0188
GEN-2020-054 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4189 | 12.4639 | 0.045
GEN-2020-054 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.2283 | 5.2461 | 0.0178
GEN-2020-054 | 04 SOUTHEAST | 510864 | B.BOW 4 | 138 | 6.5481 | 6.575 | 0.0269
GEN-2020-054 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 10.1966 | 10.2632 | 0.0666
GEN-2020-054 | 04 SOUTHEAST | 510868 | GA PAC 2 | 69 | 2.6913 | 2.7035 | 0.0122
GEN-2020-054 | 04 SOUTHEAST | 510869 | W CITY 2 | 69 | 4.1798 | 4.1995 | 0.0197
GEN-2020-054 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.9328 | 6.9674 | 0.0346
GEN-2020-054 | 04 SOUTHEAST | 510875 | KI PMPN2 | 69 | 3.7327 | 3.75 | 0.0173
GEN-2020-054 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 5.2828 | 5.308 | 0.0252
GEN-2020-054 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.2598 | 7.2947 | 0.0349
GEN-2020-054 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.6185 | 7.6509 | 0.0324
GEN-2020-054 | 04 SOUTHEAST | 510890 | CRAIGJT4 | 138 | 9.1918 | 9.2296 | 0.0378
GEN-2020-054 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.5113 | 5.5368 | 0.0255
GEN-2020-054 | 04 SOUTHEAST | 510894 | VALYTIM2 | 69 | 2.9168 | 2.9274 | 0.0106
GEN-2020-054 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.7805 | 3.7991 | 0.0186
GEN-2020-054 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.6079 | 15.6553 | 0.0474
GEN-2020-054 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.9772 | 8.0179 | 0.0407
GEN-2020-054 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.5604 | 14.7908 | 0.2304
GEN-2020-054 | 04 SOUTHEAST | 510917 | FTOWSON2 | 69 | 4.1061 | 4.125 | 0.0189
GEN-2020-054 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.8336 | 15.9566 | 0.123
GEN-2020-054 | 04 SOUTHEAST | 510920 | SAWYER 2 | 69 | 4.2105 | 4.2297 | 0.0192
GEN-2020-054 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.3186 | 15.3648 | 0.0462
GEN-2020-054 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.346 | 14.364 | 0.018
GEN-2020-054 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.3067 | 10.3181 | 0.0114
GEN-2020-054 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.8901 | 16.9193 | 0.0292
GEN-2020-054 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4073 | 11.4317 | 0.0244
GEN-2020-054 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.2166 | 34.2233 | 0.0067
GEN-2020-054 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 44.2832 | 44.2917 | 0.0085
GEN-2020-054 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.416 | 28.4217 | 0.0057
GEN-2020-054 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.4572 | 27.4624 | 0.0052
GEN-2020-054 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 44.0327 | 44.0491 | 0.0164
GEN-2020-054 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.8087 | 26.8205 | 0.0118
GEN-2020-054 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 50.1931 | 50.2265 | 0.0334
GEN-2020-054 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.5015 | 30.5244 | 0.0229
GEN-2020-054 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 22.0056 | 22.0168 | 0.0112
GEN-2020-054 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 11.0351 | 11.043 | 0.0079
GEN-2020-054 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.3819 | 12.4028 | 0.0209
GEN-2020-054 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.1092 | 12.127 | 0.0178
GEN-2020-054 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 21.0435 | 21.0802 | 0.0367
GEN-2020-054 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 13.0045 | 13.0334 | 0.0289
GEN-2020-054 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.9245 | 9.9407 | 0.0162
GEN-2020-054 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 27.9398 | 27.9483 | 0.0085
GEN-2020-054 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8647 | 11.8831 | 0.0184
GEN-2020-054 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.5551 | 14.5674 | 0.0123
GEN-2020-054 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 48.8369 | 48.8694 | 0.0325
GEN-2020-054 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.8973 | 7.9125 | 0.0152
GEN-2020-054 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 17.0331 | 17.0416 | 0.0085
GEN-2020-054 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.718 | 27.7283 | 0.0103
GEN-2020-054 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 11.0916 | 11.142 | 0.0504
GEN-2020-054 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 6.3153 | 6.34 | 0.0247
GEN-2020-054 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 23.1818 | 23.336 | 0.1542
GEN-2020-054 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 11.2312 | 11.2826 | 0.0514
GEN-2020-054 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.4291 | 23.5803 | 0.1512
GEN-2020-054 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 7.2356 | 7.2624 | 0.0268
GEN-2020-054 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 9.0723 | 9.1132 | 0.0409
GEN-2020-054 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.9908 | 7.0165 | 0.0257
GEN-2020-054 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.0356 | 12.1638 | 0.1282
GEN-2020-054 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.9797 | 8.0108 | 0.0311
GEN-2020-054 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 19.439 | 19.5552 | 0.1162
GEN-2020-054 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 19.0729 | 19.0843 | 0.0114
GEN-2020-054 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0729 | 19.0843 | 0.0114
GEN-2020-054 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.9696 | 8.0006 | 0.031
GEN-2020-054 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 5.2506 | 5.2514 | 0.0008
GEN-2020-054 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1842 | 4.1909 | 0.0067
GEN-2020-054 | 04 SOUTHEAST | 762427 | GEN-2018-003 | 138 | 11.331 | 11.3869 | 0.0559
GEN-2020-054 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 11.331 | 11.3869 | 0.0559
GEN-2020-054 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 15.6399 | 15.6777 | 0.0378
GEN-2020-054 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1314 | 10.1569 | 0.0255
GEN-2020-054 | 04 SOUTHEAST | 764075 | GEN-2020-054 | 345 | 11.9263 | 12.5791 | 0.6528
GEN-2020-054 | 04 SOUTHEAST | 764115 | G20-074-TAP | 345 | 12.235 | 12.2561 | 0.0211
GEN-2020-054 | 04 SOUTHEAST | 764510 | GEN-2020-020 | 345 | 14.4238 | 14.6505 | 0.2267
GEN-2020-054 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 14.4506 | 14.6781 | 0.2275
GEN-2020-074 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 14.0041 | 14.0135 | 0.0094
GEN-2020-074 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.6159 | 15.6553 | 0.0394
GEN-2020-074 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.764 | 14.7908 | 0.0268
GEN-2020-074 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.9399 | 15.9566 | 0.0167
GEN-2020-074 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.3267 | 15.3648 | 0.0381
GEN-2020-074 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.3556 | 14.364 | 0.0084
GEN-2020-074 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 17.3776 | 17.4113 | 0.0337
GEN-2020-074 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.1247 | 9.1292 | 0.0045
GEN-2020-074 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 19.5615 | 19.5845 | 0.023
GEN-2020-074 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.5827 | 12.5946 | 0.0119
GEN-2020-074 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.9497 | 5.958 | 0.0083
GEN-2020-074 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 17.1558 | 17.1667 | 0.0109
GEN-2020-074 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 27.5796 | 27.6343 | 0.0547
GEN-2020-074 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 16.4211 | 16.5014 | 0.0803
GEN-2020-074 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 13.4504 | 13.4645 | 0.0141
GEN-2020-074 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.533 | 10.5394 | 0.0064
GEN-2020-074 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 23.8068 | 23.8467 | 0.0399
GEN-2020-074 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 12.146 | 12.3046 | 0.1586
GEN-2020-074 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.6519 | 7.7109 | 0.059
GEN-2020-074 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.8393 | 16.9193 | 0.08
GEN-2020-074 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.3247 | 11.4317 | 0.107
GEN-2020-074 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.4151 | 28.4217 | 0.0066
GEN-2020-074 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.8033 | 26.8205 | 0.0172
GEN-2020-074 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 50.1833 | 50.2265 | 0.0432
GEN-2020-074 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.496 | 30.5244 | 0.0284
GEN-2020-074 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.3591 | 12.4028 | 0.0437
GEN-2020-074 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.9182 | 11.9554 | 0.0372
GEN-2020-074 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.0883 | 12.127 | 0.0387
GEN-2020-074 | 04 SOUTHEAST | 515128 | RATLIFF2 | 69 | 5.4545 | 5.4647 | 0.0102
GEN-2020-074 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 6.9342 | 6.9531 | 0.0189
GEN-2020-074 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 8.7401 | 8.7712 | 0.0311
GEN-2020-074 | 04 SOUTHEAST | 515131 | FOX 4 | 138 | 7.2589 | 7.2834 | 0.0245
GEN-2020-074 | 04 SOUTHEAST | 515134 | PRARPNT4 | 138 | 5.776 | 5.7874 | 0.0114
GEN-2020-074 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.8703 | 21.0802 | 0.2099
GEN-2020-074 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.7623 | 13.0334 | 0.2711
GEN-2020-074 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.8769 | 13.9586 | 0.0817
GEN-2020-074 | 04 SOUTHEAST | 515138 | CARTER 4 | 138 | 13.704 | 13.7702 | 0.0662
GEN-2020-074 | 04 SOUTHEAST | 515143 | WOLFCRK4 | 138 | 10.5515 | 10.6098 | 0.0583
GEN-2020-074 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.7722 | 14.8816 | 0.1094
GEN-2020-074 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 9.0625 | 9.0881 | 0.0256
GEN-2020-074 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 9.0601 | 9.0856 | 0.0255
GEN-2020-074 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.9119 | 9.9407 | 0.0288
GEN-2020-074 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.935 | 7.9526 | 0.0176
GEN-2020-074 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 8.0572 | 8.0803 | 0.0231
GEN-2020-074 | 04 SOUTHEAST | 515162 | FNDTION4 | 138 | 12.9137 | 12.9717 | 0.058
GEN-2020-074 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 8.595 | 8.6166 | 0.0216
GEN-2020-074 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.9113 | 12.9762 | 0.0649
GEN-2020-074 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.8517 | 12.91 | 0.0583
GEN-2020-074 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 13.6764 | 13.7543 | 0.0779
GEN-2020-074 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 13.3004 | 13.3903 | 0.0899
GEN-2020-074 | 04 SOUTHEAST | 515420 | SCMMRCT2 | 69 | 9.8756 | 9.9009 | 0.0253
GEN-2020-074 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8712 | 11.8831 | 0.0119
GEN-2020-074 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 8.9261 | 8.9581 | 0.032
GEN-2020-074 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 4.5896 | 4.6009 | 0.0113
GEN-2020-074 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.8872 | 11.9376 | 0.0504
GEN-2020-074 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.7734 | 10.8149 | 0.0415
GEN-2020-074 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.8591 | 7.9125 | 0.0534
GEN-2020-074 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 23.3013 | 23.336 | 0.0347
GEN-2020-074 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.5461 | 23.5803 | 0.0342
GEN-2020-074 | 04 SOUTHEAST | 520988 | MARIETA4 | 138 | 7.9609 | 7.9827 | 0.0218
GEN-2020-074 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.2831 | 12.3262 | 0.0431
GEN-2020-074 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.8147 | 9.8431 | 0.0284
GEN-2020-074 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 11.9729 | 12.011 | 0.0381
GEN-2020-074 | 04 SOUTHEAST | 521125 | CHEEK_4 | 138 | 9.2913 | 9.3401 | 0.0488
GEN-2020-074 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.1354 | 12.1638 | 0.0284
GEN-2020-074 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.9536 | 8.0108 | 0.0572
GEN-2020-074 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 8.8815 | 8.9132 | 0.0317
GEN-2020-074 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0772 | 19.0843 | 0.0071
GEN-2020-074 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.9435 | 8.0006 | 0.0571
GEN-2020-074 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1747 | 4.1909 | 0.0162
GEN-2020-074 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 13.3407 | 13.4518 | 0.1111
GEN-2020-074 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 13.2624 | 13.3722 | 0.1098
GEN-2020-074 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 7.1309 | 7.1822 | 0.0513
GEN-2020-074 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.1386 | 10.1569 | 0.0183
GEN-2020-074 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 16.0988 | 16.1761 | 0.0773
GEN-2020-074 | 04 SOUTHEAST | 764105 | GEN-2020-074 | 345 | 11.8641 | 12.2505 | 0.3864
GEN-2020-074 | 04 SOUTHEAST | 764115 | G20-074-TAP | 345 | 11.8697 | 12.2561 | 0.3864
GEN-2020-074 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 14.6517 | 14.6781 | 0.0264
GEN-2020-074 | 04 SOUTHEAST | 764540 | GEN-2020-075 | 345 | 16.0009 | 16.0529 | 0.052
GEN-2020-074 | 04 SOUTHEAST | 764550 | G20-075-TAP | 345 | 16.0127 | 16.0648 | 0.0521
GEN-2020-074 | 04 SOUTHEAST | 764555 | GEN-2020-087 | 345 | 16.0017 | 16.0537 | 0.052
GEN-2020-074 | 04 SOUTHEAST | 766290 | GEN-2020-009 | 345 | 9.4974 | 9.5216 | 0.0242
GEN-2020-074 | 04 SOUTHEAST | 766291 | G20-009-TAP | 345 | 9.4974 | 9.5216 | 0.0242
GEN-2020-081 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.6551 | 21.7302 | 0.0751
GEN-2020-081 | 04 SOUTHEAST | 46714 | J1671 POI | 230 | 8.1548 | 8.1741 | 0.0193
GEN-2020-081 | 04 SOUTHEAST | 334020 | 4BRYAN% | 138 | 5.1966 | 5.2064 | 0.0098
GEN-2020-081 | 04 SOUTHEAST | 334021 | 4COLSTTA% | 138 | 6.6121 | 6.6261 | 0.014
GEN-2020-081 | 04 SOUTHEAST | 334022 | 4SPEEDWY | 138 | 6.2954 | 6.3085 | 0.0131
GEN-2020-081 | 04 SOUTHEAST | 334024 | 4SOTA 1 | 138 | 6.7754 | 6.7901 | 0.0147
GEN-2020-081 | 04 SOUTHEAST | 334025 | 4MAG AND | 138 | 7.2067 | 7.2239 | 0.0172
GEN-2020-081 | 04 SOUTHEAST | 334026 | 4GRIMES% | 138 | 16.4565 | 16.5195 | 0.063
GEN-2020-081 | 04 SOUTHEAST | 334027 | 6GRIMES! | 230 | 7.4232 | 7.4461 | 0.0229
GEN-2020-081 | 04 SOUTHEAST | 334028 | 7GRIMES% | 345 | 8.6484 | 8.6944 | 0.046
GEN-2020-081 | 04 SOUTHEAST | 334029 | 7FRONTR | 345 | 8.439 | 8.4818 | 0.0428
GEN-2020-081 | 04 SOUTHEAST | 334039 | 4BENTWATER! | 138 | 7.2457 | 7.2578 | 0.0121
GEN-2020-081 | 04 SOUTHEAST | 334040 | 4WALDEN | 138 | 7.7035 | 7.7155 | 0.012
GEN-2020-081 | 04 SOUTHEAST | 334058 | 4L558T485 | 138 | 9.3495 | 9.3626 | 0.0131
GEN-2020-081 | 04 SOUTHEAST | 334060 | 4MT.ZION | 138 | 8.4741 | 8.4881 | 0.014
GEN-2020-081 | 04 SOUTHEAST | 334087 | 4PONDEROSA% | 138 | 19.5356 | 19.5632 | 0.0276
GEN-2020-081 | 04 SOUTHEAST | 334088 | 6PONDEROSA! | 230 | 7.4951 | 7.5072 | 0.0121
GEN-2020-081 | 04 SOUTHEAST | 334197 | 7ROCKYCRK% | 345 | 7.101 | 7.1312 | 0.0302
GEN-2020-081 | 04 SOUTHEAST | 334198 | 6ROCKYCRK | 230 | 8.2075 | 8.2292 | 0.0217
GEN-2020-081 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.8116 | 12.82 | 0.0084
GEN-2020-081 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 30.9528 | 30.9985 | 0.0457
GEN-2020-081 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.0303 | 16.0584 | 0.0281
GEN-2020-081 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.2073 | 14.2267 | 0.0194
GEN-2020-081 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 17.7549 | 17.7976 | 0.0427
GEN-2020-081 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.9907 | 14.0135 | 0.0228
GEN-2020-081 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 10.9423 | 10.9738 | 0.0315
GEN-2020-081 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.6551 | 21.7302 | 0.0751
GEN-2020-081 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 16.9547 | 17.0306 | 0.0759
GEN-2020-081 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 42.2042 | 42.6022 | 0.398
GEN-2020-081 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.3768 | 17.6816 | 0.3048
GEN-2020-081 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 34.4182 | 34.6976 | 0.2794
GEN-2020-081 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 13.4897 | 13.5401 | 0.0504
GEN-2020-081 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6281 | 8.6533 | 0.0252
GEN-2020-081 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.2138 | 16.5425 | 0.3287
GEN-2020-081 | 04 SOUTHEAST | 508575 | WHITNEY4 | 138 | 22.0621 | 22.1517 | 0.0896
GEN-2020-081 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 18.1455 | 18.2058 | 0.0603
GEN-2020-081 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 22.718 | 22.8664 | 0.1484
GEN-2020-081 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 7.9555 | 8.3925 | 0.437
GEN-2020-081 | 04 SOUTHEAST | 508586 | TENGEN 7 | 345 | 7.8828 | 8.3125 | 0.4297
GEN-2020-081 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 18.9927 | 19.0767 | 0.084
GEN-2020-081 | 04 SOUTHEAST | 508596 | BRANDYBR | 138 | 25.2866 | 25.3854 | 0.0988
GEN-2020-081 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 15.9871 | 16.0133 | 0.0262
GEN-2020-081 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.7737 | 29.9045 | 0.1308
GEN-2020-081 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.436 | 19.5591 | 0.1231
GEN-2020-081 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 13.6805 | 13.7122 | 0.0317
GEN-2020-081 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 13.7819 | 13.8281 | 0.0462
GEN-2020-081 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.6135 | 15.6461 | 0.0326
GEN-2020-081 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.0094 | 25.1074 | 0.098
GEN-2020-081 | 04 SOUTHEAST | 509240 | CROCKET4 | 138 | 7.1339 | 7.2087 | 0.0748
GEN-2020-081 | 04 SOUTHEAST | 509241 | CROCKET7 | 345 | 5.8912 | 5.9921 | 0.1009
GEN-2020-081 | 04 SOUTHEAST | 509320 | ALTO 4 | 138 | 3.109 | 3.1267 | 0.0177
GEN-2020-081 | 04 SOUTHEAST | 509322 | GRAPLND4 | 138 | 4.7349 | 4.7736 | 0.0387
GEN-2020-081 | 04 SOUTHEAST | 509326 | SLOCUM 4 | 138 | 3.8838 | 3.9116 | 0.0278
GEN-2020-081 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.4242 | 12.4639 | 0.0397
GEN-2020-081 | 04 SOUTHEAST | 764120 | GEN-2020-081 | 345 | 7.9289 | 8.366 | 0.4371
GEN-2020-085 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.9714 | 14.0135 | 0.0421
GEN-2020-085 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.5123 | 15.6553 | 0.143
GEN-2020-085 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.6883 | 14.7908 | 0.1025
GEN-2020-085 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.8784 | 15.9566 | 0.0782
GEN-2020-085 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.2258 | 15.3648 | 0.139
GEN-2020-085 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.3165 | 14.364 | 0.0475
GEN-2020-085 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 17.2855 | 17.4113 | 0.1258
GEN-2020-085 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.0967 | 9.1292 | 0.0325
GEN-2020-085 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 19.4658 | 19.5845 | 0.1187
GEN-2020-085 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.5259 | 12.5946 | 0.0687
GEN-2020-085 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.9192 | 5.958 | 0.0388
GEN-2020-085 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 17.0877 | 17.1667 | 0.079
GEN-2020-085 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 27.4069 | 27.6343 | 0.2274
GEN-2020-085 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 16.2343 | 16.5014 | 0.2671
GEN-2020-085 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 13.3865 | 13.4645 | 0.078
GEN-2020-085 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.4971 | 10.5394 | 0.0423
GEN-2020-085 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 23.6696 | 23.8467 | 0.1771
GEN-2020-085 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 11.8224 | 12.3046 | 0.4822
GEN-2020-085 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.51 | 7.7109 | 0.2009
GEN-2020-085 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.6223 | 16.9193 | 0.297
GEN-2020-085 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.0923 | 11.4317 | 0.3394
GEN-2020-085 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.3915 | 28.4217 | 0.0302
GEN-2020-085 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.7504 | 26.8205 | 0.0701
GEN-2020-085 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 50.0524 | 50.2265 | 0.1741
GEN-2020-085 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 30.4179 | 30.5244 | 0.1065
GEN-2020-085 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.2242 | 12.4028 | 0.1786
GEN-2020-085 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.8002 | 11.9554 | 0.1552
GEN-2020-085 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 11.9665 | 12.127 | 0.1605
GEN-2020-085 | 04 SOUTHEAST | 515128 | RATLIFF2 | 69 | 5.4057 | 5.4647 | 0.059
GEN-2020-085 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 6.8655 | 6.9531 | 0.0876
GEN-2020-085 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 8.6386 | 8.7712 | 0.1326
GEN-2020-085 | 04 SOUTHEAST | 515131 | FOX 4 | 138 | 7.1746 | 7.2834 | 0.1088
GEN-2020-085 | 04 SOUTHEAST | 515134 | PRARPNT4 | 138 | 5.73 | 5.7874 | 0.0574
GEN-2020-085 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.3955 | 21.0802 | 0.6847
GEN-2020-085 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.2546 | 13.0334 | 0.7788
GEN-2020-085 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.6556 | 13.9586 | 0.303
GEN-2020-085 | 04 SOUTHEAST | 515138 | CARTER 4 | 138 | 13.5163 | 13.7702 | 0.2539
GEN-2020-085 | 04 SOUTHEAST | 515143 | WOLFCRK4 | 138 | 10.383 | 10.6098 | 0.2268
GEN-2020-085 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.4934 | 14.8816 | 0.3882
GEN-2020-085 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 8.9741 | 9.0881 | 0.114
GEN-2020-085 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 8.9717 | 9.0856 | 0.1139
GEN-2020-085 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 9.8146 | 9.9407 | 0.1261
GEN-2020-085 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 7.8694 | 7.9526 | 0.0832
GEN-2020-085 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 7.9742 | 8.0803 | 0.1061
GEN-2020-085 | 04 SOUTHEAST | 515162 | FNDTION4 | 138 | 12.7451 | 12.9717 | 0.2266
GEN-2020-085 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 8.5053 | 8.6166 | 0.1113
GEN-2020-085 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.7264 | 12.9762 | 0.2498
GEN-2020-085 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.6826 | 12.91 | 0.2274
GEN-2020-085 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 13.4633 | 13.7543 | 0.291
GEN-2020-085 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 13.0624 | 13.3903 | 0.3279
GEN-2020-085 | 04 SOUTHEAST | 515420 | SCMMRCT2 | 69 | 9.7729 | 9.9009 | 0.128
GEN-2020-085 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8301 | 11.8831 | 0.053
GEN-2020-085 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 8.8222 | 8.9581 | 0.1359
GEN-2020-085 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 4.547 | 4.6009 | 0.0539
GEN-2020-085 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.7367 | 11.9376 | 0.2009
GEN-2020-085 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.6442 | 10.8149 | 0.1707
GEN-2020-085 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 7.7291 | 7.9125 | 0.1834
GEN-2020-085 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 23.1941 | 23.336 | 0.1419
GEN-2020-085 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.4404 | 23.5803 | 0.1399
GEN-2020-085 | 04 SOUTHEAST | 520988 | MARIETA4 | 138 | 7.8818 | 7.9827 | 0.1009
GEN-2020-085 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.1494 | 12.3262 | 0.1768
GEN-2020-085 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 9.7185 | 9.8431 | 0.1246
GEN-2020-085 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 11.8525 | 12.011 | 0.1585
GEN-2020-085 | 04 SOUTHEAST | 521125 | CHEEK_4 | 138 | 9.1453 | 9.3401 | 0.1948
GEN-2020-085 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 12.0563 | 12.1638 | 0.1075
GEN-2020-085 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.8141 | 8.0108 | 0.1967
GEN-2020-085 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 8.7783 | 8.9132 | 0.1349
GEN-2020-085 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.049 | 19.0843 | 0.0353
GEN-2020-085 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.8044 | 8.0006 | 0.1962
GEN-2020-085 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 4.1252 | 4.1909 | 0.0657
GEN-2020-085 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 13.0988 | 13.4518 | 0.353
GEN-2020-085 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 13.0228 | 13.3722 | 0.3494
GEN-2020-085 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 7.0042 | 7.1822 | 0.178
GEN-2020-085 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 10.0825 | 10.1569 | 0.0744
GEN-2020-085 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 15.9179 | 16.1761 | 0.2582
GEN-2020-085 | 04 SOUTHEAST | 764105 | GEN-2020-074 | 345 | 11.1858 | 12.2505 | 1.0647
GEN-2020-085 | 04 SOUTHEAST | 764115 | G20-074-TAP | 345 | 11.1915 | 12.2561 | 1.0646
GEN-2020-085 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 14.5771 | 14.6781 | 0.101
GEN-2020-085 | 04 SOUTHEAST | 764540 | GEN-2020-075 | 345 | 15.8705 | 16.0529 | 0.1824
GEN-2020-085 | 04 SOUTHEAST | 764550 | G20-075-TAP | 345 | 15.8821 | 16.0648 | 0.1827
GEN-2020-085 | 04 SOUTHEAST | 764555 | GEN-2020-087 | 345 | 15.8712 | 16.0537 | 0.1825
GEN-2020-085 | 04 SOUTHEAST | 766290 | GEN-2020-009 | 345 | 9.4266 | 9.5216 | 0.095
GEN-2020-085 | 04 SOUTHEAST | 766291 | G20-009-TAP | 345 | 9.4266 | 9.5216 | 0.095
GEN-2020-087 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.8528 | 17.4113 | 0.5585
GEN-2020-087 | 04 SOUTHEAST | 511422 | FLETCHR4 | 138 | 8.3192 | 8.3402 | 0.021
GEN-2020-087 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.1044 | 9.1292 | 0.0248
GEN-2020-087 | 04 SOUTHEAST | 511428 | LG-YEAR4 | 138 | 12.9397 | 13.0166 | 0.0769
GEN-2020-087 | 04 SOUTHEAST | 511431 | LWS S4 | 138 | 11.995 | 12.0644 | 0.0694
GEN-2020-087 | 04 SOUTHEAST | 511436 | COMANC-2 | 69 | 9.5666 | 9.5719 | 0.0053
GEN-2020-087 | 04 SOUTHEAST | 511437 | COMANC-4 | 138 | 19.4201 | 19.5845 | 0.1644
GEN-2020-087 | 04 SOUTHEAST | 511439 | LWSTAP 4 | 138 | 12.5192 | 12.5946 | 0.0754
GEN-2020-087 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.8613 | 4.8671 | 0.0058
GEN-2020-087 | 04 SOUTHEAST | 511453 | DUNCAN-4 | 138 | 6.6944 | 6.7053 | 0.0109
GEN-2020-087 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 5.9035 | 5.958 | 0.0545
GEN-2020-087 | 04 SOUTHEAST | 511461 | FT.SILL2 | 69 | 6.274 | 6.2828 | 0.0088
GEN-2020-087 | 04 SOUTHEAST | 511466 | L.E.S.-2 | 69 | 17.1052 | 17.1667 | 0.0615
GEN-2020-087 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 27.231 | 27.6343 | 0.4033
GEN-2020-087 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 15.8829 | 16.5014 | 0.6185
GEN-2020-087 | 04 SOUTHEAST | 511469 | LGORE-N2 | 69 | 8.4472 | 8.4626 | 0.0154
GEN-2020-087 | 04 SOUTHEAST | 511470 | LGORE-S2 | 69 | 7.3562 | 7.3681 | 0.0119
GEN-2020-087 | 04 SOUTHEAST | 511471 | LWS-NTP4 | 138 | 12.6369 | 12.7149 | 0.078
GEN-2020-087 | 04 SOUTHEAST | 511473 | PO.HILL2 | 69 | 6.1261 | 6.1346 | 0.0085
GEN-2020-087 | 04 SOUTHEAST | 511474 | SHERID4 | 138 | 13.3732 | 13.4645 | 0.0913
GEN-2020-087 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 32.845 | 32.9525 | 0.1075
GEN-2020-087 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.5026 | 10.5394 | 0.0368
GEN-2020-087 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.9569 | 8.9725 | 0.0156
GEN-2020-087 | 04 SOUTHEAST | 511488 | 112GORE4 | 138 | 13.8172 | 13.9045 | 0.0873
GEN-2020-087 | 04 SOUTHEAST | 511494 | COMMTAP4 | 138 | 23.5587 | 23.8467 | 0.288
GEN-2020-087 | 04 SOUTHEAST | 511503 | LAW WC2 | 69 | 4.8253 | 4.8306 | 0.0053
GEN-2020-087 | 04 SOUTHEAST | 511509 | 53CACHE4 | 138 | 12.6739 | 12.7535 | 0.0796
GEN-2020-087 | 04 SOUTHEAST | 511510 | LAIRGST4 | 138 | 13.3753 | 13.4565 | 0.0812
GEN-2020-087 | 04 SOUTHEAST | 511512 | RPPAPER4 | 138 | 12.9915 | 13.0705 | 0.079
GEN-2020-087 | 04 SOUTHEAST | 511524 | L-DISTP2 | 69 | 8.8779 | 8.8822 | 0.0043
GEN-2020-087 | 04 SOUTHEAST | 511537 | ARTVLTP4 | 138 | 12.6942 | 12.7743 | 0.0801
GEN-2020-087 | 04 SOUTHEAST | 511538 | ARTVILL4 | 138 | 9.1285 | 9.1708 | 0.0423
GEN-2020-087 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 11.2346 | 11.2631 | 0.0285
GEN-2020-087 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 12.1781 | 12.1984 | 0.0203
GEN-2020-087 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.415 | 10.4506 | 0.0356
GEN-2020-087 | 04 SOUTHEAST | 511565 | OKLAUN HVDC7 | 345 | 5.8866 | 5.9409 | 0.0543
GEN-2020-087 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 12.1223 | 12.3046 | 0.1823
GEN-2020-087 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 7.6417 | 7.7109 | 0.0692
GEN-2020-087 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 23.9461 | 24.1183 | 0.1722
GEN-2020-087 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 34.1675 | 34.2233 | 0.0558
GEN-2020-087 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.4078 | 47.4787 | 0.0709
GEN-2020-087 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 35.5364 | 35.6361 | 0.0997
GEN-2020-087 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 26.7638 | 26.8205 | 0.0567
GEN-2020-087 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 12.9703 | 13.0334 | 0.0631
GEN-2020-087 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 23.8539 | 24.0248 | 0.1709
GEN-2020-087 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 33.9036 | 33.9686 | 0.065
GEN-2020-087 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 14.8237 | 14.8918 | 0.0681
GEN-2020-087 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 16.8449 | 16.8709 | 0.026
GEN-2020-087 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 19.9527 | 20.3683 | 0.4156
GEN-2020-087 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.2283 | 33.3924 | 0.1641
GEN-2020-087 | 04 SOUTHEAST | 515939 | MNCWND47 | 345 | 10.4457 | 10.4815 | 0.0358
GEN-2020-087 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 11.2132 | 11.2413 | 0.0281
GEN-2020-087 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 27.656 | 27.7283 | 0.0723
GEN-2020-087 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.4355 | 44.5026 | 0.0671
GEN-2020-087 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 25.7452 | 25.8208 | 0.0756
GEN-2020-087 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.0834 | 13.1021 | 0.0187
GEN-2020-087 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 14.8381 | 14.8594 | 0.0213
GEN-2020-087 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 35.5634 | 35.6972 | 0.1338
GEN-2020-087 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 18.6873 | 18.7321 | 0.0448
GEN-2020-087 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.1206 | 11.1369 | 0.0163
GEN-2020-087 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.3814 | 8.3916 | 0.0102
GEN-2020-087 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.2652 | 9.2762 | 0.011
GEN-2020-087 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 29.2298 | 29.3279 | 0.0981
GEN-2020-087 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 5.9299 | 5.9354 | 0.0055
GEN-2020-087 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 5.9594 | 5.9688 | 0.0094
GEN-2020-087 | 04 SOUTHEAST | 529304 | OMDUNCN4 | 138 | 6.9561 | 6.9702 | 0.0141
GEN-2020-087 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 10.2645 | 10.317 | 0.0525
GEN-2020-087 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 9.8248 | 9.873 | 0.0482
GEN-2020-087 | 04 SOUTHEAST | 587740 | GEN-2016-091 | 345 | 11.7758 | 12.045 | 0.2692
GEN-2020-087 | 04 SOUTHEAST | 587770 | GEN-2016-095 | 345 | 12.0779 | 12.3638 | 0.2859
GEN-2020-087 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.26 | 9.2761 | 0.0161
GEN-2020-087 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.4343 | 11.4586 | 0.0243
GEN-2020-087 | 04 SOUTHEAST | 588760 | GEN-2017-033 | 345 | 4.2373 | 4.2673 | 0.03
GEN-2020-087 | 04 SOUTHEAST | 599891 | OKLAUN 7 | 345 | 4.3194 | 4.3194 | 0
GEN-2020-087 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 13.1501 | 13.4518 | 0.3017
GEN-2020-087 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 13.0741 | 13.3722 | 0.2981
GEN-2020-087 | 04 SOUTHEAST | 761229 | GEN-2017-150 | 345 | 23.1537 | 23.3148 | 0.1611
GEN-2020-087 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 23.1968 | 23.3586 | 0.1618
GEN-2020-087 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 8.3726 | 8.3898 | 0.0172
GEN-2020-087 | 04 SOUTHEAST | 762460 | GEN-2018-015 | 345 | 5.1497 | 5.175 | 0.0253
GEN-2020-087 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 5.1596 | 5.1849 | 0.0253
GEN-2020-087 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 7.1218 | 7.1822 | 0.0604
GEN-2020-087 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 15.5817 | 16.1761 | 0.5944
GEN-2020-087 | 04 SOUTHEAST | 764105 | GEN-2020-074 | 345 | 12.1673 | 12.2505 | 0.0832
GEN-2020-087 | 04 SOUTHEAST | 764115 | G20-074-TAP | 345 | 12.1729 | 12.2561 | 0.0832
GEN-2020-087 | 04 SOUTHEAST | 764540 | GEN-2020-075 | 345 | 15.096 | 16.0529 | 0.9569
GEN-2020-087 | 04 SOUTHEAST | 764550 | G20-075-TAP | 345 | 15.1065 | 16.0648 | 0.9583
GEN-2020-087 | 04 SOUTHEAST | 764555 | GEN-2020-087 | 345 | 15.0954 | 16.0537 | 0.9583
GEN-2020-087 | 04 SOUTHEAST | 766290 | GEN-2020-009 | 345 | 9.3458 | 9.5216 | 0.1758
GEN-2020-087 | 04 SOUTHEAST | 766291 | G20-009-TAP | 345 | 9.3458 | 9.5216 | 0.1758
GEN-2020-092 | 04 SOUTHEAST | 510366 | MCARBDE4 | 138 | 8.0231 | 8.4016 | 0.3785
GEN-2020-092 | 04 SOUTHEAST | 510373 | CHOUTEA4 | 138 | 7.2565 | 7.4444 | 0.1879
GEN-2020-092 | 04 SOUTHEAST | 510387 | ADAIR--2 | 69 | 6.0091 | 6.0696 | 0.0605
GEN-2020-092 | 04 SOUTHEAST | 510398 | BIRDHOL4 | 138 | 4.9938 | 5.091 | 0.0972
GEN-2020-092 | 04 SOUTHEAST | 510399 | LSTAR--3 | 115 | 11.1458 | 11.3057 | 0.1599
GEN-2020-092 | 04 SOUTHEAST | 510400 | PRY-JCT2 | 69 | 11.4376 | 11.681 | 0.2434
GEN-2020-092 | 04 SOUTHEAST | 510401 | EXCLART4 | 138 | 7.5353 | 7.7776 | 0.2423
GEN-2020-092 | 04 SOUTHEAST | 510402 | GROVE 4 | 138 | 5.3382 | 5.3764 | 0.0382
GEN-2020-092 | 04 SOUTHEAST | 510404 | VINITA-2 | 69 | 6.9137 | 6.9278 | 0.0141
GEN-2020-092 | 04 SOUTHEAST | 510405 | EXPCLAR4 | 138 | 5.2944 | 5.425 | 0.1306
GEN-2020-092 | 04 SOUTHEAST | 510407 | PRY-JCT3 | 115 | 9.6233 | 9.8397 | 0.2164
GEN-2020-092 | 04 SOUTHEAST | 510408 | PCP-TAP2 | 69 | 8.1118 | 8.1686 | 0.0568
GEN-2020-092 | 04 SOUTHEAST | 510411 | GROVE 5 | 161 | 5.8085 | 5.8357 | 0.0272
GEN-2020-092 | 04 SOUTHEAST | 510416 | HUNTAP-2 | 69 | 9.1106 | 9.1534 | 0.0428
GEN-2020-092 | 04 SOUTHEAST | 510418 | VINTAJC2 | 69 | 6.5713 | 6.581 | 0.0097
GEN-2020-092 | 04 SOUTHEAST | 510419 | PRY-JCT4 | 138 | 9.0023 | 9.4879 | 0.4856
GEN-2020-092 | 04 SOUTHEAST | 510421 | JAY 4 | 138 | 4.7011 | 4.755 | 0.0539
GEN-2020-092 | 04 SOUTHEAST | 510423 | L GROVE3 | 115 | 17.0778 | 17.2022 | 0.1244
GEN-2020-092 | 04 SOUTHEAST | 510425 | NEOHOME2 | 69 | 5.8177 | 5.8524 | 0.0347
GEN-2020-092 | 04 SOUTHEAST | 510431 | PRY_CRK4 | 138 | 7.6169 | 7.8955 | 0.2786
GEN-2020-092 | 04 SOUTHEAST | 510437 | ROCKPT-4 | 138 | 8.5738 | 8.6658 | 0.092
GEN-2020-092 | 04 SOUTHEAST | 512622 | PRYORC32 | 69 | 9.6908 | 9.7674 | 0.0766
GEN-2020-092 | 04 SOUTHEAST | 512634 | KERR GR3 | 115 | 18.2051 | 18.3271 | 0.122
GEN-2020-092 | 04 SOUTHEAST | 512639 | PRY0RC22 | 69 | 10.0909 | 10.1596 | 0.0687
GEN-2020-092 | 04 SOUTHEAST | 512680 | ESH TP 2 | 69 | 6.6512 | 6.6635 | 0.0123
GEN-2020-092 | 04 SOUTHEAST | 512719 | COWSKIN 4 | 138 | 4.5377 | 4.5665 | 0.0288
GEN-2020-092 | 04 SOUTHEAST | 512810 | PRYORC12 | 69 | 10.2098 | 10.3221 | 0.1123
GEN-2020-092 | 04 SOUTHEAST | 589120 | GEN-2017-074 | 138 | 8.9551 | 9.4357 | 0.4806
GEN-2020-092 | 04 SOUTHEAST | 589150 | GEN-2017-077 | 138 | 6.9922 | 7.2015 | 0.2093
GEN-2020-092 | 04 SOUTHEAST | 764150 | GEN-2020-092 | 138 | 8.5591 | 9.0742 | 0.5151
GEN-2020-092 | 04 SOUTHEAST | 764160 | G20-092-TAP | 138 | 8.669 | 9.1837 | 0.5147
GEN-2020-060 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.815 | 8.8205 | 0.0055
GEN-2020-060 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 12.7314 | 12.7374 | 0.006
GEN-2020-060 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 26.7074 | 26.7231 | 0.0157
GEN-2020-060 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 16.7535 | 16.7632 | 0.0097
GEN-2020-060 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 29.6206 | 29.6355 | 0.0149
GEN-2020-060 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.0459 | 16.0558 | 0.0099
GEN-2020-060 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 18.2047 | 18.2153 | 0.0106
GEN-2020-060 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.958 | 14.9685 | 0.0105
GEN-2020-060 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.9377 | 6.9431 | 0.0054
GEN-2020-060 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.6665 | 8.6732 | 0.0067
GEN-2020-060 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.5741 | 11.5833 | 0.0092
GEN-2020-060 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.4164 | 10.4252 | 0.0088
GEN-2020-060 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4874 | 5.4936 | 0.0062
GEN-2020-060 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.3392 | 8.3495 | 0.0103
GEN-2020-060 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 8.0288 | 8.042 | 0.0132
GEN-2020-060 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 7.0698 | 7.0819 | 0.0121
GEN-2020-060 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.8281 | 4.8369 | 0.0088
GEN-2020-060 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.7531 | 12.7815 | 0.0284
GEN-2020-060 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 12.1671 | 12.1935 | 0.0264
GEN-2020-060 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2805 | 11.3075 | 0.027
GEN-2020-060 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 7.0086 | 7.0251 | 0.0165
GEN-2020-060 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.7669 | 5.7831 | 0.0162
GEN-2020-060 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.7637 | 6.7805 | 0.0168
GEN-2020-060 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.8509 | 2.8575 | 0.0066
GEN-2020-060 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.5876 | 3.5978 | 0.0102
GEN-2020-060 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.8708 | 6.8934 | 0.0226
GEN-2020-060 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.3908 | 2.4003 | 0.0095
GEN-2020-060 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.2285 | 5.2377 | 0.0092
GEN-2020-060 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 8.0265 | 8.0418 | 0.0153
GEN-2020-060 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 6.1655 | 6.1807 | 0.0152
GEN-2020-060 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.4216 | 7.4345 | 0.0129
GEN-2020-060 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 9.6581 | 9.6731 | 0.015
GEN-2020-060 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 7.1657 | 7.1836 | 0.0179
GEN-2020-060 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.9064 | 10.9385 | 0.0321
GEN-2020-060 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.3987 | 15.4242 | 0.0255
GEN-2020-060 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.8837 | 11.9043 | 0.0206
GEN-2020-060 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.8335 | 15.8576 | 0.0241
GEN-2020-060 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.3986 | 24.4382 | 0.0396
GEN-2020-060 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.65 | 31.6958 | 0.0458
GEN-2020-060 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.7308 | 13.745 | 0.0142
GEN-2020-060 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5435 | 11.5562 | 0.0127
GEN-2020-060 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5435 | 11.5562 | 0.0127
GEN-2020-060 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.9887 | 9.0017 | 0.013
GEN-2020-060 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0115 | 6.019 | 0.0075
GEN-2020-060 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.5173 | 2.5275 | 0.0102
GEN-2020-060 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.4418 | 3.4561 | 0.0143
GEN-2020-060 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.8106 | 2.8221 | 0.0115
GEN-2020-060 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.7792 | 2.7906 | 0.0114
GEN-2020-060 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1443 | 6.1713 | 0.027
GEN-2020-060 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.8205 | 5.8458 | 0.0253
GEN-2020-060 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.9222 | 6.9569 | 0.0347
GEN-2020-060 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.8055 | 2.8167 | 0.0112
GEN-2020-060 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 5.613 | 5.6451 | 0.0321
GEN-2020-060 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.6141 | 5.6462 | 0.0321
GEN-2020-060 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.6706 | 4.6904 | 0.0198
GEN-2020-060 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 5.2338 | 5.2565 | 0.0227
GEN-2020-060 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.7857 | 8.8273 | 0.0416
GEN-2020-060 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.5873 | 20.7443 | 0.157
GEN-2020-060 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 24.0024 | 24.1991 | 0.1967
GEN-2020-060 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 15.5989 | 15.6719 | 0.073
GEN-2020-060 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 23.8028 | 23.9966 | 0.1938
GEN-2020-060 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 15.4815 | 15.5534 | 0.0719
GEN-2020-060 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.9106 | 2.9225 | 0.0119
GEN-2020-060 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.5838 | 2.5943 | 0.0105
GEN-2020-060 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.7767 | 3.7926 | 0.0159
GEN-2020-060 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 3.0318 | 3.0443 | 0.0125
GEN-2020-060 | 05 SOUTHWEST | 525906 | SP-ACUFF +2 | 69 | 2.1406 | 2.1602 | 0.0196
GEN-2020-060 | 05 SOUTHWEST | 525915 | SP-CROSBY 2 | 69 | 5.2414 | 5.2713 | 0.0299
GEN-2020-060 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 5.7547 | 5.7889 | 0.0342
GEN-2020-060 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4394 | 5.4781 | 0.0387
GEN-2020-060 | 05 SOUTHWEST | 525936 | LH-CROSBY +2 | 69 | 3.8043 | 3.8256 | 0.0213
GEN-2020-060 | 05 SOUTHWEST | 525943 | HENDRICKS 2 | 69 | 3.766 | 3.7871 | 0.0211
GEN-2020-060 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.5696 | 11.629 | 0.0594
GEN-2020-060 | 05 SOUTHWEST | 526075 | STANTON_E 2 | 69 | 3.5135 | 3.5478 | 0.0343
GEN-2020-060 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.8139 | 9.8839 | 0.07
GEN-2020-060 | 05 SOUTHWEST | 526086 | SW_6786_N 2 | 69 | 5.5248 | 5.5834 | 0.0586
GEN-2020-060 | 05 SOUTHWEST | 526087 | SW_6786_S 2 | 69 | 5.5248 | 5.5834 | 0.0586
GEN-2020-060 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.9167 | 12.0132 | 0.0965
GEN-2020-060 | 05 SOUTHWEST | 526123 | VICKERS 2 | 69 | 2.2645 | 2.2853 | 0.0208
GEN-2020-060 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 10.2076 | 10.2826 | 0.075
GEN-2020-060 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.9523 | 2.9681 | 0.0158
GEN-2020-060 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 13.7327 | 13.8534 | 0.1207
GEN-2020-060 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.2489 | 11.3588 | 0.1099
GEN-2020-060 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.269 | 12.3683 | 0.0993
GEN-2020-060 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.2068 | 11.3086 | 0.1018
GEN-2020-060 | 05 SOUTHWEST | 526199 | SP-FRANKFRD3 | 115 | 10.3943 | 10.4984 | 0.1041
GEN-2020-060 | 05 SOUTHWEST | 526205 | IVORY 2 | 69 | 4.2085 | 4.246 | 0.0375
GEN-2020-060 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 11.4564 | 11.5974 | 0.141
GEN-2020-060 | 05 SOUTHWEST | 526228 | BATTON_S 2 | 69 | 2.9505 | 2.9755 | 0.025
GEN-2020-060 | 05 SOUTHWEST | 526236 | LP-WHEELOCK3 | 115 | 9.2435 | 9.3471 | 0.1036
GEN-2020-060 | 05 SOUTHWEST | 526243 | SP-QUAKER 3 | 115 | 10.4949 | 10.6075 | 0.1126
GEN-2020-060 | 05 SOUTHWEST | 526249 | ACCO 2 | 69 | 3.4425 | 3.4723 | 0.0298
GEN-2020-060 | 05 SOUTHWEST | 526256 | IVORY_TP 2 | 69 | 4.1971 | 4.2345 | 0.0374
GEN-2020-060 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.6317 | 4.6736 | 0.0419
GEN-2020-060 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.1707 | 19.5446 | 0.3739
GEN-2020-060 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.1946 | 16.6522 | 0.4576
GEN-2020-060 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 6.3971 | 6.4673 | 0.0702
GEN-2020-060 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 8.9699 | 9.0776 | 0.1077
GEN-2020-060 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.8253 | 16.1475 | 0.3222
GEN-2020-060 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 11.9966 | 12.645 | 0.6484
GEN-2020-060 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.974 | 6.0388 | 0.0648
GEN-2020-060 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 17.934 | 18.54 | 0.606
GEN-2020-060 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.4226 | 11.4561 | 0.0335
GEN-2020-060 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.8225 | 11.8809 | 0.0584
GEN-2020-060 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.4752 | 10.5192 | 0.044
GEN-2020-060 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 11.6147 | 11.7037 | 0.089
GEN-2020-060 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.1264 | 12.2138 | 0.0874
GEN-2020-060 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.5745 | 13.7562 | 0.1817
GEN-2020-060 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.6899 | 2.7152 | 0.0253
GEN-2020-060 | 05 SOUTHWEST | 526569 | SP-SLATON 2 | 69 | 1.3173 | 1.3281 | 0.0108
GEN-2020-060 | 05 SOUTHWEST | 526576 | SOUTHLAND 2 | 69 | 1.5065 | 1.519 | 0.0125
GEN-2020-060 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 10.0005 | 10.1388 | 0.1383
GEN-2020-060 | 05 SOUTHWEST | 526655 | LYNN_CNTY 2 | 69 | 4.8755 | 4.922 | 0.0465
GEN-2020-060 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 6.5279 | 6.6059 | 0.078
GEN-2020-060 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.5625 | 7.6591 | 0.0966
GEN-2020-060 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.5409 | 6.6513 | 0.1104
GEN-2020-060 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1334 | 5.2099 | 0.0765
GEN-2020-060 | 05 SOUTHWEST | 526693 | GRAHAM 2 | 69 | 3.6072 | 3.6402 | 0.033
GEN-2020-060 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 3.1029 | 3.1332 | 0.0303
GEN-2020-060 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.5927 | 11.6273 | 0.0346
GEN-2020-060 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 22.0927 | 22.1267 | 0.034
GEN-2020-060 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 12.1165 | 12.1338 | 0.0173
GEN-2020-060 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 13.169 | 13.1787 | 0.0097
GEN-2020-060 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.4164 | 10.4252 | 0.0088
GEN-2020-060 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.2225 | 8.2298 | 0.0073
GEN-2020-060 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.3562 | 14.3712 | 0.015
GEN-2020-060 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 9.6542 | 9.6827 | 0.0285
GEN-2020-060 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.1315 | 7.1498 | 0.0183
GEN-2020-060 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 6.1718 | 6.1798 | 0.008
GEN-2020-060 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.545 | 11.5648 | 0.0198
GEN-2020-060 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.3678 | 9.3755 | 0.0077
GEN-2020-060 | 05 SOUTHWEST | 764825 | GEN-2020-017 | 230 | 5.9911 | 5.9986 | 0.0075
GEN-2020-060 | 05 SOUTHWEST | 764875 | GEN-2020-060 | 230 | 11.807 | 12.4558 | 0.6488
GEN-2020-060 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 7.9538 | 7.9682 | 0.0144
GEN-2020-060 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 9.7031 | 9.7221 | 0.019
GEN-2020-060 | 05 SOUTHWEST | 764950 | GEN-2020-068 | 345 | 9.6577 | 9.6765 | 0.0188
GEN-2020-065 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 16.3816 | 16.7632 | 0.3816
GEN-2020-065 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 6.7552 | 6.9314 | 0.1762
GEN-2020-065 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.2882 | 31.6958 | 0.4076
GEN-2020-065 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.4578 | 13.745 | 0.2872
GEN-2020-065 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.6629 | 22.1267 | 0.4638
GEN-2020-065 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.661 | 12.1338 | 0.4728
GEN-2020-065 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 345 | 7.8125 | 13.4586 | 5.6461
GEN-2020-065 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 8.9309 | 14.1095 | 5.1786
GEN-2020-065 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 14.1785 | 14.3258 | 0.1473
GEN-2020-065 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.1005 | 12.3427 | 0.2422
GEN-2020-065 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 10.0656 | 10.729 | 0.6634
GEN-2020-065 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.0656 | 10.729 | 0.6634
GEN-2020-065 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 8.8442 | 9.3089 | 0.4647
GEN-2020-065 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.3484 | 11.0061 | 0.6577
GEN-2020-065 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 12.2221 | 13.1787 | 0.9566
GEN-2020-065 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 5.4596 | 5.7303 | 0.2707
GEN-2020-065 | 05 SOUTHWEST | 527799 | EDDY_NORTH 6 | 230 | 10.2316 | 10.6863 | 0.4547
GEN-2020-065 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 8.1115 | 8.6502 | 0.5387
GEN-2020-065 | 05 SOUTHWEST | 527864 | CUNNINHAM 3 | 115 | 29.8065 | 30.7672 | 0.9607
GEN-2020-065 | 05 SOUTHWEST | 527865 | CUNNIGHM_N 6 | 230 | 18.9049 | 19.9777 | 1.0728
GEN-2020-065 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 18.9049 | 19.9777 | 1.0728
GEN-2020-065 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 34.0257 | 35.196 | 1.1703
GEN-2020-065 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 20.9774 | 22.481 | 1.5036
GEN-2020-065 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 14.3311 | 18.2313 | 3.9002
GEN-2020-065 | 05 SOUTHWEST | 527962 | POTASH_JCT 3 | 115 | 19.212 | 20.242 | 1.03
GEN-2020-065 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 10.9737 | 12.2426 | 1.2689
GEN-2020-065 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 19.2274 | 20.2673 | 1.0399
GEN-2020-065 | 05 SOUTHWEST | 528013 | PHANTOM 3 | 115 | 18.512 | 19.3842 | 0.8722
GEN-2020-065 | 05 SOUTHWEST | 528014 | PHANTOM 9 | 765 | 4.6483 | 4.9613 | 0.313
GEN-2020-065 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 10.328 | 11.0781 | 0.7501
GEN-2020-065 | 05 SOUTHWEST | 528018 | RED_BLUFF 3 | 115 | 12.1434 | 12.6199 | 0.4765
GEN-2020-065 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 16.1561 | 17.1756 | 1.0195
GEN-2020-065 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 16.1561 | 17.1756 | 1.0195
GEN-2020-065 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 11.0583 | 12.6728 | 1.6145
GEN-2020-065 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.4836 | 3.5479 | 0.0643
GEN-2020-065 | 05 SOUTHWEST | 528182 | NORTH_LOVNG3 | 115 | 15.4646 | 16.1179 | 0.6533
GEN-2020-065 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 8.9323 | 9.6356 | 0.7033
GEN-2020-065 | 05 SOUTHWEST | 528223 | CHINA_DRAW 7 | 345 | 8.8358 | 9.4495 | 0.6137
GEN-2020-065 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 14.301 | 15.1096 | 0.8086
GEN-2020-065 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 13.4062 | 14.1197 | 0.7135
GEN-2020-065 | 05 SOUTHWEST | 528239 | CUSTERMTN 3 | 115 | 8.3771 | 8.6705 | 0.2934
GEN-2020-065 | 05 SOUTHWEST | 528333 | LE-WEST_SUB3 | 115 | 9.4681 | 9.5573 | 0.0892
GEN-2020-065 | 05 SOUTHWEST | 528355 | MADDOX 3 | 115 | 28.6973 | 29.5751 | 0.8778
GEN-2020-065 | 05 SOUTHWEST | 528433 | BENSING 3 | 115 | 8.5445 | 8.6297 | 0.0852
GEN-2020-065 | 05 SOUTHWEST | 528434 | MILLEN_TPW 3 | 115 | 12.478 | 12.6853 | 0.2073
GEN-2020-065 | 05 SOUTHWEST | 528589 | DRINKARD 3 | 115 | 8.9318 | 9.5031 | 0.5713
GEN-2020-065 | 05 SOUTHWEST | 528602 | ANDREWS 3 | 115 | 13.486 | 15.5884 | 2.1024
GEN-2020-065 | 05 SOUTHWEST | 528603 | NA_ENRICH 3 | 115 | 12.7415 | 14.4117 | 1.6702
GEN-2020-065 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 7.0953 | 9.7535 | 2.6582
GEN-2020-065 | 05 SOUTHWEST | 528605 | TARGA 3 | 115 | 9.8117 | 10.6615 | 0.8498
GEN-2020-065 | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 14.7842 | 15.6484 | 0.8642
GEN-2020-065 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 15.8633 | 16.8481 | 0.9848
GEN-2020-065 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.8605 | 11.2734 | 0.4129
GEN-2020-065 | 05 SOUTHWEST | 764840 | GEN-2020-059 | 345 | 10.4946 | 11.2843 | 0.7897
GEN-2020-065 | 05 SOUTHWEST | 764866 | G20-059-TAP | 345 | 10.5553 | 11.3548 | 0.7995
GEN-2020-065 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 9.5741 | 9.7221 | 0.148
GEN-2020-067 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 6.6508 | 6.6621 | 0.0113
GEN-2020-067 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.6807 | 12.6947 | 0.014
GEN-2020-067 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.8842 | 12.8947 | 0.0105
GEN-2020-067 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 6.6298 | 6.641 | 0.0112
GEN-2020-067 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 19.7657 | 19.7725 | 0.0068
GEN-2020-067 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 25.7228 | 25.73 | 0.0072
GEN-2020-067 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.144 | 17.1481 | 0.0041
GEN-2020-067 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.8076 | 8.8205 | 0.0129
GEN-2020-067 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 14.2055 | 14.2086 | 0.0031
GEN-2020-067 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 12.3267 | 12.3306 | 0.0039
GEN-2020-067 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 12.7232 | 12.7374 | 0.0142
GEN-2020-067 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9867 | 14.9928 | 0.0061
GEN-2020-067 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 26.6933 | 26.7231 | 0.0298
GEN-2020-067 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 16.7366 | 16.7632 | 0.0266
GEN-2020-067 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 6.9199 | 6.9314 | 0.0115
GEN-2020-067 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 29.6107 | 29.6355 | 0.0248
GEN-2020-067 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 6.3981 | 6.405 | 0.0069
GEN-2020-067 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.0415 | 16.0558 | 0.0143
GEN-2020-067 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 18.2003 | 18.2153 | 0.015
GEN-2020-067 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.954 | 14.9685 | 0.0145
GEN-2020-067 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.9349 | 6.9431 | 0.0082
GEN-2020-067 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.6626 | 8.6732 | 0.0106
GEN-2020-067 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.5697 | 11.5833 | 0.0136
GEN-2020-067 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.4116 | 10.4252 | 0.0136
GEN-2020-067 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.7556 | 12.7815 | 0.0259
GEN-2020-067 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 12.1684 | 12.1935 | 0.0251
GEN-2020-067 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2782 | 11.3075 | 0.0293
GEN-2020-067 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.8785 | 6.8934 | 0.0149
GEN-2020-067 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 8.0277 | 8.0418 | 0.0141
GEN-2020-067 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 7.1694 | 7.1836 | 0.0142
GEN-2020-067 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.9137 | 10.9385 | 0.0248
GEN-2020-067 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.3972 | 15.4242 | 0.027
GEN-2020-067 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.8812 | 11.9043 | 0.0231
GEN-2020-067 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.8315 | 15.8576 | 0.0261
GEN-2020-067 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.3864 | 24.4382 | 0.0518
GEN-2020-067 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.6224 | 31.6958 | 0.0734
GEN-2020-067 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.7159 | 13.745 | 0.0291
GEN-2020-067 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.9201 | 10.9431 | 0.023
GEN-2020-067 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5314 | 11.5562 | 0.0248
GEN-2020-067 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5314 | 11.5562 | 0.0248
GEN-2020-067 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.9869 | 9.0017 | 0.0148
GEN-2020-067 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.0097 | 6.019 | 0.0093
GEN-2020-067 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.4459 | 3.4561 | 0.0102
GEN-2020-067 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.8139 | 2.8221 | 0.0082
GEN-2020-067 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1569 | 6.1713 | 0.0144
GEN-2020-067 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.8326 | 5.8458 | 0.0132
GEN-2020-067 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.9397 | 6.9569 | 0.0172
GEN-2020-067 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.6341 | 5.6462 | 0.0121
GEN-2020-067 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 5.2405 | 5.2565 | 0.016
GEN-2020-067 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.7987 | 8.8273 | 0.0286
GEN-2020-067 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.6468 | 20.7443 | 0.0975
GEN-2020-067 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 23.972 | 24.1991 | 0.2271
GEN-2020-067 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 15.4203 | 15.6719 | 0.2516
GEN-2020-067 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 23.7729 | 23.9966 | 0.2237
GEN-2020-067 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 15.3059 | 15.5534 | 0.2475
GEN-2020-067 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.914 | 2.9225 | 0.0085
GEN-2020-067 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.7813 | 3.7926 | 0.0113
GEN-2020-067 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4668 | 5.4781 | 0.0113
GEN-2020-067 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.562 | 11.629 | 0.067
GEN-2020-067 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.8521 | 9.8839 | 0.0318
GEN-2020-067 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.9742 | 12.0132 | 0.039
GEN-2020-067 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 10.2495 | 10.2826 | 0.0331
GEN-2020-067 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.9607 | 2.9681 | 0.0074
GEN-2020-067 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 13.8074 | 13.8534 | 0.046
GEN-2020-067 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.31 | 11.3588 | 0.0488
GEN-2020-067 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.3288 | 12.3683 | 0.0395
GEN-2020-067 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.2744 | 11.3086 | 0.0342
GEN-2020-067 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.4876 | 19.5446 | 0.057
GEN-2020-067 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.5967 | 16.6522 | 0.0555
GEN-2020-067 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 9.0568 | 9.0776 | 0.0208
GEN-2020-067 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 16.1016 | 16.1475 | 0.0459
GEN-2020-067 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.6093 | 12.645 | 0.0357
GEN-2020-067 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.4794 | 18.54 | 0.0606
GEN-2020-067 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.4246 | 11.4561 | 0.0315
GEN-2020-067 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.8372 | 11.8809 | 0.0437
GEN-2020-067 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.4793 | 10.5192 | 0.0399
GEN-2020-067 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.1761 | 12.2138 | 0.0377
GEN-2020-067 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.7025 | 13.7562 | 0.0537
GEN-2020-067 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.6423 | 7.6591 | 0.0168
GEN-2020-067 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6355 | 6.6513 | 0.0158
GEN-2020-067 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.198 | 5.2099 | 0.0119
GEN-2020-067 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.5932 | 11.6273 | 0.0341
GEN-2020-067 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 17.0681 | 17.1598 | 0.0917
GEN-2020-067 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.5563 | 6.5762 | 0.0199
GEN-2020-067 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.7997 | 10.8402 | 0.0405
GEN-2020-067 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 20.4414 | 20.5405 | 0.0991
GEN-2020-067 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.9247 | 22.1267 | 0.202
GEN-2020-067 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.791 | 12.1338 | 0.3428
GEN-2020-067 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.5416 | 8.5709 | 0.0293
GEN-2020-067 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 345 | 13.4187 | 13.4586 | 0.0399
GEN-2020-067 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 17.1754 | 17.2891 | 0.1137
GEN-2020-067 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 17.01 | 17.122 | 0.112
GEN-2020-067 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.8178 | 16.9211 | 0.1033
GEN-2020-067 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.8618 | 14.9114 | 0.0496
GEN-2020-067 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 14.0614 | 14.1095 | 0.0481
GEN-2020-067 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 14.2835 | 14.3258 | 0.0423
GEN-2020-067 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.2866 | 12.3427 | 0.0561
GEN-2020-067 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 13.2346 | 13.2724 | 0.0378
GEN-2020-067 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.7592 | 14.8086 | 0.0494
GEN-2020-067 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.7489 | 11.786 | 0.0371
GEN-2020-067 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 18.0109 | 18.0687 | 0.0578
GEN-2020-067 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 24.2639 | 24.3425 | 0.0786
GEN-2020-067 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 24.2639 | 24.3425 | 0.0786
GEN-2020-067 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.8892 | 25.9727 | 0.0835
GEN-2020-067 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 19.5859 | 19.6859 | 0.1
GEN-2020-067 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 19.5859 | 19.6859 | 0.1
GEN-2020-067 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.598 | 8.6229 | 0.0249
GEN-2020-067 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.8958 | 9.9234 | 0.0276
GEN-2020-067 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 15.4118 | 15.4577 | 0.0459
GEN-2020-067 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.8929 | 8.9225 | 0.0296
GEN-2020-067 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.6985 | 10.729 | 0.0305
GEN-2020-067 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.9762 | 11.0061 | 0.0299
GEN-2020-067 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 13.1392 | 13.1787 | 0.0395
GEN-2020-067 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 5.7176 | 5.7303 | 0.0127
GEN-2020-067 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 8.6269 | 8.6502 | 0.0233
GEN-2020-067 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 19.9266 | 19.9777 | 0.0511
GEN-2020-067 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 35.1278 | 35.196 | 0.0682
GEN-2020-067 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 22.4129 | 22.481 | 0.0681
GEN-2020-067 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 18.1307 | 18.2313 | 0.1006
GEN-2020-067 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 12.201 | 12.2426 | 0.0416
GEN-2020-067 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 20.2175 | 20.2673 | 0.0498
GEN-2020-067 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 11.0486 | 11.0781 | 0.0295
GEN-2020-067 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 17.1307 | 17.1756 | 0.0449
GEN-2020-067 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 12.6243 | 12.6728 | 0.0485
GEN-2020-067 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 9.6083 | 9.6356 | 0.0273
GEN-2020-067 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.6289 | 9.6522 | 0.0233
GEN-2020-067 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.7254 | 9.7535 | 0.0281
GEN-2020-067 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.8906 | 3.9023 | 0.0117
GEN-2020-067 | 05 SOUTHWEST | 560071 | G16-003-TAP | 345 | 15.0176 | 15.0226 | 0.005
GEN-2020-067 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 9.8496 | 9.8566 | 0.007
GEN-2020-067 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 14.2835 | 14.3258 | 0.0423
GEN-2020-067 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.9435 | 4.9509 | 0.0074
GEN-2020-067 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.4116 | 10.4252 | 0.0136
GEN-2020-067 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.2203 | 8.2298 | 0.0095
GEN-2020-067 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 15.0672 | 15.1537 | 0.0865
GEN-2020-067 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.3487 | 14.3712 | 0.0225
GEN-2020-067 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 9.5962 | 9.6827 | 0.0865
GEN-2020-067 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0984 | 7.1498 | 0.0514
GEN-2020-067 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 6.149 | 6.1692 | 0.0202
GEN-2020-067 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 6.1597 | 6.1798 | 0.0201
GEN-2020-067 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.5426 | 11.5648 | 0.0222
GEN-2020-067 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.3637 | 9.3755 | 0.0118
GEN-2020-067 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.9719 | 11.2734 | 0.3015
GEN-2020-067 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 17.4922 | 17.498 | 0.0058
GEN-2020-067 | 05 SOUTHWEST | 764825 | GEN-2020-017 | 230 | 5.9893 | 5.9986 | 0.0093
GEN-2020-067 | 05 SOUTHWEST | 764840 | GEN-2020-059 | 345 | 11.1183 | 11.2843 | 0.166
GEN-2020-067 | 05 SOUTHWEST | 764866 | G20-059-TAP | 345 | 11.187 | 11.3548 | 0.1678
GEN-2020-067 | 05 SOUTHWEST | 764875 | GEN-2020-060 | 230 | 12.4208 | 12.4558 | 0.035
GEN-2020-067 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 7.2083 | 7.9682 | 0.7599
GEN-2020-067 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 8.9732 | 9.7221 | 0.7489
GEN-2020-067 | 05 SOUTHWEST | 764948 | G20-068-SS1 | 345 | 7.3495 | 7.8532 | 0.5037
GEN-2020-067 | 05 SOUTHWEST | 764949 | G20-068-SS2 | 345 | 7.3471 | 7.8507 | 0.5036
GEN-2020-067 | 05 SOUTHWEST | 764950 | GEN-2020-068 | 345 | 8.9345 | 9.6765 | 0.742
GEN-2020-067 | 05 SOUTHWEST | 766291 | G20-009-TAP | 345 | 9.6378 | 9.6466 | 0.0088
GEN-2020-068 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 6.6457 | 6.6621 | 0.0164
GEN-2020-068 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 12.6747 | 12.6947 | 0.02
GEN-2020-068 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 12.8792 | 12.8947 | 0.0155
GEN-2020-068 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 6.6247 | 6.641 | 0.0163
GEN-2020-068 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 19.7627 | 19.7725 | 0.0098
GEN-2020-068 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 25.7196 | 25.73 | 0.0104
GEN-2020-068 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.1421 | 17.1481 | 0.006
GEN-2020-068 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 8.8019 | 8.8205 | 0.0186
GEN-2020-068 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 14.204 | 14.2086 | 0.0046
GEN-2020-068 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 12.3249 | 12.3306 | 0.0057
GEN-2020-068 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 12.717 | 12.7374 | 0.0204
GEN-2020-068 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 14.9841 | 14.9928 | 0.0087
GEN-2020-068 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 26.6828 | 26.7231 | 0.0403
GEN-2020-068 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 16.7272 | 16.7632 | 0.036
GEN-2020-068 | 05 SOUTHWEST | 523966 | POTTER_CO 9 | 765 | 6.9158 | 6.9314 | 0.0156
GEN-2020-068 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 29.6019 | 29.6355 | 0.0336
GEN-2020-068 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 6.3952 | 6.405 | 0.0098
GEN-2020-068 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 16.0362 | 16.0558 | 0.0196
GEN-2020-068 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 18.1944 | 18.2153 | 0.0209
GEN-2020-068 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.9485 | 14.9685 | 0.02
GEN-2020-068 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.9315 | 6.9431 | 0.0116
GEN-2020-068 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 8.6583 | 8.6732 | 0.0149
GEN-2020-068 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.5641 | 11.5833 | 0.0192
GEN-2020-068 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 10.4062 | 10.4252 | 0.019
GEN-2020-068 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.7451 | 12.7815 | 0.0364
GEN-2020-068 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 12.1583 | 12.1935 | 0.0352
GEN-2020-068 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.2674 | 11.3075 | 0.0401
GEN-2020-068 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.8722 | 6.8934 | 0.0212
GEN-2020-068 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 8.0218 | 8.0418 | 0.02
GEN-2020-068 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 7.1631 | 7.1836 | 0.0205
GEN-2020-068 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.9036 | 10.9385 | 0.0349
GEN-2020-068 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.3864 | 15.4242 | 0.0378
GEN-2020-068 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.8725 | 11.9043 | 0.0318
GEN-2020-068 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.821 | 15.8576 | 0.0366
GEN-2020-068 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.3691 | 24.4382 | 0.0691
GEN-2020-068 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 31.5992 | 31.6958 | 0.0966
GEN-2020-068 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.706 | 13.745 | 0.039
GEN-2020-068 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.9117 | 10.9431 | 0.0314
GEN-2020-068 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.5225 | 11.5562 | 0.0337
GEN-2020-068 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.5225 | 11.5562 | 0.0337
GEN-2020-068 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.9809 | 9.0017 | 0.0208
GEN-2020-068 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 6.006 | 6.019 | 0.013
GEN-2020-068 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.4416 | 3.4561 | 0.0145
GEN-2020-068 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.8104 | 2.8221 | 0.0117
GEN-2020-068 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.1507 | 6.1713 | 0.0206
GEN-2020-068 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.8267 | 5.8458 | 0.0191
GEN-2020-068 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 6.9325 | 6.9569 | 0.0244
GEN-2020-068 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 5.6286 | 5.6462 | 0.0176
GEN-2020-068 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 5.2339 | 5.2565 | 0.0226
GEN-2020-068 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.7873 | 8.8273 | 0.04
GEN-2020-068 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.6146 | 20.7443 | 0.1297
GEN-2020-068 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 23.9103 | 24.1991 | 0.2888
GEN-2020-068 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 15.3554 | 15.6719 | 0.3165
GEN-2020-068 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 23.712 | 23.9966 | 0.2846
GEN-2020-068 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 15.2419 | 15.5534 | 0.3115
GEN-2020-068 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.9103 | 2.9225 | 0.0122
GEN-2020-068 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.7766 | 3.7926 | 0.016
GEN-2020-068 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4617 | 5.4781 | 0.0164
GEN-2020-068 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 11.5406 | 11.629 | 0.0884
GEN-2020-068 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.8401 | 9.8839 | 0.0438
GEN-2020-068 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.9597 | 12.0132 | 0.0535
GEN-2020-068 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 10.2371 | 10.2826 | 0.0455
GEN-2020-068 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.9576 | 2.9681 | 0.0105
GEN-2020-068 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 13.7906 | 13.8534 | 0.0628
GEN-2020-068 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 11.2937 | 11.3588 | 0.0651
GEN-2020-068 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 12.3142 | 12.3683 | 0.0541
GEN-2020-068 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.2616 | 11.3086 | 0.047
GEN-2020-068 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.4676 | 19.5446 | 0.077
GEN-2020-068 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.5789 | 16.6522 | 0.0733
GEN-2020-068 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 9.0483 | 9.0776 | 0.0293
GEN-2020-068 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 16.0848 | 16.1475 | 0.0627
GEN-2020-068 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.5972 | 12.645 | 0.0478
GEN-2020-068 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.4602 | 18.54 | 0.0798
GEN-2020-068 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.4127 | 11.4561 | 0.0434
GEN-2020-068 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.8224 | 11.8809 | 0.0585
GEN-2020-068 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.4657 | 10.5192 | 0.0535
GEN-2020-068 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 12.1622 | 12.2138 | 0.0516
GEN-2020-068 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.685 | 13.7562 | 0.0712
GEN-2020-068 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.6357 | 7.6591 | 0.0234
GEN-2020-068 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.6296 | 6.6513 | 0.0217
GEN-2020-068 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1936 | 5.2099 | 0.0163
GEN-2020-068 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.5805 | 11.6273 | 0.0468
GEN-2020-068 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 17.0402 | 17.1598 | 0.1196
GEN-2020-068 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.5486 | 6.5762 | 0.0276
GEN-2020-068 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.785 | 10.8402 | 0.0552
GEN-2020-068 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 20.4093 | 20.5405 | 0.1312
GEN-2020-068 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.8695 | 22.1267 | 0.2572
GEN-2020-068 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 11.7074 | 12.1338 | 0.4264
GEN-2020-068 | 05 SOUTHWEST | 526944 | LG-PLAINS 3 | 115 | 8.5305 | 8.5709 | 0.0404
GEN-2020-068 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 345 | 13.4061 | 13.4586 | 0.0525
GEN-2020-068 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 17.1418 | 17.2891 | 0.1473
GEN-2020-068 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 16.9768 | 17.122 | 0.1452
GEN-2020-068 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.7868 | 16.9211 | 0.1343
GEN-2020-068 | 05 SOUTHWEST | 527018 | BENNETT 3 | 115 | 14.8444 | 14.9114 | 0.067
GEN-2020-068 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 14.0465 | 14.1095 | 0.063
GEN-2020-068 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 14.2684 | 14.3258 | 0.0574
GEN-2020-068 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.2684 | 12.3427 | 0.0743
GEN-2020-068 | 05 SOUTHWEST | 527030 | ALRDCRTZ_TP3 | 115 | 13.221 | 13.2724 | 0.0514
GEN-2020-068 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.7418 | 14.8086 | 0.0668
GEN-2020-068 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.7355 | 11.786 | 0.0505
GEN-2020-068 | 05 SOUTHWEST | 527062 | SHELL_CO2 3 | 115 | 17.991 | 18.0687 | 0.0777
GEN-2020-068 | 05 SOUTHWEST | 527130 | DENVER_N 3 | 115 | 24.2376 | 24.3425 | 0.1049
GEN-2020-068 | 05 SOUTHWEST | 527136 | DENVER_S 3 | 115 | 24.2376 | 24.3425 | 0.1049
GEN-2020-068 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.8615 | 25.9727 | 0.1112
GEN-2020-068 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 19.5559 | 19.6859 | 0.13
GEN-2020-068 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 19.5559 | 19.6859 | 0.13
GEN-2020-068 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.5885 | 8.6229 | 0.0344
GEN-2020-068 | 05 SOUTHWEST | 527202 | SEAGRAVES 3 | 115 | 9.8853 | 9.9234 | 0.0381
GEN-2020-068 | 05 SOUTHWEST | 527275 | SEMINOLE 3 | 115 | 15.3956 | 15.4577 | 0.0621
GEN-2020-068 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.8826 | 8.9225 | 0.0399
GEN-2020-068 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.6884 | 10.729 | 0.0406
GEN-2020-068 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.9661 | 11.0061 | 0.04
GEN-2020-068 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 13.1264 | 13.1787 | 0.0523
GEN-2020-068 | 05 SOUTHWEST | 527669 | CROSSROADS 9 | 765 | 5.7132 | 5.7303 | 0.0171
GEN-2020-068 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 8.6187 | 8.6502 | 0.0315
GEN-2020-068 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 19.91 | 19.9777 | 0.0677
GEN-2020-068 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 35.1049 | 35.196 | 0.0911
GEN-2020-068 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 22.3917 | 22.481 | 0.0893
GEN-2020-068 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 18.1018 | 18.2313 | 0.1295
GEN-2020-068 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 12.1874 | 12.2426 | 0.0552
GEN-2020-068 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 20.1996 | 20.2673 | 0.0677
GEN-2020-068 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 11.0384 | 11.0781 | 0.0397
GEN-2020-068 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 17.1146 | 17.1756 | 0.061
GEN-2020-068 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 12.6089 | 12.6728 | 0.0639
GEN-2020-068 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 9.5989 | 9.6356 | 0.0367
GEN-2020-068 | 05 SOUTHWEST | 528325 | LE-WAITS 3 | 115 | 9.6202 | 9.6522 | 0.032
GEN-2020-068 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 9.7161 | 9.7535 | 0.0374
GEN-2020-068 | 05 SOUTHWEST | 528626 | LE-PLNSINT 2 | 69 | 3.8859 | 3.9023 | 0.0164
GEN-2020-068 | 05 SOUTHWEST | 560071 | G16-003-TAP | 345 | 15.0153 | 15.0226 | 0.0073
GEN-2020-068 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 9.8463 | 9.8566 | 0.0103
GEN-2020-068 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 14.2684 | 14.3258 | 0.0574
GEN-2020-068 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.94 | 4.9509 | 0.0109
GEN-2020-068 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 10.4062 | 10.4252 | 0.019
GEN-2020-068 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.2163 | 8.2298 | 0.0135
GEN-2020-068 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 15.0406 | 15.1537 | 0.1131
GEN-2020-068 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.3404 | 14.3712 | 0.0308
GEN-2020-068 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 9.57 | 9.6827 | 0.1127
GEN-2020-068 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 7.0815 | 7.1498 | 0.0683
GEN-2020-068 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 6.1411 | 6.1692 | 0.0281
GEN-2020-068 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 6.1517 | 6.1798 | 0.0281
GEN-2020-068 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.5341 | 11.5648 | 0.0307
GEN-2020-068 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 9.3589 | 9.3755 | 0.0166
GEN-2020-068 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 10.8972 | 11.2734 | 0.3762
GEN-2020-068 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 17.4895 | 17.498 | 0.0085
GEN-2020-068 | 05 SOUTHWEST | 764825 | GEN-2020-017 | 230 | 5.9856 | 5.9986 | 0.013
GEN-2020-068 | 05 SOUTHWEST | 764840 | GEN-2020-059 | 345 | 11.0737 | 11.2843 | 0.2106
GEN-2020-068 | 05 SOUTHWEST | 764866 | G20-059-TAP | 345 | 11.1419 | 11.3548 | 0.2129
GEN-2020-068 | 05 SOUTHWEST | 764875 | GEN-2020-060 | 230 | 12.4089 | 12.4558 | 0.0469
GEN-2020-068 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 7.341 | 7.9682 | 0.6272
GEN-2020-068 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 8.8128 | 9.7221 | 0.9093
GEN-2020-068 | 05 SOUTHWEST | 764948 | G20-068-SS1 | 345 | 7.0836 | 7.8532 | 0.7696
GEN-2020-068 | 05 SOUTHWEST | 764949 | G20-068-SS2 | 345 | 7.0836 | 7.8507 | 0.7671
GEN-2020-068 | 05 SOUTHWEST | 764950 | GEN-2020-068 | 345 | 8.7669 | 9.6765 | 0.9096
GEN-2020-068 | 05 SOUTHWEST | 766291 | G20-009-TAP | 345 | 9.6335 | 9.6466 | 0.0131

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | Critical_Clearing_Time | Stability_Margin | Pg_out | Pg_rated | SCR PASS/FAIL | CCT PASS/FAIL
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | Base | 8.7454 | 1.465 | 1365.0135 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | Base | 8.7454 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | Base | 9.6295 | 16.0209 | 15920.8538 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | Base | 9.6295 | 6.1572 | 6057.24 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | Base | 33.1676 | 35.7818 | 35681.7541 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 8.7448 | 1.465 | 1365.0149 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 8.7448 | 1.4963 | 1396.2653 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 9.2847 | 16.6794 | 16579.4134 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 9.2847 | 6.1961 | 6096.1336 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 33.0937 | 35.7979 | 35697.9327 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 8.7433 | 1.465 | 1365.0199 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 8.7433 | 1.4963 | 1396.27 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 9.5629 | 16.2603 | 16160.2611 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 9.5629 | 6.1676 | 6067.6254 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 30.7031 | 36.24 | 36139.9935 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 8.7449 | 1.465 | 1365.0177 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 8.7449 | 1.4963 | 1396.2663 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 9.546 | 16.2057 | 16105.6527 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 9.546 | 6.157 | 6057.0215 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 32.9614 | 35.8312 | 35731.1679 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 8.7443 | 1.465 | 1365.012 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 8.7443 | 1.4963 | 1396.2653 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 9.6296 | 16.0035 | 15903.4628 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 9.6296 | 6.157 | 6057.0172 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 33.1616 | 35.7787 | 35678.6533 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 8.7445 | 1.465 | 1365.0142 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 8.7445 | 1.4963 | 1396.2651 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 9.5542 | 16.1835 | 16083.4714 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 9.5542 | 6.1588 | 6058.7781 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 32.9707 | 35.834 | 35733.9571 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 8.7448 | 1.465 | 1365.0171 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 8.7448 | 1.4963 | 1396.2647 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 9.5625 | 16.1322 | 16032.2347 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 9.5625 | 6.1568 | 6056.8268 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 32.8703 | 35.8416 | 35741.5652 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7396 | 1.465 | 1365.0215 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7396 | 1.4963 | 1396.2833 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6209 | 16.0523 | 15952.2651 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6209 | 6.152 | 6051.9847 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 31.1361 | 36.2572 | 36157.1803 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 8.7446 | 1.465 | 1365.0115 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 8.7446 | 1.4963 | 1396.2655 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 9.6211 | 15.7202 | 15620.2086 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 9.6211 | 6.1577 | 6057.743 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 33.1623 | 35.7798 | 35679.8265 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 8.7044 | 1.4653 | 1365.344 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 8.7044 | 1.4965 | 1396.5297 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 9.6266 | 16.0338 | 15933.7902 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 9.6266 | 6.1573 | 6057.289 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 32.8795 | 35.8574 | 35757.421 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 8.7044 | 1.4653 | 1365.3442 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 8.7044 | 1.4965 | 1396.5298 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 9.6266 | 16.0338 | 15933.761 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 9.6266 | 6.1573 | 6057.288 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 32.8795 | 35.8573 | 35757.2781 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7322 | 1.4651 | 1365.091 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7322 | 1.4963 | 1396.3473 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.5973 | 16.1453 | 16045.3246 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.5973 | 6.1597 | 6059.6789 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 31.428 | 36.1677 | 36067.6791 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7263 | 1.4651 | 1365.1452 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7263 | 1.4964 | 1396.3961 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.5856 | 16.2307 | 16130.6629 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.5856 | 6.1598 | 6059.7631 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 29.3831 | 36.8921 | 36792.0877 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 4.5244 | 1.5284 | 1428.4403 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 4.5244 | 1.5471 | 1447.1298 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 9.6267 | 16.0337 | 15933.6879 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 9.6267 | 6.1577 | 6057.6579 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 33.0355 | 35.8171 | 35717.0867 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 3.9808 | 1.5558 | 1455.8443 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 3.9808 | 1.5687 | 1468.7398 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 9.6259 | 16.0309 | 15930.8724 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 9.6259 | 6.1574 | 6057.3738 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 32.9781 | 35.8002 | 35700.2414 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.7451 | 1.465 | 1365.0148 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.7451 | 1.4963 | 1396.2647 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.7696 | 18.0927 | 17992.7331 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.7696 | 6.2141 | 6114.1198 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 33.0771 | 35.8132 | 35713.2256 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 8.7451 | 1.465 | 1365.0158 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 8.7451 | 1.4963 | 1396.2641 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 6.5692 | 6.1576 | 6057.5709 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 6.5692 | 7.1098 | 7009.781 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 32.9926 | 35.834 | 35733.9727 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 8.7433 | 1.465 | 1365.0296 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 8.7433 | 1.4963 | 1396.2766 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 9.3574 | 18.2539 | 18153.929 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 9.3574 | 6.2138 | 6113.794 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 32.7169 | 35.8176 | 35717.6329 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7428 | 1.465 | 1365.0197 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7428 | 1.4963 | 1396.273 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.6173 | 16.0233 | 15923.287 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.6173 | 6.1572 | 6057.1964 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 33.1601 | 35.7822 | 35682.1574 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 8.7454 | 1.465 | 1365.0141 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 8.7454 | 1.4963 | 1396.2647 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 9.6293 | 16.0209 | 15920.9171 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 9.6293 | 6.1572 | 6057.1933 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 33.1648 | 35.7816 | 35681.6196 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 8.7451 | 1.465 | 1365.0181 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 8.7451 | 1.4963 | 1396.2676 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 9.6281 | 16.021 | 15920.9565 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 9.6281 | 6.1568 | 6056.7718 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 33.1452 | 35.78 | 35680.038 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 8.7473 | 1.465 | 1365.0134 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 8.7473 | 1.4963 | 1396.2663 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 9.6444 | 16.2012 | 16101.1971 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 9.6444 | 6.1819 | 6081.9018 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 30.4614 | 36.3739 | 36273.9446 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 8.7433 | 1.465 | 1365.0199 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 8.7433 | 1.4963 | 1396.2699 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 9.5631 | 16.2618 | 16161.8403 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 9.5631 | 6.1679 | 6067.8551 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 30.703 | 36.2402 | 36140.2358 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 8.7418 | 1.4651 | 1365.0581 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 8.7418 | 1.4963 | 1396.3023 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 9.6163 | 16.0317 | 15931.7013 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 9.6163 | 6.1503 | 6050.3449 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 28.7943 | 37.0578 | 36957.7838 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 8.7448 | 1.465 | 1365.01 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 8.7448 | 1.4963 | 1396.2639 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 9.6284 | 16.0116 | 15911.5803 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 9.6284 | 6.1559 | 6055.8539 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 33.1896 | 35.7407 | 35640.6651 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 8.7448 | 1.465 | 1365.01 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 8.7448 | 1.4963 | 1396.2639 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 9.6284 | 16.0116 | 15911.5803 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 9.6284 | 6.1559 | 6055.8539 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 33.1896 | 35.7407 | 35640.6651 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.7448 | 1.465 | 1365.0172 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.7448 | 1.4963 | 1396.267 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6272 | 16.0212 | 15921.2336 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6272 | 6.1573 | 6057.2892 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 32.8642 | 35.7579 | 35657.8789 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 8.7448 | 1.465 | 1365.0171 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 8.7448 | 1.4963 | 1396.2671 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 9.6272 | 16.0213 | 15921.2562 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 9.6272 | 6.1573 | 6057.2905 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 32.8619 | 35.7578 | 35657.823 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 8.7457 | 1.465 | 1365.0162 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 8.7457 | 1.4963 | 1396.264 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 9.6063 | 16.1629 | 16062.9042 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 9.6063 | 6.1773 | 6077.3202 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 33.1525 | 35.8166 | 35716.5513 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 8.7455 | 1.465 | 1365.015 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 8.7455 | 1.4963 | 1396.2644 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 9.5745 | 16.189 | 16089.0471 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 9.5745 | 6.1658 | 6065.82 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 33.1405 | 35.8116 | 35711.6316 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 8.7452 | 1.465 | 1365.0133 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 8.7452 | 1.4963 | 1396.264 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 9.605 | 15.9328 | 15832.782 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 9.605 | 6.1555 | 6055.4907 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 33.1624 | 35.7768 | 35676.792 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 8.7449 | 1.465 | 1365.0178 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 8.7449 | 1.4963 | 1396.2664 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 9.5476 | 16.1949 | 16094.903 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 9.5476 | 6.1568 | 6056.7839 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 32.9625 | 35.831 | 35731.0478 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.7449 | 1.465 | 1365.0122 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.7449 | 1.4963 | 139626% | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.5964 | 16.0382 | 15938.1935 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.5964 | 6.157 | 605703% | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 33.0891 | 35.7621 | 35662.0941 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 8.7463 | 1.465 | 1365.0157 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 8.7463 | 1.4963 | 1396.2621 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 9.6057 | 15.8779 | 15777.9298 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 9.6057 | 6.1371 | 6037.0946 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 32.6811 | 35.905 | 35804.9905 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 8.7449 | 1.465 | 1365.0133 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 8.7449 | 1.4963 | 1396.2644 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 9.6137 | 16.0542 | 15954.1973 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 9.6137 | 6.1572 | 6057.2128 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 32.9141 | 35.8225 | 35722.5187 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7453 | 1.465 | 1365.0137 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7453 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.0646 | 5.7953 | 5695.336 | 54.6 | 86.4 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.0646 | 7.2852 | 7185.1591 | 19.9 | 31.5 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 33.0945 | 35.8003 | 35700.2777 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 8.7423 | 1.465 | 1364.993 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 8.7423 | 1.4963 | 1396.2641 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 9.6139 | 16.0418 | 15941.7726 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 9.6139 | 6.1534 | 6053.4376 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 32.4519 | 35.8561 | 35756.0957 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 8.7455 | 1.465 | 1365.0204 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 8.7455 | 1.4963 | 1396.267 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 9.6297 | 16.0279 | 15927.9184 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 9.6297 | 6.1582 | 6058.2118 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 33.0974 | 35.8189 | 35718.8662 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 8.7451 | 1.465 | 1365.0199 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 8.7451 | 1.4963 | 1396.2686 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 9.6295 | 16.0234 | 15923.4402 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 9.6295 | 6.1574 | 6057.4252 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 33.0592 | 35.8184 | 35718.403 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7445 | 1.465 | 1365.0122 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7445 | 1.4963 | 1396.265 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6534 | 14.9693 | 14869.3122 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6534 | 6.11 | 6009.9917 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 33.1653 | 35.7786 | 35678.6098 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7443 | 1.465 | 1365.012 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7443 | 1.4963 | 1396.2651 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.625 | 15.2187 | 15118.673 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.625 | 6.1305 | 6030.451 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 33.162 | 35.7792 | 35679.2028 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 8.7445 | 1.465 | 1365.0133 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 8.7445 | 1.4963 | 1396.2645 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 9.5528 | 16.2132 | 16113.2072 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 9.5528 | 6.1579 | 6057.8523 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 32.9756 | 35.8363 | 35736.3262 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 8.745 | 1.465 | 1365.0129 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 8.745 | 1.4963 | 1396.2647 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 9.6296 | 16.0159 | 15915.8783 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 9.6296 | 6.1573 | 6057.3336 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 33.1652 | 35.7809 | 35680.8511 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 8.7343 | 1.4654 | 1365.3593 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 8.7343 | 1.4964 | 1396.4176 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 9.6138 | 16.09 | 15990.0335 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 9.6138 | 6.1594 | 6059.4113 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 32.2847 | 36.0217 | 35921.7476 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 8.7344 | 1.4654 | 1365.3567 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 8.7344 | 1.4964 | 1396.4154 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 9.6139 | 16.0906 | 15990.6352 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 9.6139 | 6.1594 | 6059.4301 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 32.2869 | 36.0238 | 35923.8316 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7454 | 1.465 | 1365.0135 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7454 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6295 | 16.0209 | 15920.8535 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6295 | 6.1572 | 6057.2387 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 33.1676 | 35.7817 | 35681.7264 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 8.7454 | 1.465 | 1365.0135 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 8.7454 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 9.6295 | 16.0209 | 15920.8535 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 9.6295 | 6.1572 | 6057.2387 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 33.1676 | 35.7817 | 35681.7264 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 8.7398 | 1.465 | 1365.0126 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 8.7398 | 1.4963 | 1396.2766 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 9.6287 | 16.0187 | 15918.7015 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 9.6287 | 6.1572 | 6057.158 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 33.1551 | 35.7737 | 35673.6566 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 8.7241 | 1.4649 | 1364.9387 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 8.7241 | 1.4963 | 1396.2808 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 9.6257 | 16.0372 | 15937.2237 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 9.6257 | 6.1576 | 6057.6012 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 32.9315 | 35.8336 | 35733.5665 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 8.7573 | 1.4651 | 1365.1074 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 8.7573 | 1.4963 | 1396.3136 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 9.6294 | 16.0258 | 15925.7828 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 9.6294 | 6.1573 | 6057.3236 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 33.1745 | 35.7982 | 35698.2126 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 8.7064 | 1.4653 | 1365.2846 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 8.7064 | 1.4965 | 1396.526 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 9.5967 | 16.1024 | 16002.4205 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 9.5967 | 6.1563 | 6056.2547 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 32.7944 | 35.8524 | 35752.4479 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 8.6981 | 1.4655 | 1365.48 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 8.6981 | 1.4966 | 1396.5625 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 9.6211 | 16.0501 | 15950.1257 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 9.6211 | 6.158 | 6058.0098 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 32.7958 | 35.8716 | 35771.6027 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 8.7038 | 1.4651 | 1365.1285 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 8.7038 | 1.4964 | 1396.4198 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 9.6264 | 16.0358 | 15935.8223 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 9.6264 | 6.158 | 6057.9516 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 32.9949 | 35.8168 | 35716.7858 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 8.7569 | 1.4651 | 1365.0935 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 8.7569 | 1.4963 | 1396.302 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 9.6295 | 16.0253 | 15925.2592 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 9.6295 | 6.1574 | 6057.4278 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 33.1757 | 35.7958 | 35695.8253 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 8.7119 | 1.4653 | 1365.2985 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 8.7119 | 1.4965 | 1396.4884 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 9.6279 | 16.0287 | 15928.6887 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 9.6279 | 6.1577 | 6057.6784 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 33.0498 | 35.8067 | 35706.6755 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 8.7169 | 1.4652 | 1365.2028 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 8.7169 | 1.4964 | 1396.4194 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 9.6282 | 16.0271 | 15927.1438 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 9.6282 | 6.1574 | 6057.4339 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 33.0757 | 35.8039 | 35703.9189 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 3.7541 | 1.5213 | 1421.2769 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 3.7541 | 1.5424 | 1442.4253 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 9.6241 | 16.025 | 15924.9543 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 9.6241 | 6.1562 | 6056.1714 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 32.9018 | 35.7757 | 35675.7004 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 8.7635 | 1.4666 | 1366.6325 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 8.7635 | 1.4975 | 1397.5487 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 9.6294 | 16.0211 | 15921.1163 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 9.6294 | 6.1572 | 6057.2277 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 33.1705 | 35.7835 | 35683.4888 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7453 | 1.465 | 1365.0137 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.7453 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 4.8261 | 4.8373 | 4737.2841 | 54.6 | 86.4 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 4.8261 | 7.9501 | 7850.091 | 19.9 | 31.5 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 33.1138 | 35.7892 | 35689.2005 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 8.7444 | 1.465 | 1365.0193 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 8.7444 | 1.4963 | 1396.2685 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 9.615 | 16.0294 | 15929.4181 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 9.615 | 6.1578 | 6057.8413 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 32.8143 | 35.8275 | 35727.518 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 8.745 | 1.465 | 1365.013 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 8.745 | 1.4963 | 1396.2648 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 9.6293 | 16.0179 | 15917.9079 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 9.6293 | 6.157 | 6057.0209 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 33.1659 | 35.778 | 35677.9683 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.7448 | 1.465 | 1365.0206 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.7448 | 1.4963 | 1396.2691 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.836 | 22.3626 | 22262.5813 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.836 | 6.2817 | 6181.6872 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 33.079 | 35.7986 | 35698.589 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 8.7441 | 1.465 | 1365.0117 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 8.7441 | 1.4963 | 1396.2658 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 9.6288 | 16.0116 | 15911.62 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 9.6288 | 6.1565 | 6056.5225 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 33.1626 | 35.7697 | 35669.657 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7442 | 1.465 | 1365.0274 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7442 | 1.4963 | 1396.2754 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6246 | 16.0103 | 15910.3377 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6246 | 6.1541 | 6054.1486 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 27.0674 | 36.673 | 36573.0178 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.7451 | 1.465 | 1365.0152 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.7451 | 1.4963 | 1396.265 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.7709 | 18.251 | 18150.965 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.7709 | 6.2168 | 6116.8345 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 33.0768 | 35.813 | 35712.9515 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 8.7454 | 1.465 | 1365.0134 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 8.7454 | 1.4963 | 1396.2641 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 9.6292 | 16.0271 | 15927.0557 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 9.6292 | 6.1574 | 6057.355 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 33.1645 | 35.784 | 35683.9596 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 8.7541 | 1.465 | 1365.0355 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 8.7541 | 1.4963 | 1396.2578 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 9.56 | 16.1964 | 16096.3786 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 9.56 | 6.1626 | 6062.5836 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 32.8374 | 35.8618 | 35761.7863 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.7463 | 1.465 | 1365.0396 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.7463 | 1.4963 | 1396.282 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.62 | 16.0126 | 15912.5791 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.62 | 6.1525 | 6052.5122 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 33.026 | 35.7794 | 35679.3531 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7419 | 1.465 | 1364.9999 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7419 | 1.4963 | 1396.2634 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.5561 | 16.1386 | 16038.5514 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.5561 | 6.1582 | 6058.2433 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 23.7378 | 38.4426 | 38342.6024 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 8.7324 | 1.465 | 1365.004 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 8.7324 | 1.4963 | 1396.2946 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 9.6294 | 16.0042 | 15904.2139 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 9.6294 | 6.1582 | 6058.226 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 33.0861 | 35.6925 | 35592.5257 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7426 | 1.465 | 1365.0113 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.7426 | 1.4963 | 1396.2667 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6212 | 16.019 | 15919.0075 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6212 | 6.1576 | 6057.6322 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 28.2329 | 35.8396 | 35739.5816 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 8.7327 | 1.465 | 1365.0023 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 8.7327 | 1.4963 | 1396.2918 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 9.6318 | 16.0146 | 15914.6408 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 9.6318 | 6.1608 | 6060.8256 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 33.0255 | 35.6318 | 35531.7614 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 8.73 | 1.465 | 1364.9979 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 8.73 | 1.4963 | 1396.2968 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 9.6315 | 16.007 | 15906.9527 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 9.6315 | 6.1604 | 6060.4372 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 33.0114 | 35.5834 | 35483.3768 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 8.743 | 1.465 | 1365.0122 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 8.743 | 1.4963 | 1396.2681 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 9.6296 | 16.0192 | 15919.1788 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 9.6296 | 6.1576 | 6057.5865 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 33.1468 | 35.7609 | 35660.8772 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 8.7373 | 1.465 | 1365.0082 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 8.7373 | 1.4963 | 1396.2824 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 9.631 | 16.0197 | 15919.7176 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 9.631 | 6.16 | 6059.9937 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 33.0627 | 35.7014 | 3560144% | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 8.7433 | 1.465 | 1365.0124 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 8.7433 | 1.4963 | 139627% | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 9.6295 | 16.0192 | 15919.1506 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 9.6295 | 6.1575 | 6057.5018 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 33.1502 | 35.7626 | 35662.5652 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 8.739 | 1.465 | 1365.0034 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 8.739 | 1.4963 | 1396.2756 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 9.6297 | 16.0109 | 15910.865 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 9.6297 | 6.158 | 6058.0012 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 33.0843 | 35.641 | 35540.9632 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 8.7345 | 1.465 | 1364.9968 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 8.7345 | 1.4963 | 1396.2837 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 9.6302 | 16.0078 | 15907.7683 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 9.6302 | 6.1591 | 6059.0586 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 33.0064 | 35.5647 | 35464.6788 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 8.7416 | 1.465 | 1365.0069 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 8.7416 | 1.4963 | 1396.271 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 9.6295 | 16.0122 | 15912.1939 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 9.6295 | 6.1573 | 6057.3261 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 33.1308 | 35.6828 | 35582.7871 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.744 | 1.465 | 1365.0127 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.744 | 1.4963 | 1396.2644 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.6243 | 16.0398 | 15939.8215 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.6243 | 6.1571 | 6057.1431 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 32.5992 | 35.9259 | 35825.9403 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 8.7442 | 1.465 | 1365.0129 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 8.7442 | 1.4963 | 1396.2643 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 9.625 | 16.037 | 15937.041 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 9.625 | 6.1571 | 6057.1447 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 32.6804 | 35.9051 | 35805.0742 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.7448 | 1.465 | 1365.0172 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.7448 | 1.4963 | 1396.267 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6272 | 16.0212 | 15921.2358 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6272 | 6.1573 | 6057.2896 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 32.8643 | 35.7579 | 35657.8945 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 8.7448 | 1.465 | 1365.0171 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 8.7448 | 1.4963 | 1396.2671 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 9.6272 | 16.0213 | 15921.2579 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 9.6272 | 6.1573 | 6057.2908 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 32.862 | 35.7578 | 35657.834 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.6414 | 1.5216 | 1421.5618 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.6414 | 1.5421 | 1442.1433 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6266 | 16.0308 | 15930.7927 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6266 | 6.1572 | 6057.1922 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 33.0381 | 35.8098 | 35709.8181 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 3.945 | 1.5591 | 1459.1175 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 3.945 | 1.5712 | 1471.1652 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6259 | 16.0314 | 15931.3725 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6259 | 6.1574 | 6057.4418 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 32.9748 | 35.8015 | 35701.517 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 8.7431 | 1.465 | 1365.0212 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 8.7431 | 1.4963 | 1396.2701 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 9.5943 | 16.1249 | 16024.8552 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 9.5943 | 6.1546 | 6054.5573 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 31.6286 | 36.0735 | 35973.463 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 8.7478 | 1.465 | 1365.0421 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 8.7478 | 1.4963 | 1396.2755 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 9.6372 | 16.5109 | 16410.9318 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 9.6372 | 6.2203 | 6120.2991 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 32.6156 | 36.0129 | 35912.9404 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7455 | 1.465 | 1365.0137 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7455 | 1.4963 | 1396.2642 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7045 | 19.4005 | 19300.4581 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7045 | 6.238 | 6138.0158 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 33.1612 | 35.7836 | 35683.6245 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.7517 | 1.465 | 1365.0279 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.7517 | 1.4963 | 1396.2609 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.5428 | 48.2135 | 48113.4613 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.5428 | 6.4815 | 6381.4887 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 32.974 | 35.8318 | 35731.8211 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 8.7499 | 1.465 | 1365.0188 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 8.7499 | 1.4963 | 1396.2628 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 9.3253 | 18.3815 | 18281.5398 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 9.3253 | 6.2223 | 6122.345 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 33.1191 | 35.7936 | 35693.6379 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7291 | 1.465 | 1365.025 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7291 | 1.4963 | 1396.3191 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6292 | 16.0165 | 15916.452 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6292 | 6.1576 | 6057.6181 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 33.1244 | 35.7619 | 35661.9368 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.751 | 1.465 | 1365.0351 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.751 | 1.4963 | 1396.2623 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.5974 | 16.1546 | 16054.6112 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.5974 | 6.1581 | 6058.1342 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25SP | GEN-2020-091 | Patent Gate Substation 345 kV | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 29.3798 | 36.7726 | 36672.6076 | 150 | 167.2 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | Base | 8.8054 | 1.4649 | 1364.9483 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | Base | 8.8054 | 1.4961 | 1396.0849 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | Base | 9.6373 | 16.9559 | 16855.9321 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | Base | 9.6373 | 6.1875 | 6087.4827 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 8.8048 | 1.4649 | 1364.949 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 8.8048 | 1.4961 | 1396.0855 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 9.2974 | 17.7937 | 17693.7455 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652421 [WILISTN7 115.00] CKT Z1 | 9.2974 | 6.2361 | 6136.1139 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 8.8042 | 1.465 | 1364.9577 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 8.8042 | 1.4961 | 1396.0903 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 9.5756 | 17.3442 | 17244.2045 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659334 [JUDSON__-BE4230.00] CKT 1 | 9.5756 | 6.2049 | 6104.8995 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 8.805 | 1.465 | 1364.9521 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 8.805 | 1.4961 | 1396.0866 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 9.5534 | 17.172 | 17071.9924 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652421 [WILISTN7 115.00] TO BUS 652621 [WILISTN9 13.200] CKT 1 | 9.5534 | 6.187 | 6086.9583 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 8.8047 | 1.4649 | 1364.948 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 8.8047 | 1.4961 | 1396.0856 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 9.6377 | 16.9289 | 16828.8672 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655793 [MARLEY -LY7115.00] CKT 1 | 9.6377 | 6.1874 | 6087.3683 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 8.8046 | 1.4649 | 1364.9483 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 8.8046 | 1.4961 | 1396.085 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 9.5624 | 17.1725 | 17072.4583 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 655925 [JUDSON -MW7115.00] CKT 1 | 9.5624 | 6.1901 | 6090.0675 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 8.8047 | 1.4649 | 1364.9489 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 8.8047 | 1.4961 | 1396.0851 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 9.5718 | 17.1206 | 17020.6462 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 659262 [CULBSN.E-BE7115.00] CKT 1 | 9.5718 | 6.1877 | 6087.7005 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7987 | 1.465 | 1364.9525 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7987 | 1.4961 | 1396.1053 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6266 | 16.9611 | 16861.1059 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6266 | 6.1793 | 6079.3136 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 8.8046 | 1.4649 | 1364.9477 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 8.8046 | 1.4961 | 1396.0856 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 9.6325 | 16.5199 | 16419.9242 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655790 [HELMUT -LY7115.00] TO BUS 659151 [RICHLAND-BE7115.00] CKT 1 | 9.6325 | 6.1884 | 6088.4174 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 8.7627 | 1.4653 | 1365.2795 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 8.7627 | 1.4964 | 1396.3549 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 9.6339 | 16.9714 | 16871.4276 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 1 | 9.6339 | 6.1871 | 6087.1155 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 8.7627 | 1.4653 | 1365.2798 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 8.7627 | 1.4964 | 1396.3552 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 9.6339 | 16.9714 | 16871.4007 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659105 [LELAND_O-BE3345.00] CKT 2 | 9.6339 | 6.1871 | 6087.1157 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7928 | 1.465 | 1365.0362 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 8.7928 | 1.4962 | 1396.1726 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6054 | 17.1327 | 17032.71 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659183 [CHARL_CK-BE3345.00] CKT 1 | 9.6054 | 6.1896 | 6089.5962 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7875 | 1.4651 | 1365.0974 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.7875 | 1.4962 | 1396.2243 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.5938 | 17.2379 | 17137.8975 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.5938 | 6.1882 | 6088.2345 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 4.5452 | 1.5282 | 1428.2481 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 4.5452 | 1.5469 | 1446.9492 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 9.6347 | 16.9731 | 16873.1205 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659424 [LO.LS-FT-BE3345.00] CKT Z | 9.6347 | 6.1878 | 6087.7956 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 3.9821 | 1.5555 | 1455.5176 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 3.9821 | 1.5685 | 1468.4898 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 9.6338 | 16.9677 | 16867.6518 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659428 [CC.LS-LO-BE3345.00] CKT Z | 9.6338 | 6.1874 | 6087.4088 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.8038 | 1.4649 | 1364.9481 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.8038 | 1.4961 | 1396.0853 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.782 | 19.3992 | 19299.2334 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 659186 [E.SIDNEY-LY7115.00] CKT 1 | 8.782 | 6.2538 | 6153.8433 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 8.8049 | 1.4649 | 1364.9485 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 8.8049 | 1.4961 | 1396.0846 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 6.5862 | 5.9302 | 5830.1711 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 661056 [LEWIS 7 115.00] CKT 1 | 6.5862 | 7.1835 | 7083.5455 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 8.8034 | 1.465 | 1364.9641 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 8.8034 | 1.4961 | 1396.0967 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 9.3664 | 19.7759 | 19675.8521 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659211 [CCR.KV2A-BE913.800] CKT 1 | 9.3664 | 6.2483 | 6148.2953 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.802 | 1.465 | 1364.9522 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 8.802 | 1.4961 | 1396.0942 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.6291 | 16.9899 | 16889.895 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659384 [ROUNDUP_-BE3345.00] CKT 1 | 9.6291 | 6.1914 | 6091.3926 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 8.8054 | 1.4649 | 1364.9489 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 8.8054 | 1.4961 | 1396.0854 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 9.6372 | 16.9563 | 16856.2589 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659318 [CCR.KV3A-BE913.800] CKT 1 | 9.6372 | 6.1875 | 6087.4527 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 8.805 | 1.465 | 1364.9527 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 8.805 | 1.4961 | 1396.0885 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 9.6359 | 16.9571 | 16857.1396 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659302 [CHARL_CK-BE4230.00] TO BUS 659319 [CCR.KV4A-BE913.800] CKT 2 | 9.6359 | 6.187 | 6086.9714 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 8.8054 | 1.465 | 1364.9507 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 8.8054 | 1.4961 | 1396.0851 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 9.6544 | 17.1744 | 17074.4349 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659600 [EFORK_-BE334345.00] CKT 1 | 9.6544 | 6.214 | 6114.0419 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 8.8042 | 1.465 | 1364.9577 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 8.8042 | 1.4961 | 1396.0904 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 9.5758 | 17.346 | 17245.9992 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659334 [JUDSON__-BE4230.00] TO BUS 659335 [JDS.KU6A-BE913.800] CKT 1 | 9.5758 | 6.2051 | 6105.1278 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 8.8012 | 1.465 | 1364.9966 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 8.8012 | 1.4961 | 1396.1266 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 9.6218 | 16.9566 | 16856.6083 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659387 [KUMMERDG-BE3345.00] CKT 1 | 9.6218 | 6.1771 | 6077.1346 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 8.8046 | 1.4649 | 1364.9438 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 8.8046 | 1.4961 | 1396.0847 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 9.6344 | 16.937 | 16837.0267 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659389 [KR.KU4A_-BE913.800] CKT 1 | 9.6344 | 6.1847 | 6084.7191 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 8.8046 | 1.4649 | 1364.9438 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 8.8046 | 1.4961 | 1396.0847 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 9.6344 | 16.937 | 16837.0267 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659388 [KUMMERDG-MK7115.00] TO BUS 659394 [KR.KU6A_-BE913.800] CKT 2 | 9.6344 | 6.1847 | 6084.7191 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.8048 | 1.465 | 1364.9516 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.8048 | 1.4961 | 1396.0876 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6349 | 16.958 | 16857.9531 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.6349 | 6.1876 | 6087.5626 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 8.8048 | 1.465 | 1364.9518 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 8.8048 | 1.4961 | 1396.0876 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 9.6349 | 16.958 | 16857.9842 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 1 | 9.6349 | 6.1876 | 6087.5645 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 8.8056 | 1.465 | 1364.95 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 8.8056 | 1.4961 | 1396.0846 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 9.6186 | 17.1321 | 17032.0938 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655935 [NW.WLSTN-MW7115.00] CKT 1 | 9.6186 | 6.2122 | 6112.1981 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 8.8055 | 1.4649 | 1364.9495 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 8.8055 | 1.4961 | 1396.0849 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 9.5857 | 17.1854 | 17085.435 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 655940 [MONT -MW7115.00] CKT 1 | 9.5857 | 6.2 | 6099.9603 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 8.8049 | 1.4649 | 1364.9475 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 8.8049 | 1.4961 | 1396.0846 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 9.6126 | 16.8585 | 16758.5424 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 661089 [LTLMUDY7 115.00] CKT 1 | 9.6126 | 6.1862 | 6086.2084 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 8.805 | 1.465 | 1364.952 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 8.805 | 1.4961 | 1396.0866 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 9.5551 | 17.1598 | 17059.7514 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652391 [WILLISTON27 115.00] TO BUS 652400 [WILISTN4 230.00] TO BUS 652622 [WILISTN29 13.200] CKT 1 | 9.5551 | 6.1868 | 608678% | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.8052 | 1.4649 | 1364.9475 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.8052 | 1.4961 | 139609% | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.6036 | 16.9942 | 16894.1921 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.6036 | 6.1867 | 6086.7083 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 8.8043 | 1.4649 | 1364.9484 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 8.8043 | 1.4961 | 1396.0874 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 9.6223 | 16.8761 | 16776.1407 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 652403 [DAWSONC4 230.00] CKT 1 | 9.6223 | 6.1764 | 6076.3555 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 8.805 | 1.4649 | 1364.948 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 8.805 | 1.4961 | 1396.0852 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 9.6213 | 17.0132 | 16913.1533 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652400 [WILISTN4 230.00] TO BUS 659362 [WHEELOCK-BE4230.00] CKT 1 | 9.6213 | 6.1883 | 6088.3163 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.805 | 1.4649 | 1364.9475 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.805 | 1.4961 | 1396.0848 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.061 | 5.6261 | 5526.0733 | 54.6 | 86.4 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652421 [WILISTN7 115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 5.061 | 7.3656 | 7265.571 | 19.9 | 31.5 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 8.8044 | 1.4649 | 1364.9325 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 8.8044 | 1.4961 | 1396.0821 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 9.6205 | 16.9922 | 16892.1618 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 800121 [MAURINE 2 345.00] CKT 1 | 9.6205 | 6.183 | 6082.9953 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 8.8053 | 1.465 | 1364.9543 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 8.8053 | 1.4961 | 1396.0879 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 9.6401 | 16.974 | 16874.0348 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652221 [BELFELD9 13.800] CKT 1 | 9.6401 | 6.1905 | 6090.4629 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 8.805 | 1.465 | 1364.9545 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 8.805 | 1.4961 | 1396.0896 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 9.6379 | 16.9598 | 16859.8435 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 652424 [BELFELD3 345.00] TO BUS 652425 [BELFELD4 230.00] TO BUS 652220 [BELFELD29 13.800] CKT 1 | 9.6379 | 6.188 | 6088.0179 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8052 | 1.4649 | 1364.9479 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8052 | 1.4961 | 1396.0853 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6592 | 15.7492 | 15649.2175 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655791 [SPRINGLK-LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6592 | 6.1384 | 6038.4384 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8047 | 1.4649 | 1364.9478 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8047 | 1.4961 | 1396.0854 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6306 | 15.8803 | 15780.2885 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655792 [NOHLEY -LY7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 9.6306 | 6.1553 | 6055.3317 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 8.8047 | 1.4649 | 1364.947 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 8.8047 | 1.4961 | 1396.0844 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 9.5607 | 17.2227 | 17122.711 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655924 [STATELIN-MW7115.00] CKT 1 | 9.5607 | 6.1886 | 6088.6333 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 8.8051 | 1.4649 | 1364.9482 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 8.8051 | 1.4961 | 1396.0853 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 9.6379 | 16.9501 | 16850.0786 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 655925 [JUDSON -MW7115.00] TO BUS 655926 [SW.WLSTN-MW7115.00] CKT 1 | 9.6379 | 6.188 | 6087.9629 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 8.7653 | 1.4652 | 1365.2042 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 8.7653 | 1.4963 | 1396.2551 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 9.6226 | 17.0517 | 16951.6669 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659103 [ANTELP_1-BEG23.000] CKT 1 | 9.6226 | 6.1896 | 6089.6045 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 8.7654 | 1.4652 | 1365.2015 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 8.7654 | 1.4963 | 1396.2528 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 9.6227 | 17.0523 | 16952.2801 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659107 [ANTELP_2-BEG23.000] CKT 1 | 9.6227 | 6.1896 | 6089.6214 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.8054 | 1.4649 | 1364.9482 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.8054 | 1.4961 | 1396.0848 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6373 | 16.9559 | 16855.9139 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6373 | 6.1875 | 6087.4784 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 8.8054 | 1.4649 | 1364.9482 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 8.8054 | 1.4961 | 1396.0848 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 9.6373 | 16.9559 | 16855.9139 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 2 | 9.6373 | 6.1875 | 6087.4784 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 8.8026 | 1.465 | 1364.9522 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 8.8026 | 1.4961 | 1396.0975 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 9.6367 | 16.9508 | 16850.7864 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659218 [COTEAU__-RR3345.00] CKT Z | 9.6367 | 6.187 | 6087.0338 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 8.8003 | 1.4649 | 1364.942 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 8.8003 | 1.4961 | 1396.0902 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 9.6329 | 16.9753 | 16875.2718 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659420 [AV.LS-BD-BE3345.00] CKT Z | 9.6329 | 6.1872 | 6087.2372 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 8.8087 | 1.465 | 1365.0245 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 8.8087 | 1.4961 | 1396.1379 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 9.6371 | 16.9626 | 16862.6398 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 588210 [GEN-2016-130345.00] CKT 1 | 9.6371 | 6.1875 | 6087.4784 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 8.7656 | 1.4652 | 1365.2404 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 8.7656 | 1.4964 | 1396.3619 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 9.6048 | 17.0688 | 16968.7514 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659060 [FINSTAD345 345.00] CKT 1 | 9.6048 | 6.1843 | 6084.2907 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 8.742 | 1.4654 | 1365.3608 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 8.742 | 1.4964 | 1396.3864 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 9.6295 | 16.9964 | 16896.3997 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659111 [LELAND_2-BEG20.000] CKT 1 | 9.6295 | 6.1881 | 6088.0953 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 8.781 | 1.4651 | 1365.1048 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 8.781 | 1.4962 | 1396.2197 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 9.6347 | 16.9766 | 16876.6473 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659422 [LO.LS-GR-BE3345.00] CKT Z | 9.6347 | 6.1884 | 6088.3592 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 8.8073 | 1.465 | 1365.0072 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 8.8073 | 1.4961 | 1396.1285 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 9.6377 | 16.9626 | 16862.572 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 763703 [GEN-2019-037345.00] CKT 1 | 9.6377 | 6.1877 | 6087.7175 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 8.7731 | 1.4652 | 1365.2344 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 8.7731 | 1.4963 | 1396.3062 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 9.6364 | 16.9689 | 16868.8621 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659201 [LO.KU1A_-BE913.800] CKT 1 | 9.6364 | 6.1884 | 6088.384 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 8.7781 | 1.4651 | 1365.1399 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 8.7781 | 1.4962 | 1396.2378 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 9.6362 | 16.9651 | 16865.0998 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659105 [LELAND_O-BE3345.00] TO BUS 659106 [LELAND_O-BE4230.00] TO BUS 659202 [LO.KVA2_-BE913.800] CKT 1 | 9.6362 | 6.1878 | 6087.8391 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 3.7563 | 1.5211 | 1421.0823 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 3.7563 | 1.5423 | 1442.2735 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 9.6317 | 16.9581 | 16858.1032 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 652806 [FTTHOM1-LNX3345.00] CKT 1 | 9.6317 | 6.1858 | 6085.8001 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 8.8422 | 1.4666 | 1366.6143 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 8.8422 | 1.4973 | 1397.3395 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 9.6377 | 16.9579 | 16857.9461 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659130 [CHAPELLE-BE3345.00] TO BUS 659433 [TRIPLEH__UA3345.00] CKT 1 | 9.6377 | 6.1878 | 6087.8014 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8056 | 1.4649 | 1364.9484 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 8.8056 | 1.4961 | 1396.0849 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 4.831 | 4.7688 | 4668.8052 | 54.6 | 86.4 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659151 [RICHLAND-BE7115.00] TO BUS 652651 [FAIRVIEW 7 115.00] CKT 1 | 4.831 | 8.019 | 7919.0226 | 19.9 | 31.5 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 8.8046 | 1.465 | 1364.9538 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 8.8046 | 1.4961 | 1396.0886 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 9.6251 | 16.9865 | 16886.4814 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 652419 [KILDEER7 115.00] CKT 1 | 9.6251 | 6.1901 | 6090.0856 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 8.8051 | 1.4649 | 1364.9482 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 8.8051 | 1.4961 | 1396.0853 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 9.6365 | 16.9502 | 16850.2036 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 655833 [GRSYBTTP-MK7115.00] CKT 1 | 9.6365 | 6.1869 | 6086.8636 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.8047 | 1.465 | 1364.9549 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.8047 | 1.4961 | 1396.0899 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.8449 | 25.5494 | 25449.4059 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659184 [ROUGHRDR-BE7115.00] CKT 1 | 8.8449 | 6.3252 | 6225.2457 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 8.8049 | 1.4649 | 1364.9478 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 8.8049 | 1.4961 | 1396.0861 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 9.6358 | 16.9401 | 16840.1496 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659182 [CHARL_CK-BE7115.00] TO BUS 659185 [FOUREYES-RR7115.00] CKT 1 | 9.6358 | 6.1859 | 6085.8933 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8039 | 1.465 | 1364.9629 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8039 | 1.4961 | 1396.0972 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6303 | 16.934 | 16834.0045 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659183 [CHARL_CK-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6303 | 6.1824 | 6082.4413 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.8039 | 1.4649 | 1364.9483 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.8039 | 1.4961 | 1396.0856 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.783 | 19.6475 | 19547.4927 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659186 [E.SIDNEY-LY7115.00] TO BUS 659180 [KOCH_OIL-BE7115.00] CKT 1 | 8.783 | 6.2595 | 6159.5087 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 8.8051 | 1.4649 | 1364.9478 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 8.8051 | 1.4961 | 1396.0845 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 9.6347 | 16.9603 | 16860.2728 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659112 [CULBRTSN-UM7115.00] CKT 1 | 9.6347 | 6.1866 | 6086.6456 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 8.8067 | 1.465 | 1364.9548 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 8.8067 | 1.4961 | 1396.0816 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 9.5702 | 17.2381 | 17138.1443 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659262 [CULBSN.E-BE7115.00] TO BUS 659269 [CULB_GEN-BE7115.00] CKT 1 | 9.5702 | 6.1954 | 6095.4219 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.8025 | 1.465 | 1364.9731 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 8.8025 | 1.4961 | 1396.1036 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.626 | 16.9473 | 16847.2878 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659302 [CHARL_CK-BE4230.00] TO BUS 652216 [WATFORD4 230.00] CKT 1 | 9.626 | 6.1814 | 6081.3977 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8044 | 1.465 | 1364.9576 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8044 | 1.4961 | 1396.0913 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.5615 | 17.1438 | 17043.767 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659333 [JUDSON__-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.5615 | 6.1879 | 6087.9399 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 8.7994 | 1.465 | 1364.9626 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 8.7994 | 1.4961 | 1396.1098 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 9.6422 | 16.9605 | 16860.4972 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659384 [ROUNDUP_-BE3345.00] TO BUS 659385 [ROUNDUP_-MK7115.00] TO BUS 659386 [RP.KU3A_-BE913.800] CKT 1 | 9.6422 | 6.1931 | 6093.1142 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8017 | 1.4649 | 1364.9414 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 8.8017 | 1.4961 | 1396.0867 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6269 | 16.9554 | 16855.4181 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659387 [KUMMERDG-BE3345.00] TO BUS 659390 [PATENTGT-BE3345.00] CKT 1 | 9.6269 | 6.1873 | 6087.286 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 8.7999 | 1.465 | 1364.9609 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 8.7999 | 1.4961 | 1396.1064 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 9.6456 | 16.9774 | 16877.4443 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655849 [VEEDER -MK7115.00] CKT 1 | 9.6456 | 6.1968 | 6096.7729 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 8.7984 | 1.465 | 1364.9615 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 8.7984 | 1.4961 | 1396.1106 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 9.6457 | 16.9725 | 16872.4622 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655873 [BBCOMPTP-MK7115.00] CKT 1 | 9.6457 | 6.1971 | 6097.0939 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 8.8045 | 1.465 | 1364.9503 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 8.8045 | 1.4961 | 1396.0878 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 9.6385 | 16.9591 | 16859.1293 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655881 [DAP_____-MK7115.00] CKT 1 | 9.6385 | 6.1888 | 6088.8094 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 8.8023 | 1.465 | 1364.9584 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 8.8023 | 1.4961 | 1396.099 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 9.6442 | 16.9785 | 16878.5306 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655882 [GALAXYTP-MK7115.00] CKT 1 | 9.6442 | 6.1949 | 6094.9306 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 8.8044 | 1.4649 | 1364.9499 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 8.8044 | 1.4961 | 1396.0874 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 9.6383 | 16.9582 | 16858.1769 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659388 [KUMMERDG-MK7115.00] TO BUS 655899 [FNCYBTAP-MK7115.00] CKT 1 | 9.6383 | 6.1885 | 6088.5497 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 8.8027 | 1.4649 | 1364.9496 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 8.8027 | 1.4961 | 1396.0929 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 9.6401 | 16.9566 | 16856.6422 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655844 [TIMBERCK-MK7115.00] CKT 1 | 9.6401 | 6.1907 | 6090.681 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 8.8008 | 1.465 | 1364.9508 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 8.8008 | 1.4961 | 1396.0987 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 9.6433 | 16.9657 | 16865.6775 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655856 [STNJOHNY-MK7115.00] CKT 1 | 9.6433 | 6.1942 | 6094.1711 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 8.8037 | 1.4649 | 1364.9479 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 8.8037 | 1.4961 | 1396.0896 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 9.6373 | 16.9446 | 16844.5989 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 655889 [LC_GAS_P-MK7115.00] CKT 1 | 9.6373 | 6.1876 | 6087.6437 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.8044 | 1.4649 | 1364.9463 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.8044 | 1.4961 | 1396.0843 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.632 | 16.9767 | 16876.6964 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.632 | 6.1865 | 6086.4963 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 8.8043 | 1.4649 | 1364.9466 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 8.8043 | 1.4961 | 1396.0844 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 9.6318 | 16.973 | 16872.9516 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 2 | 9.6318 | 6.1865 | 6086.5018 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.8048 | 1.465 | 1364.9516 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 8.8048 | 1.4961 | 1396.0876 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.635 | 16.958 | 16857.9584 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659392 [PG.KU17A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659466 [PG.KU17A-BE7115.00] CKT 1 | 9.635 | 6.1876 | 6087.5634 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 8.8048 | 1.465 | 1364.9518 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 8.8048 | 1.4961 | 1396.0876 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 9.6349 | 16.958 | 16857.9872 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659393 [PG.KU19A-BE913.800] TO BUS 659390 [PATENTGT-BE3345.00] TO BUS 659467 [PG.KU19A-BE7115.00] CKT 2 | 9.6349 | 6.1876 | 6087.565 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.6627 | 1.5214 | 1421.4056 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 4.6627 | 1.542 | 1441.9887 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6336 | 16.9665 | 16866.4522 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659424 [LO.LS-FT-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6336 | 6.1867 | 6086.6993 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 3.9464 | 1.5588 | 1458.7831 | 125.33 | 140.51 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 3.9464 | 1.5709 | 1470.9087 | 109.67 | 122.95 | FAIL | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6339 | 16.9687 | 16868.7034 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659428 [CC.LS-LO-BE3345.00] TO BUS 764220 [G20-021-TAP 345.00] CKT 1 | 9.6339 | 6.1876 | 6087.563 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 8.8026 | 1.465 | 136496% | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 8.8026 | 1.4961 | 1396.0917 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 9.5992 | 17.1043 | 1700429% | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 659427 [TN.LS-JD-BE3345.00] CKT 1 | 9.5992 | 6.1837 | 6083.7057 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 8.8049 | 1.465 | 1364.9768 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 8.8049 | 1.4961 | 1396.095 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 9.647 | 17.5442 | 17444.1652 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659600 [EFORK_-BE334345.00] TO BUS 655957 [EASTFORK-MW7115.00] TO BUS 659601 [EASTFORKTERT13.800] CKT 1 | 9.647 | 6.252 | 6151.9662 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.8055 | 1.4649 | 1364.9481 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.8055 | 1.4961 | 1396.0847 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7059 | 20.7272 | 20627.1711 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 652404 [DAWSONC7 115.00] CKT 1 | 8.7059 | 6.26 | 6159.998 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.8059 | 1.465 | 1364.9529 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.8059 | 1.4961 | 1396.0835 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.5558 | 77.9305 | 77830.5344 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661055 [LEWIS71G 13.800] CKT 1 | 8.5558 | 6.5282 | 6428.2332 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 8.8057 | 1.4649 | 1364.9499 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 8.8057 | 1.4961 | 1396.0844 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 9.3316 | 19.852 | 19751.9811 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 661056 [LEWIS 7 115.00] TO BUS 661104 [LEWIS72G 13.800] CKT 1 | 9.3316 | 6.2541 | 6154.0885 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7984 | 1.465 | 1364.9848 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 8.7984 | 1.4961 | 1396.129 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6382 | 16.9571 | 16857.1051 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659101 [ANTELOPE-BE3345.00] TO BUS 659212 [DGC_____-BE3345.00] CKT 1 | 9.6382 | 6.1889 | 6088.9408 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.8021 | 1.465 | 1364.9534 | 125.33 | 140.51 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-021 | LeLand Olds-Chapelle Creek 345kV line | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 8.8021 | 1.4961 | 1396.0812 | 109.67 | 122.95 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.6068 | 17.1371 | 17037.1467 | 54.6 | 86.4 | PASS | PASS
DISIS-2020-001-1 | 01 NORTH | 25WP | GEN-2020-083 | Fairview 115kV Substation | OPEN LINE FROM BUS 659391 [PATENTGT-MK7115.00] TO BUS 659349 [LC_SWY.N-BE7115.00] CKT 1 | 9.6068 | 6.1877 | 6087.7381 | 19.9 | 31.5 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | Base | 10.4627 | 16.412 | 16312.0055 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.7351 | 19.9681 | 19868.0961 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.7351 | 19.7407 | 19640.69 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.7351 | 19.9498 | 19849.8294 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.7351 | 20.0037 | 19903.707 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.4778 | 64.7086 | 64608.6241 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.4778 | 63.0042 | 62904.2373 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.4778 | 56.276 | 56176.0152 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | Base | 42.4974 | 16.124 | 16024.0159 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | Base | 24.5844 | 2.3581 | 2258.0683 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | Base | 24.5844 | 2.3011 | 2201.0923 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | Base | 36.6031 | 2.19 | 2089.9899 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | Base | 36.6031 | 2.2495 | 2149.5318 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.4594 | 16.4104 | 16310.3579 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.9892 | 20.4914 | 20391.3982 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.9892 | 20.2518 | 20151.7777 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.9892 | 20.4721 | 20372.0774 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.9892 | 20.5291 | 20429.0683 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.4113 | 68.6205 | 68520.5362 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.4113 | 66.7242 | 66624.159 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.4113 | 59.0443 | 58944.2805 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 42.4741 | 16.1232 | 16023.1691 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 24.5681 | 2.3561 | 2256.1181 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 24.5681 | 2.2993 | 2199.2952 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 36.4489 | 2.1771 | 2077.1294 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 36.4489 | 2.2362 | 2136.1847 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.4606 | 16.4161 | 16316.0535 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.6817 | 19.9218 | 19821.764 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.6817 | 19.6953 | 19595.2589 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.6817 | 19.9036 | 19803.6026 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.6817 | 19.9573 | 19857.2805 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4729 | 64.7019 | 64601.8808 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4729 | 63 | 62899.9825 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4729 | 56.2642 | 56164.2285 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 42.4472 | 16.1273 | 16027.3462 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.5301 | 2.3602 | 2260.2004 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.5301 | 2.3033 | 2203.3269 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.9953 | 2.2045 | 2104.4734 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.9953 | 2.2647 | 2164.6665 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 10.4624 | 16.4118 | 16311.8288 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 15.5725 | 19.9513 | 19851.3075 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 15.5725 | 19.7236 | 19623.6092 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 15.5725 | 19.9331 | 19833.1157 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 15.5725 | 19.9872 | 19887.1691 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.4674 | 65.4047 | 65304.6876 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.4674 | 63.6729 | 63572.92 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.4674 | 56.7524 | 56652.4104 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 42.4972 | 16.1241 | 16024.0568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 24.5842 | 2.3581 | 2258.0715 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 24.5842 | 2.3011 | 2201.1015 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 36.5993 | 2.1896 | 2089.614 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 36.5993 | 2.2491 | 2149.1441 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.4627 | 16.412 | 16312.0354 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.7684 | 19.9712 | 19871.2214 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.7684 | 19.7436 | 19643.6151 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.7684 | 19.953 | 19852.9549 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.7684 | 20.0069 | 19906.9032 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.4779 | 64.9181 | 64818.0538 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.4779 | 63.2049 | 63104.9313 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.4779 | 56.4214 | 56321.3631 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 42.4983 | 16.1241 | 16024.088 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 24.5851 | 2.3582 | 2258.163 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 24.5851 | 2.3012 | 2201.1849 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 36.6079 | 2.1904 | 2090.3798 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 36.6079 | 2.2499 | 2149.9381 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.4404 | 16.4212 | 16321.2426 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7376 | 19.971 | 19870.9603 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7376 | 19.7435 | 19643.4964 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7376 | 19.9527 | 19852.687 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7376 | 20.0066 | 19906.5778 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4783 | 64.7131 | 64613.1015 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4783 | 63.0083 | 62908.276 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4783 | 56.2799 | 56179.8715 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 41.4065 | 16.1486 | 16048.5754 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 16.7462 | 2.3616 | 2261.5764 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 16.7462 | 2.322 | 2222.0242 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 36.3548 | 2.1838 | 2083.8304 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 36.3548 | 2.2432 | 2143.1683 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 10.4623 | 16.412 | 16311.9604 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.5042 | 19.9852 | 19885.2288 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.5042 | 19.7574 | 19657.4272 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.5042 | 19.9669 | 19866.934 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.5042 | 20.0209 | 19920.9167 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 3.1157 | 19.2363 | 19136.2808 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 3.1157 | 18.9722 | 18872.2264 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 3.1157 | 19.32 | 19219.9776 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 42.496 | 16.124 | 16024.0095 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 24.5836 | 2.358 | 2258.0444 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 24.5836 | 2.3011 | 2201.0704 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 36.6 | 2.1898 | 2089.7976 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 36.6 | 2.2493 | 2149.332 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 10.4625 | 16.412 | 16311.9867 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 15.1475 | 19.9883 | 19888.2594 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 15.1475 | 19.7605 | 19660.4671 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 15.1475 | 19.97 | 19869.9637 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 15.1475 | 20.0239 | 19923.9389 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.395 | 66.1964 | 66096.3766 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.395 | 64.4278 | 64327.8387 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.395 | 57.3318 | 57231.776 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 42.4966 | 16.124 | 16024.0103 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 24.584 | 2.3581 | 2258.0582 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 24.584 | 2.3011 | 2201.0827 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 36.5996 | 2.1898 | 2089.8326 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 36.5996 | 2.2494 | 2149.3676 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 10.4626 | 16.412 | 16311.9857 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 15.5696 | 19.9601 | 19860.0712 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 15.5696 | 19.7329 | 19632.946 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 15.5696 | 19.9418 | 19841.8227 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 15.5696 | 19.9956 | 19895.6212 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.4472 | 64.8229 | 64722.9237 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.4472 | 63.1154 | 63015.3866 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.4472 | 56.3604 | 56260.3683 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 42.4971 | 16.124 | 16024.0127 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 24.5843 | 2.3581 | 2258.0599 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 24.5843 | 2.3011 | 2201.0846 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 36.6024 | 2.1899 | 2089.8989 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 36.6024 | 2.2494 | 2149.4369 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.4543 | 16.4125 | 16312.5486 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7135 | 19.9472 | 19847.2403 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7135 | 19.7202 | 19620.2429 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7135 | 19.929 | 19829.02 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7135 | 19.9828 | 19882.8064 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4756 | 64.6985 | 64598.5232 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4756 | 62.9956 | 62895.6332 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4756 | 56.2654 | 56165.4155 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 42.365 | 16.1277 | 16027.7246 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.464 | 2.3573 | 2257.2837 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.464 | 2.3007 | 2200.689 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.6525 | 2.1825 | 2082.511 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.6525 | 2.2419 | 2141.8928 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.4624 | 16.4122 | 16312.1785 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 15.0397 | 20.0484 | 19948.418 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 15.0397 | 19.8189 | 19718.8864 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 15.0397 | 20.03 | 19930.0047 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 15.0397 | 20.0845 | 19984.4615 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.4618 | 65.349 | 65248.9852 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.4618 | 63.6161 | 63516.0918 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.4618 | 56.7254 | 56625.4135 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 42.4939 | 16.1241 | 16024.1119 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 24.5804 | 2.3581 | 2258.1209 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 24.5804 | 2.3012 | 2201.154 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 36.5647 | 2.1903 | 2090.3467 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 36.5647 | 2.2499 | 2149.908 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.4624 | 16.4123 | 16312.2904 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.7955 | 20.0552 | 19955.1865 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.7955 | 19.8256 | 19725.5624 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.7955 | 20.0368 | 19936.758 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.7955 | 20.0912 | 19991.231 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4571 | 65.3725 | 65272.5428 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4571 | 63.6379 | 63537.9231 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4571 | 56.7448 | 56644.7945 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 42.4928 | 16.1241 | 16024.1405 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 24.5787 | 2.3582 | 2258.1658 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 24.5787 | 2.3012 | 2201.1962 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 36.5504 | 2.1907 | 2090.6701 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 36.5504 | 2.2502 | 2150.2438 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 10.4625 | 16.4119 | 16311.8674 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.7138 | 19.9559 | 19855.9218 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.7138 | 19.7288 | 19628.7553 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.7138 | 19.9377 | 19837.6818 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.7138 | 19.9915 | 19891.5061 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.3695 | 133.0964 | 132996.4075 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.3695 | 126.8955 | 126795.5006 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.3695 | 94.1743 | 94074.28 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 42.4967 | 16.124 | 16023.9949 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 24.5841 | 2.358 | 2258.0018 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 24.5841 | 2.301 | 2201.0318 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 36.598 | 2.1894 | 2089.4355 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 36.598 | 2.249 | 2148.9568 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 10.4627 | 16.4121 | 16312.077 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.7419 | 19.9685 | 19868.5222 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.7419 | 19.7411 | 19641.1048 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.7419 | 19.9503 | 1985025% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.7419 | 20.0041 | 19904.1342 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.4496 | 60.2408 | 6014081% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.4496 | 60.7391 | 60639.1255 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.4496 | 558.5173 | 558417.3468 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 42.4972 | 16.124 | 16024.0382 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 24.5841 | 2.3581 | 2258.0988 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 24.5841 | 2.3011 | 2201.1209 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 36.5996 | 2.1903 | 2090.254 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 36.5996 | 2.2498 | 2149.8054 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0089 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 15.5628 | 19.9746 | 19874.6371 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 15.5628 | 19.747 | 19646.9825 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 15.5628 | 19.9564 | 19856.3614 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 15.5628 | 20.0103 | 19910.3174 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.97 | 61.7725 | 61672.5456 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.97 | 62.2229 | 62122.8631 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.97 | 501.5191 | 501419.1473 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 42.497 | 16.124 | 16024.016 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 24.584 | 2.3581 | 2258.0564 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 24.584 | 2.3011 | 2201.0818 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 36.5972 | 2.1898 | 2089.8321 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 36.5972 | 2.2494 | 2149.3681 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 10.4627 | 16.412 | 16312.0028 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.7354 | 19.9676 | 19867.6289 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.7354 | 19.7402 | 19640.2319 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.7354 | 19.9494 | 19849.3621 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.7354 | 20.0032 | 19903.2386 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.4795 | 64.5385 | 64438.5207 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.4795 | 62.8423 | 62742.3373 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.4795 | 56.1538 | 56053.8153 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 42.4974 | 16.124 | 16024.0151 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 24.5844 | 2.3581 | 2258.067 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 24.5844 | 2.3011 | 2201.091 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 36.6031 | 2.19 | 2089.9797 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 36.6031 | 2.2495 | 2149.5211 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 10.4627 | 16.412 | 16312.0028 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.7354 | 19.9676 | 19867.6278 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.7354 | 19.7402 | 19640.2308 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.7354 | 19.9494 | 19849.3611 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.7354 | 20.0032 | 19903.2375 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.4795 | 64.5382 | 64438.1914 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.4795 | 62.842 | 62742.0315 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.4795 | 56.1536 | 56053.5846 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 42.4974 | 16.124 | 16024.0151 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 24.5844 | 2.3581 | 2258.067 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 24.5844 | 2.3011 | 2201.091 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 36.6031 | 2.19 | 2089.9797 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 36.6031 | 2.2495 | 2149.5211 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 10.4626 | 16.4119 | 16311.9396 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.6995 | 19.9538 | 19853.7589 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.6995 | 19.7268 | 19626.7516 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.6995 | 19.9355 | 19835.5209 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.6995 | 19.9893 | 19889.2904 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.4109 | 53.1287 | 53028.7362 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.4109 | 51.9011 | 51801.0605 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.4109 | 47.7824 | 47682.4309 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 42.4964 | 16.124 | 16023.9719 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 24.5838 | 2.358 | 2257.982 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 24.5838 | 2.301 | 2201.0111 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 36.5978 | 2.1894 | 2089.421 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 36.5978 | 2.2489 | 2148.9402 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.4564 | 16.4136 | 16313.6365 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.6613 | 20.0658 | 19965.7802 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.6613 | 19.8354 | 19735.4216 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.6613 | 20.0474 | 19947.368 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.6613 | 20.1021 | 20002.104 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3742 | 67.6369 | 67536.8838 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3742 | 65.7996 | 65699.5789 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3742 | 58.3201 | 58220.0801 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 42.4522 | 16.1254 | 16025.3638 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 24.545 | 2.3574 | 2257.4391 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 24.545 | 2.3007 | 2200.7049 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 36.0003 | 2.1818 | 2081.7997 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 36.0003 | 2.2411 | 2141.134 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.4605 | 16.4149 | 16314.8737 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.5842 | 19.9808 | 19880.7705 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.5842 | 19.753 | 19652.9901 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.5842 | 19.9625 | 19862.4815 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.5842 | 20.0165 | 19916.4661 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4685 | 65.0201 | 64920.1278 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4685 | 63.302 | 63202.0068 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4685 | 56.4948 | 56394.8194 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 42.4311 | 16.1268 | 16026.7823 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 24.5208 | 2.3591 | 2259.1494 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 24.5208 | 2.3023 | 2202.2771 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 33.4291 | 2.2057 | 2105.6781 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 33.4291 | 2.2661 | 2166.0675 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 10.4626 | 16.4119 | 16311.9485 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.7236 | 19.9565 | 19856.4793 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.7236 | 19.7294 | 19629.3627 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.7236 | 19.9382 | 19838.2375 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.7236 | 19.992 | 19892.0415 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.4661 | 57.0768 | 56976.7673 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.4661 | 55.704 | 55604.0268 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.4661 | 50.7402 | 50640.1877 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 42.4969 | 16.124 | 16023.9898 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 24.5842 | 2.358 | 2258.017 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 24.5842 | 2.301 | 2201.044 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 36.6008 | 2.1896 | 2089.6279 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 36.6008 | 2.2492 | 2149.1551 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.4606 | 16.4134 | 16313.3924 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.1755 | 20.3232 | 20223.2444 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.1755 | 20.0859 | 19985.884 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.1755 | 20.3043 | 20204.3383 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.1755 | 20.361 | 20260.9799 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3418 | 71.9694 | 71869.4177 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3418 | 69.9217 | 69821.7217 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.3418 | 61.2615 | 61161.5305 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 42.4713 | 16.1246 | 16024.5916 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 24.5606 | 2.3579 | 2257.9191 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 24.5606 | 2.301 | 2201.0134 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 36.2006 | 2.1871 | 2087.1427 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 36.2006 | 2.2466 | 2146.6055 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 10.4627 | 16.4122 | 16312.1869 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 15.1357 | 19.9501 | 19850.0514 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 15.1357 | 19.7234 | 19623.4084 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 15.1357 | 19.9318 | 19831.8332 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 15.1357 | 19.9855 | 19885.4856 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.4165 | 68.4323 | 68332.3479 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.4165 | 66.5571 | 66457.0796 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.4165 | 58.8661 | 58766.0621 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 42.4949 | 16.1241 | 16024.0721 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 24.5819 | 2.3581 | 2258.0945 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 24.5819 | 2.3011 | 2201.1171 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 36.5581 | 2.1901 | 2090.0781 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 36.5581 | 2.2496 | 2149.6213 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.4613 | 16.4118 | 16311.8478 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 14.461 | 20.0221 | 19922.0683 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 14.461 | 19.7933 | 19693.2529 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 14.461 | 20.0037 | 19903.7284 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 14.461 | 20.058 | 19958.0021 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.4615 | 65.1235 | 65023.5263 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.4615 | 63.4019 | 63301.884 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.4615 | 56.5647 | 56464.6551 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 42.4872 | 16.1241 | 16024.1286 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 24.5724 | 2.3579 | 2257.8846 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 24.5724 | 2.301 | 2200.9631 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 36.5368 | 2.1873 | 2087.297 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 36.5368 | 2.2467 | 2146.7467 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.4621 | 16.412 | 16311.9807 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.8651 | 20.0395 | 19939.492 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.8651 | 19.81 | 19709.9903 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.8651 | 20.0211 | 19921.1108 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.8651 | 20.0756 | 19975.5877 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4556 | 65.5852 | 65485.2355 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4556 | 63.8434 | 63743.3958 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.4556 | 56.8856 | 56785.5843 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 42.4925 | 16.1241 | 16024.0875 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 24.5793 | 2.358 | 2258.0188 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 24.5793 | 2.3011 | 2201.0633 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 36.5525 | 2.1895 | 2089.5164 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 36.5525 | 2.249 | 2149.0474 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 10.4605 | 16.4126 | 16312.6494 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.7354 | 19.9685 | 19868.5444 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.7354 | 19.7411 | 19641.1282 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.7354 | 19.9503 | 19850.2755 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.7354 | 20.0042 | 19904.1563 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.4779 | 64.709 | 64608.967 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.4779 | 63.0046 | 62904.5668 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.4779 | 56.2764 | 56176.4 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 41.0034 | 16.1553 | 16055.3086 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 24.4901 | 2.3563 | 2256.3349 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 24.4901 | 2.2997 | 2199.6577 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 36.5781 | 2.1894 | 2089.3998 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 36.5781 | 2.2489 | 2148.9225 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 10.463 | 16.4123 | 16312.2674 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.7428 | 19.9764 | 19876.355 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.7428 | 19.7488 | 19648.7853 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.7428 | 19.9581 | 19858.0682 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.7428 | 20.012 | 19911.984 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.4787 | 64.7167 | 64616.6696 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.4787 | 63.0115 | 62911.4772 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.4787 | 56.2832 | 56183.1531 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 42.4986 | 16.1241 | 16024.1068 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 24.5848 | 2.3582 | 2258.2343 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 24.5848 | 2.3012 | 2201.2485 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 36.6071 | 2.1909 | 2090.8719 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 36.6071 | 2.2504 | 2150.4477 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 10.4627 | 16.412 | 16311.9923 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.7347 | 19.9677 | 19867.7075 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.7347 | 19.7403 | 19640.3075 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.7347 | 19.9494 | 19849.4402 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.7347 | 20.0033 | 19903.3176 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.4778 | 64.7082 | 64608.2406 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.4778 | 63.0039 | 62903.8748 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.4778 | 56.2757 | 56175.6626 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 42.4973 | 16.124 | 16024.0123 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 24.5843 | 2.3581 | 2258.0602 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 24.5843 | 2.3011 | 2201.0847 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 36.6029 | 2.1899 | 2089.9478 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 36.6029 | 2.2495 | 2149.488 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.4573 | 16.4163 | 16316.2548 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7698 | 20.0175 | 19917.4832 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7698 | 19.7891 | 19689.0902 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7698 | 19.9991 | 19899.1026 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7698 | 20.0532 | 19953.2068 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4816 | 64.7643 | 64664.259 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4816 | 63.0552 | 62955.2417 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4816 | 56.3224 | 5622243% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 42.3837 | 16.1271 | 1602708% | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.4768 | 2.3579 | 2257.8913 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.4768 | 2.3013 | 2201.2835 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.4069 | 2.1846 | 2084.6103 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.4069 | 2.2441 | 2144.0995 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.4541 | 16.4153 | 16315.3349 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7676 | 20.0179 | 19917.9326 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7676 | 19.7895 | 19689.528 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7676 | 19.9996 | 19899.5523 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7676 | 20.0537 | 19953.6595 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4814 | 64.7702 | 64670.1894 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4814 | 63.0609 | 62960.9057 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4814 | 56.3265 | 56226.4544 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 42.3493 | 16.1269 | 16026.8863 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.45 | 2.3561 | 2256.0788 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.45 | 2.2997 | 2199.6587 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.1037 | 2.1685 | 2068.5392 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.1037 | 2.2274 | 2127.4374 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.4476 | 16.4383 | 16338.2893 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7277 | 19.9628 | 19862.7665 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7277 | 19.7355 | 19635.4581 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7277 | 19.9445 | 19844.5117 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.7277 | 19.9984 | 19898.3693 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4766 | 64.7122 | 64612.2388 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4766 | 63.0083 | 62908.2651 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.4766 | 56.2767 | 56176.733 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 41.4818 | 16.175 | 16074.9847 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 8.2487 | 2.4896 | 2389.5929 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 8.2487 | 2.4671 | 2367.05 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 36.4129 | 2.1965 | 2096.5475 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 36.4129 | 2.2564 | 2156.4107 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.4538 | 16.4181 | 16318.1109 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7328 | 19.9692 | 19869.1631 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7328 | 19.7417 | 19641.736 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7328 | 19.9509 | 19850.8939 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.7328 | 20.0048 | 19904.7764 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4777 | 64.7119 | 64611.879 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4777 | 63.0073 | 62907.2742 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.4777 | 56.2786 | 56178.5629 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 42.2233 | 16.133 | 16033.002 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.3485 | 2.3577 | 2257.6821 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 24.3485 | 2.3016 | 2201.6043 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.4893 | 2.1964 | 2096.4278 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 35.4893 | 2.2562 | 2156.2092 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 10.4526 | 16.4168 | 16316.827 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.7329 | 19.9671 | 19867.0556 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.7329 | 19.7397 | 19639.6705 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.7329 | 19.9488 | 19848.7913 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.7329 | 20.0027 | 19902.6641 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.4776 | 64.7082 | 64608.2261 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.4776 | 63.0039 | 62903.9113 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.4776 | 56.2756 | 56175.5511 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 42.2807 | 16.1301 | 16030.1453 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 24.3888 | 2.3569 | 2256.8889 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 24.3888 | 2.3006 | 2200.6157 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 35.697 | 2.1992 | 2099.1977 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 35.697 | 2.2591 | 2159.1047 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 6.7433 | 32.0499 | 31949.9155 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.735 | 19.9684 | 19868.3665 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.735 | 19.741 | 19640.9549 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.735 | 19.9501 | 19850.0995 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.735 | 20.004 | 19903.9781 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.4778 | 64.7094 | 64609.4424 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.4778 | 63.005 | 62905.0026 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.4778 | 56.2767 | 56176.662 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 42.4987 | 16.124 | 16023.9743 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 24.5855 | 2.3581 | 2258.1212 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 24.5855 | 2.3011 | 2201.1313 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 36.5992 | 2.1906 | 2090.6458 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 36.5992 | 2.2502 | 2150.2125 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 10.4623 | 16.4117 | 16311.6536 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.735 | 19.968 | 19868.0179 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.735 | 19.7406 | 19640.612 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.735 | 19.9498 | 19849.7502 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.735 | 20.0036 | 19903.6286 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.4778 | 64.7085 | 64608.533 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.4778 | 63.0042 | 62904.1509 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.4778 | 56.2759 | 56175.9278 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 41.497 | 16.1395 | 16039.488 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 24.4903 | 2.3568 | 2256.837 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 24.4903 | 2.3 | 2199.9802 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 36.6027 | 2.19 | 2089.9509 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 36.6027 | 2.2495 | 2149.4916 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 10.4107 | 16.4464 | 16346.4448 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.7355 | 19.9685 | 19868.4713 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.7355 | 19.7411 | 19641.0579 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.7355 | 19.9502 | 19850.2037 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.7355 | 20.0041 | 19904.0831 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.4778 | 64.7089 | 64608.9014 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.4778 | 63.0045 | 62904.5012 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.4778 | 56.2763 | 56176.2905 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 41.7331 | 16.1457 | 16045.7235 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 24.4737 | 2.3595 | 2259.4903 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 24.4737 | 2.3027 | 2202.681 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 36.5902 | 2.1899 | 2089.9363 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 36.5902 | 2.2495 | 2149.4775 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 10.462 | 16.413 | 16313.0264 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.735 | 19.9681 | 19868.0963 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.735 | 19.7407 | 19640.6886 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.735 | 19.9498 | 19849.8282 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.735 | 20.0037 | 19903.707 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.4778 | 64.7086 | 64608.5667 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.4778 | 63.0042 | 62904.1841 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.4778 | 56.276 | 56175.9767 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 40.5681 | 16.1903 | 16090.2817 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 24.4824 | 2.3574 | 2257.3537 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 24.4824 | 2.3005 | 2200.4855 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 36.6013 | 2.1899 | 2089.8792 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 36.6013 | 2.2494 | 2149.4167 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 10.462 | 16.413 | 16313.0264 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.735 | 19.9681 | 19868.0963 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.735 | 19.7407 | 19640.6886 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.735 | 19.9498 | 19849.8282 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.735 | 20.0037 | 19903.707 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.4778 | 64.7086 | 64608.5667 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.4778 | 63.0042 | 62904.1841 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.4778 | 56.276 | 56175.9767 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 40.5681 | 16.1903 | 16090.2817 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 24.4824 | 2.3574 | 2257.3537 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 24.4824 | 2.3005 | 2200.4855 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 36.6013 | 2.1899 | 2089.8792 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 36.6013 | 2.2494 | 2149.4167 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 10.4622 | 16.4118 | 16311.8061 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.9681 | 19868.0574 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.7407 | 19640.6506 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.9498 | 19849.7896 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 20.0037 | 19903.6682 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 64.7087 | 64608.6691 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 63.0043 | 62904.278 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 56.276 | 56176.0325 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 39.6112 | 16.2069 | 16106.9218 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 24.5816 | 2.3578 | 2257.8317 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 24.5816 | 2.3009 | 2200.8753 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 36.602 | 2.1899 | 2089.8838 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 36.602 | 2.2494 | 2149.4214 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 10.4618 | 16.412 | 16311.9928 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.7349 | 19.968 | 19868.0393 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.7349 | 19.7406 | 19640.6339 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.7349 | 19.9498 | 19849.7713 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.7349 | 20.0036 | 19903.6499 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.4778 | 64.7087 | 64608.6996 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.4778 | 63.0043 | 62904.3052 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.4778 | 56.276 | 56176.0387 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 38.7674 | 16.2329 | 16132.8992 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 24.552 | 2.3583 | 2258.2997 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 24.552 | 2.3013 | 2201.3193 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 36.5998 | 2.1899 | 2089.8753 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 36.5998 | 2.2494 | 2149.4137 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 10.4622 | 16.4118 | 16311.8027 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.9681 | 19868.0718 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.7407 | 19640.6662 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 19.9498 | 19849.8037 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.735 | 20.0037 | 19903.6827 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 64.7087 | 64608.6789 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 63.0043 | 62904.3485 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.4778 | 56.2761 | 56176.0853 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 39.6135 | 16.2111 | 16111.0874 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 24.5821 | 2.3577 | 2257.7272 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 24.5821 | 2.3008 | 2200.7862 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 36.6022 | 2.1898 | 2089.8348 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 36.6022 | 2.2494 | 2149.3708 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 9.8047 | 16.5158 | 16415.8302 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.7348 | 19.9678 | 19867.7941 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.7348 | 19.7404 | 19640.3941 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.7348 | 19.9495 | 19849.5281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.7348 | 20.0034 | 19903.4044 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.4777 | 64.7083 | 64608.3467 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.4777 | 63.004 | 62903.9738 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.4777 | 56.2757 | 56175.7442 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 42.4921 | 16.1236 | 16023.5573 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 24.5835 | 2.3575 | 2257.509 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 24.5835 | 2.3006 | 2200.5663 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 36.6019 | 2.1896 | 2089.5995 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 36.6019 | 2.2491 | 2149.1258 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 10.4636 | 16.4019 | 16301.9416 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.7348 | 19.9678 | 19867.8115 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.7348 | 19.7404 | 19640.411 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.7348 | 19.9495 | 19849.544 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.7348 | 20.0034 | 19903.4218 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.4778 | 64.7084 | 64608.3864 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.4778 | 63.0041 | 62904.0741 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.4778 | 56.2758 | 56175.843 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 42.4974 | 16.124 | 16024.0344 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 24.5842 | 2.3581 | 2258.1065 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 24.5842 | 2.3011 | 2201.1257 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 36.6027 | 2.19 | 2089.9872 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 36.6027 | 2.2495 | 2149.5286 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 6.1183 | 21.8977 | 21797.6855 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.735 | 19.9682 | 19868.2288 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.735 | 19.7408 | 19640.8198 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.735 | 19.95 | 19849.9618 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.735 | 20.0038 | 19903.8401 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.4778 | 64.7091 | 64609.1342 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.4778 | 63.0047 | 62904.7132 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.4778 | 56.2764 | 56176.4004 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 42.4885 | 16.124 | 16024.0019 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 24.5834 | 2.3577 | 225770% | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 24.5834 | 2.3008 | 2200.7502 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 36.5967 | 2.1899 | 208994% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 36.5967 | 2.2495 | 2149.4807 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.4563 | 16.4174 | 16317.4242 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.712 | 19.9688 | 19868.805 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.712 | 19.7414 | 19641.3813 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.712 | 19.9505 | 19850.5377 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.712 | 20.0044 | 19904.4209 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4766 | 64.7366 | 64636.5727 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4766 | 63.0309 | 62930.9378 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.4766 | 56.2959 | 56195.8566 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 42.4251 | 16.1267 | 16026.6609 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 24.5103 | 2.3581 | 2258.1324 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 24.5103 | 2.3015 | 2201.4585 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 33.0732 | 2.2027 | 2102.6731 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 33.0732 | 2.2629 | 2162.8534 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 10.4654 | 16.4154 | 16315.3735 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.7531 | 19.9869 | 19886.9132 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.7531 | 19.7591 | 19659.1364 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.7531 | 19.9686 | 19868.602 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.7531 | 20.0226 | 19922.565 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.4797 | 64.7211 | 64621.0635 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.4797 | 63.0152 | 62915.2126 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.4797 | 56.2878 | 56187.8182 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 42.5181 | 16.1276 | 16027.6215 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 24.622 | 2.374 | 2274.0125 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 24.622 | 2.3174 | 2217.4103 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 36.6253 | 2.1948 | 2094.8203 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 36.6253 | 2.2546 | 2154.5526 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 10.4654 | 16.4154 | 16315.3735 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.7531 | 19.9869 | 19886.9132 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.7531 | 19.7591 | 19659.1364 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.7531 | 19.9686 | 19868.602 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.7531 | 20.0226 | 19922.565 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.4797 | 64.7211 | 64621.0635 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.4797 | 63.0152 | 62915.2126 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.4797 | 56.2878 | 56187.8182 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 42.5181 | 16.1276 | 16027.6215 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 24.622 | 2.374 | 2274.0125 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 24.622 | 2.3174 | 2217.4103 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 36.6253 | 2.1948 | 2094.8203 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 36.6253 | 2.2546 | 2154.5526 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 10.4654 | 16.4154 | 16315.3518 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.753 | 19.9868 | 19886.8027 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.753 | 19.759 | 19659.0281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.753 | 19.9685 | 19868.4932 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.753 | 20.0225 | 19922.4543 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.4797 | 64.721 | 64620.9937 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.4797 | 63.0151 | 62915.146 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.4797 | 56.2878 | 56187.7923 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 42.5179 | 16.1276 | 16027.5975 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 24.6217 | 2.3739 | 2273.86 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 24.6217 | 2.3173 | 2217.2609 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 36.6252 | 2.1948 | 2094.7899 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 36.6252 | 2.2545 | 2154.5208 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 10.4624 | 16.412 | 16311.9593 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 15.0419 | 20.0695 | 19969.4834 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 15.0419 | 19.8395 | 19739.5372 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 15.0419 | 20.051 | 19951.0208 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 15.0419 | 20.1056 | 20005.5697 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.4636 | 65.5018 | 65401.8298 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.4636 | 63.7597 | 63659.6959 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.4636 | 56.841 | 56741.0325 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 42.4938 | 16.1239 | 16023.9281 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 24.5815 | 2.3578 | 2257.8335 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 24.5815 | 2.3009 | 2200.8793 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 36.5755 | 2.1884 | 2088.4006 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 36.5755 | 2.2479 | 2147.8837 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 10.4622 | 16.4118 | 16311.8154 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 15.1627 | 20.0652 | 19965.1542 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 15.1627 | 19.8356 | 19735.6298 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 15.1627 | 20.0467 | 19946.6918 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 15.1627 | 20.1011 | 20001.0926 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.4667 | 65.395 | 65294.9883 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.4667 | 63.657 | 63556.9875 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.4667 | 56.7698 | 56669.7894 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 42.4937 | 16.1239 | 16023.8978 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 24.5816 | 2.3578 | 2257.7949 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 24.5816 | 2.3008 | 2200.8412 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 36.5796 | 2.1885 | 2088.4694 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 36.5796 | 2.248 | 2147.9538 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 10.4593 | 16.4137 | 16313.7412 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 15.6527 | 19.9396 | 19839.5716 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 15.6527 | 19.7127 | 19612.6865 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 15.6527 | 19.9214 | 19821.3708 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 15.6527 | 19.9751 | 19875.1384 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.4727 | 64.7378 | 64637.8354 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.4727 | 63.0338 | 62933.8153 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.4727 | 56.291 | 56190.957 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 42.4349 | 16.126 | 16025.9558 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 24.5201 | 2.3591 | 2259.0824 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 24.5201 | 2.3022 | 2202.181 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 35.8834 | 2.1979 | 2097.9406 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 35.8834 | 2.2578 | 2157.8379 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 10.4627 | 16.4128 | 16312.7617 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.7417 | 19.975 | 19875.0237 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.7417 | 19.7475 | 19647.4797 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.7417 | 19.9567 | 19856.741 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.7417 | 20.0107 | 19910.6517 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.4785 | 64.717 | 64616.9697 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.4785 | 63.0119 | 62911.8901 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.4785 | 56.2829 | 56182.898 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 42.4986 | 16.1245 | 16024.5478 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 24.5861 | 2.3582 | 2258.1798 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 24.5861 | 2.3013 | 2201.2518 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 36.6237 | 2.19 | 2089.97 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 36.6237 | 2.2495 | 2149.5344 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 10.4631 | 16.4124 | 16312.3561 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.7355 | 19.9687 | 19868.6859 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.7355 | 19.7413 | 19641.2681 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.7355 | 19.9504 | 19850.4178 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.7355 | 20.0043 | 19904.2981 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.4779 | 64.7091 | 64609.1179 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.4779 | 63.0046 | 62904.6454 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.4779 | 56.2765 | 56176.4593 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 42.4987 | 16.1242 | 16024.1874 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 24.5845 | 2.3584 | 2258.3997 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 24.5845 | 2.3014 | 2201.405 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 36.6061 | 2.1927 | 2092.6969 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 36.6061 | 2.2523 | 2152.3447 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 10.4624 | 16.4118 | 16311.7578 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.7348 | 19.9677 | 19867.6885 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.7348 | 19.7403 | 19640.2905 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.7348 | 19.9494 | 19849.4229 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.7348 | 20.0033 | 19903.2985 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.4778 | 64.7082 | 64608.224 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.4778 | 63.0039 | 62903.8586 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.4778 | 56.2756 | 56175.6372 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 42.4959 | 16.1239 | 16023.897 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 24.5841 | 2.3578 | 2257.8319 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 24.5841 | 2.3009 | 2200.8694 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 36.6009 | 2.1881 | 2088.0597 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 36.6009 | 2.2475 | 2147.5259 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.46 | 16.411 | 16310.9728 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.9052 | 20.5351 | 20435.0837 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.9052 | 20.2934 | 20193.3891 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.9052 | 20.5157 | 20415.7274 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.9052 | 20.5734 | 20473.391 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4036 | 70.1513 | 70051.2977 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4036 | 68.1843 | 68084.3134 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4036 | 60.0756 | 59975.5884 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 42.477 | 16.1235 | 16023.452 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5692 | 2.3566 | 2256.5692 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5692 | 2.2997 | 2199.7277 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.4609 | 2.1798 | 2079.8408 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.4609 | 2.239 | 2139.0056 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 10.4625 | 16.4119 | 16311.8927 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.6888 | 19.9628 | 19862.8363 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.6888 | 19.735 | 19635.0182 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.6888 | 19.9446 | 19844.6116 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.6888 | 19.9987 | 19898.6742 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.4719 | 65.2922 | 65192.2462 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.4719 | 63.5645 | 63464.5489 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.4719 | 56.6769 | 56576.9479 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 42.4976 | 16.1241 | 16024.0599 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 24.5845 | 2.3581 | 2258.0899 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 24.5845 | 2.3011 | 2201.1177 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 36.6028 | 2.1898 | 2089.8345 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 36.6028 | 2.2494 | 2149.3727 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 10.4627 | 16.412 | 16312.0191 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 15.6171 | 19.9777 | 19877.666 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 15.6171 | 19.75 | 19649.9608 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 15.6171 | 19.9594 | 19859.3838 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 15.6171 | 20.0133 | 19913.3489 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.4744 | 64.8349 | 64734.9298 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.4744 | 63.1251 | 63025.0967 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.4744 | 56.3644 | 56264.3905 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 42.4973 | 16.124 | 16024.036 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 24.5841 | 2.3581 | 2258.0932 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 24.5841 | 2.3011 | 2201.1167 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 36.6006 | 2.1901 | 2090.1323 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 36.6006 | 2.2497 | 2149.6801 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.463 | 16.4123 | 16312.3147 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.7681 | 20.0151 | 19915.1468 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.7681 | 19.7866 | 19686.6261 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.7681 | 19.9968 | 19896.7826 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.7681 | 20.0509 | 19950.944 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.4802 | 65.0059 | 64905.8937 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.4802 | 63.2872 | 63187.1531 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.4802 | 56.489 | 56388.9721 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 42.499 | 16.1242 | 16024.1629 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 24.585 | 2.3583 | 2258.3034 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 24.585 | 2.3013 | 2201.3175 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 36.6104 | 2.1915 | 2091.528 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 36.6104 | 2.2511 | 2151.1312 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.4614 | 16.4131 | 16313.1125 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.7304 | 19.9666 | 19866.6242 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.7304 | 19.7392 | 19639.2416 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.7304 | 19.9484 | 19848.3607 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.7304 | 20.0022 | 19902.2335 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.4774 | 64.7189 | 64618.866 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.4774 | 63.0141 | 62914.0687 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.4774 | 56.2829 | 56182.9088 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 42.4436 | 16.1265 | 16026.4789 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 24.3356 | 2.3612 | 2261.174 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 24.3356 | 2.3048 | 2204.8209 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 36.5816 | 2.1895 | 2089.4988 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 36.5816 | 2.249 | 214903% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.4626 | 16.412 | 16312.0459 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.7348 | 19.9678 | 1986778% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.7348 | 19.7404 | 19640.3755 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.7348 | 19.9495 | 19849.5092 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.7348 | 20.0034 | 19903.3868 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.4778 | 64.7082 | 64608.2476 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.4778 | 63.0039 | 62903.944 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.4778 | 56.2757 | 56175.7304 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 42.4821 | 16.1241 | 16024.1075 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 24.5738 | 2.3571 | 2257.1452 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 24.5738 | 2.3001 | 2200.1176 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 36.6029 | 2.1899 | 2089.8532 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 36.6029 | 2.2494 | 2149.3894 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.4651 | 16.4168 | 16316.8435 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.7805 | 20.0211 | 19921.0517 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.7805 | 19.7926 | 19692.5989 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.7805 | 20.0027 | 19902.6637 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.7805 | 20.0568 | 19956.7787 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.483 | 64.7518 | 64651.7602 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.483 | 63.0428 | 62942.8339 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.483 | 56.3152 | 56215.2133 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 42.4128 | 16.1276 | 16027.6282 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 24.1549 | 2.3633 | 2263.3067 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 24.1549 | 2.307 | 2206.9925 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 36.6026 | 2.199 | 2099.0058 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 36.6026 | 2.2589 | 2158.9031 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.4654 | 16.4182 | 16318.219 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.7929 | 20.0361 | 19936.1465 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.7929 | 19.8074 | 19707.3938 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.7929 | 20.0177 | 19917.7235 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.7929 | 20.0719 | 19971.9064 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.4844 | 64.765 | 64665.0089 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.4844 | 63.0547 | 62954.7467 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.4844 | 56.327 | 56226.9835 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 42.3783 | 16.1288 | 16028.82 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 23.9949 | 2.3649 | 2264.8717 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 23.9949 | 2.3089 | 2208.8898 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 36.5978 | 2.2014 | 2101.3577 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 36.5978 | 2.2613 | 2161.3486 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.4615 | 16.4118 | 16311.7515 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.7287 | 19.9633 | 19863.3341 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.7287 | 19.736 | 19636.0195 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.7287 | 19.9451 | 19845.0784 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.7287 | 19.9989 | 19898.937 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.4771 | 64.7113 | 64611.2752 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.4771 | 63.007 | 62907.0335 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.4771 | 56.277 | 56176.9992 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 42.4698 | 16.1248 | 16024.7714 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 24.4256 | 2.359 | 2258.9631 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 24.4256 | 2.3024 | 2202.3569 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 36.5957 | 2.189 | 2089.0393 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 36.5957 | 2.2485 | 2148.5461 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 10.4627 | 16.412 | 16311.9627 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 15.6705 | 19.971 | 19870.953 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 15.6705 | 19.7434 | 19643.4365 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 15.6705 | 19.9527 | 19852.6815 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 15.6705 | 20.0066 | 19906.5938 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.4728 | 64.8344 | 64734.4109 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.4728 | 63.1245 | 63024.5173 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.4728 | 56.3641 | 56264.1388 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 42.4887 | 16.1243 | 16024.3352 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 24.367 | 2.359 | 2259.0074 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 24.367 | 2.3022 | 2202.156 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 36.5471 | 2.19 | 2090.049 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 36.5471 | 2.2496 | 2149.6003 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.4611 | 16.4115 | 16311.4689 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.7374 | 19.9708 | 19870.828 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.7374 | 19.7434 | 19643.3684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.7374 | 19.9526 | 19852.555 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.7374 | 20.0064 | 19906.4447 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.4782 | 64.711 | 64610.9834 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.4782 | 63.0063 | 62906.3075 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.4782 | 56.2783 | 56178.3161 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 42.4459 | 16.1238 | 16023.7987 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 24.2707 | 2.3566 | 2256.6447 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 24.2707 | 2.2998 | 2199.8079 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 36.5852 | 2.1887 | 2088.7351 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 36.5852 | 2.2482 | 2148.2287 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.4626 | 16.412 | 16312.0477 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.7348 | 19.9678 | 19867.7763 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.7348 | 19.7404 | 19640.3752 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.7348 | 19.9495 | 19849.5088 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.7348 | 20.0034 | 19903.3865 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.4778 | 64.7082 | 64608.2466 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.4778 | 63.0039 | 62903.943 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.4778 | 56.2757 | 56175.7295 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 42.4822 | 16.1241 | 16024.1099 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 24.5738 | 2.3571 | 2257.1464 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 24.5738 | 2.3001 | 2200.1186 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 36.6029 | 2.1899 | 2089.8536 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 36.6029 | 2.2494 | 2149.3898 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.4627 | 16.412 | 16312.0352 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 14.0226 | 19.9806 | 19880.5816 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 14.0226 | 19.7537 | 19653.6952 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 14.0226 | 19.9623 | 19862.3259 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 14.0226 | 20.016 | 19916 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.7072 | 45.6853 | 45585.3096 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.7072 | 45.5619 | 45461.9251 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.7072 | 53.7115 | 53611.4617 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 42.4973 | 16.124 | 16024.0217 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 24.5843 | 2.3581 | 2258.0864 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 24.5843 | 2.3011 | 2201.1072 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 36.599 | 2.1901 | 2090.1018 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 36.599 | 2.2496 | 2149.646 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 10.4626 | 16.412 | 16311.9736 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7339 | 19.9671 | 19867.0732 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7339 | 19.7397 | 19639.6874 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7339 | 19.9488 | 19848.8088 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7339 | 20.0027 | 19902.6819 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4777 | 64.7077 | 64607.6628 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4777 | 63.0033 | 62903.3274 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4777 | 56.2751 | 56175.1145 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 42.497 | 16.124 | 16024.0048 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 24.5842 | 2.358 | 2258.0475 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 24.5842 | 2.3011 | 2201.0728 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 36.6024 | 2.1899 | 2089.8809 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 36.6024 | 2.2494 | 2149.4186 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.4606 | 16.4123 | 16312.2953 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.695 | 19.9352 | 19835.2392 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.695 | 19.7085 | 19608.475 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.695 | 19.917 | 19817.0473 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.695 | 19.9708 | 19870.7819 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.4743 | 64.7032 | 64603.1951 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.4743 | 63.0006 | 62900.5591 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.4743 | 56.2673 | 56167.3374 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 42.4711 | 16.1243 | 16024.2773 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 24.5607 | 2.3574 | 2257.4312 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 24.5607 | 2.3005 | 2200.5459 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 36.3521 | 2.1838 | 2083.8301 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 36.3521 | 2.2431 | 2143.1441 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.4596 | 16.4129 | 16312.922 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 15.6439 | 19.9346 | 19834.6412 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 15.6439 | 19.7079 | 19607.8524 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 15.6439 | 19.9165 | 19816.453 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 15.6439 | 19.9702 | 19870.1996 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.472 | 64.743 | 64643.0267 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.472 | 63.039 | 62938.9896 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.472 | 56.2939 | 56193.935 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 42.4529 | 16.1247 | 16024.7099 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 24.5424 | 2.3575 | 2257.4984 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 24.5424 | 2.3006 | 2200.6469 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 36.1975 | 2.1838 | 2083.802 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 36.1975 | 2.2431 | 2143.1238 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.4624 | 16.4123 | 16312.311 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.7275 | 19.9688 | 19868.7925 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.7275 | 19.7414 | 19641.361 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.7275 | 19.9505 | 19850.5238 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.7275 | 20.0044 | 19904.4098 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.4773 | 64.7343 | 64634.2595 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.4773 | 63.0287 | 62928.7252 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.4773 | 56.294 | 56194.009 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 42.4937 | 16.1239 | 16023.8998 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 24.5815 | 2.3576 | 2257.6015 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 24.5815 | 2.3007 | 2200.6607 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 36.3607 | 2.1874 | 2087.3947 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 36.3607 | 2.2469 | 2146.8645 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.4549 | 16.4129 | 16312.8923 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.7704 | 20.0282 | 19928.1686 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.7704 | 19.7996 | 19699.5527 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.7704 | 20.0098 | 19909.7643 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.7704 | 20.0639 | 19963.9212 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.4817 | 64.7899 | 64689.8547 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.4817 | 63.0794 | 62979.354 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.4817 | 56.3413 | 56241.2859 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 42.4051 | 16.1255 | 16025.5366 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 24.4996 | 2.3567 | 2256.722 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 24.4996 | 2.3001 | 2200.1023 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 35.8386 | 2.1783 | 2078.3487 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 35.8386 | 2.2375 | 2137.5452 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.4606 | 16.4131 | 16313.1382 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5733 | 19.9701 | 19870.1132 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5733 | 19.7425 | 19642.5033 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5733 | 19.9519 | 19851.8501 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5733 | 20.0058 | 19905.8025 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4672 | 65.0632 | 64963.1903 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4672 | 63.3438 | 63243.7665 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4672 | 56.523 | 56422.9531 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 42.4881 | 16.124 | 16024.0238 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 24.5747 | 2.3576 | 2257.6166 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 24.5747 | 2.3007 | 2200.722 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 36.3109 | 2.1859 | 2085.8571 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 36.3109 | 2.2453 | 2145.2975 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.4621 | 16.4119 | 16311.9473 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.7349 | 19.9679 | 19867.9437 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.7349 | 19.7405 | 19640.5408 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.7349 | 19.9497 | 19849.6774 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.7349 | 20.0036 | 19903.5543 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.4778 | 64.7085 | 64608.5339 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.4778 | 63.0042 | 62904.1523 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.4778 | 56.2759 | 56175.9329 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 42.4962 | 16.124 | 16023.9995 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 24.584 | 2.358 | 2258.0033 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 24.584 | 2.301 | 2201.0337 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 36.5989 | 2.19 | 2090.0046 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 36.5989 | 2.2495 | 2149.546 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.4622 | 16.412 | 16311.9547 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.7349 | 19.9679 | 19867.9491 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.7349 | 19.7405 | 1964055% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.7349 | 19.9497 | 19849.6813 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.7349 | 20.0036 | 1990356% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.4778 | 64.7085 | 64608.538 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.4778 | 63.0042 | 62904.1561 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.4778 | 56.2759 | 56175.9361 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 42.4963 | 16.124 | 16024.0025 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 24.5841 | 2.358 | 2258.0078 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 24.5841 | 2.301 | 2201.0376 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 36.5992 | 2.19 | 2089.994 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 36.5992 | 2.2495 | 2149.5348 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 10.464 | 16.4136 | 16313.5751 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 15.3676 | 20.1514 | 20051.4138 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 15.3676 | 19.9198 | 19819.8115 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 15.3676 | 20.1328 | 20032.7532 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 15.3676 | 20.1877 | 20087.6783 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.4594 | 66.209 | 66108.9918 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.4594 | 64.4298 | 64329.8262 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.4594 | 57.3523 | 57252.2837 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 42.5005 | 16.1248 | 16024.7886 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 24.5792 | 2.3593 | 2259.3401 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 24.5792 | 2.3023 | 2202.3057 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 36.5931 | 2.1976 | 2097.598 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 36.5931 | 2.2574 | 2157.4419 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.4626 | 16.412 | 16312.023 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 15.6451 | 19.9721 | 19872.1286 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 15.6451 | 19.7446 | 19644.6428 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 15.6451 | 19.9539 | 19853.8542 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 15.6451 | 20.0078 | 19907.7515 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.4747 | 64.7697 | 64669.7215 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.4747 | 63.0625 | 62962.4599 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.4747 | 56.3202 | 56220.2007 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 42.4963 | 16.124 | 16024.0307 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 24.583 | 2.3581 | 2258.0705 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 24.583 | 2.3011 | 2201.0961 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 36.5953 | 2.19 | 2090.0391 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 36.5953 | 2.2496 | 2149.5833 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.4604 | 16.4102 | 16310.1769 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 15.5466 | 19.8461 | 19746.0704 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 15.5466 | 19.621 | 19521.0477 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 15.5466 | 19.8281 | 19728.0839 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 15.5466 | 19.8814 | 19781.4306 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.4585 | 64.6863 | 64586.2735 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.4585 | 62.9917 | 62891.6787 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.4585 | 56.231 | 56130.9948 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 42.4881 | 16.1234 | 16023.4165 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 24.58 | 2.3569 | 2256.8663 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 24.58 | 2.3 | 2199.9714 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 36.5628 | 2.1824 | 2082.3782 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 36.5628 | 2.2416 | 2141.6265 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.4628 | 16.4123 | 16312.3262 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.7114 | 19.9631 | 19863.0768 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.7114 | 19.7358 | 19635.7733 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.7114 | 19.9448 | 19844.8212 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.7114 | 19.9987 | 19898.676 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.4767 | 64.7272 | 64627.2373 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.4767 | 63.0223 | 62922.3147 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.4767 | 56.2885 | 56188.4731 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 42.4927 | 16.1242 | 16024.1575 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 24.5725 | 2.3582 | 2258.2425 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 24.5725 | 2.3013 | 2201.2763 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 36.5945 | 2.1904 | 2090.384 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 36.5945 | 2.2499 | 2149.9423 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.4627 | 16.412 | 16312.0085 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.6998 | 19.9688 | 19868.7784 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.6998 | 19.7414 | 19641.3561 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.6998 | 19.9505 | 19850.511 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.6998 | 20.0044 | 19904.3931 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.4772 | 64.7066 | 64606.5911 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.4772 | 63.0025 | 62902.5251 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.4772 | 56.2739 | 56173.9096 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 42.4969 | 16.124 | 16024.0203 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 24.5839 | 2.3581 | 2258.0676 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 24.5839 | 2.3011 | 2201.0926 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 36.6006 | 2.19 | 2089.9721 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 36.6006 | 2.2495 | 2149.5131 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.4627 | 16.412 | 16312.0094 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.7033 | 19.9687 | 19868.6926 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.7033 | 19.7413 | 19641.272 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.7033 | 19.9504 | 19850.4254 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.7033 | 20.0043 | 19904.3069 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.4773 | 64.7068 | 64606.8425 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.4773 | 63.0028 | 62902.7661 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.4773 | 56.2741 | 56174.1399 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 42.497 | 16.124 | 16024.0193 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 24.5839 | 2.3581 | 2258.0677 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 24.5839 | 2.3011 | 2201.0926 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 36.6008 | 2.19 | 2089.9737 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 36.6008 | 2.2495 | 2149.5149 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 10.4627 | 16.412 | 16312.0199 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.7075 | 19.9613 | 19861.3059 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.7075 | 19.7341 | 19634.1343 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.7075 | 19.9431 | 19843.0514 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.7075 | 19.9969 | 19896.8604 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.4503 | 59.7526 | 59652.6481 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.4503 | 58.2598 | 58159.8466 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.4503 | 52.754 | 52653.9985 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 42.4966 | 16.124 | 16023.9921 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 24.5838 | 2.358 | 2258.023 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 24.5838 | 2.301 | 2201.0491 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 36.5987 | 2.1898 | 2089.756 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 36.5987 | 2.2493 | 2149.288 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 10.4631 | 16.4124 | 16312.4102 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7629 | 20.0423 | 19942.2811 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7629 | 19.813 | 19713.0251 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7629 | 20.0239 | 19923.8596 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7629 | 20.0782 | 19978.2213 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 42.5002 | 16.1243 | 16024.2681 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 24.5853 | 2.3585 | 2258.5011 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 24.5853 | 2.3015 | 2201.5028 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 36.6153 | 2.1929 | 2092.8546 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 36.6153 | 2.2525 | 2152.5099 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 10.4628 | 16.4121 | 16312.0679 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.7252 | 19.9751 | 19875.1403 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.7252 | 19.7476 | 19647.5684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.7252 | 19.9569 | 19856.859 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.7252 | 20.0108 | 19910.7782 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.4666 | 65.3089 | 65208.8599 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.4666 | 63.5772 | 63477.1932 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.4666 | 56.7 | 56600.0093 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 42.4976 | 16.124 | 16024.0475 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 24.5844 | 2.3581 | 2258.1202 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 24.5844 | 2.3011 | 2201.1417 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 36.6033 | 2.1903 | 2090.3194 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 36.6033 | 2.2499 | 2149.874 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0065 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7353 | 19.9681 | 19868.0882 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7353 | 19.7407 | 19640.6826 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7353 | 19.9498 | 19849.8218 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7353 | 20.0037 | 19903.6991 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.4568 | 65.6003 | 65500.339 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.4568 | 63.8564 | 63756.3964 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.4568 | 56.9037 | 56803.7286 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 42.4974 | 16.124 | 16024.0165 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 24.5844 | 2.3581 | 2258.0686 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 24.5844 | 2.3011 | 2201.0927 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 36.6031 | 2.19 | 2089.9928 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 36.6031 | 2.2495 | 2149.5348 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 10.4627 | 16.412 | 16312.0065 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.7353 | 19.9681 | 19868.0882 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.7353 | 19.7407 | 19640.6826 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.7353 | 19.9498 | 19849.8218 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.7353 | 20.0037 | 19903.6991 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.4568 | 65.6003 | 65500.339 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.4568 | 63.8564 | 63756.3964 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.4568 | 56.9037 | 56803.7286 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 42.4974 | 16.124 | 16024.0165 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 24.5844 | 2.3581 | 2258.0686 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 24.5844 | 2.3011 | 2201.0927 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 36.6031 | 2.19 | 2089.9928 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 36.6031 | 2.2495 | 2149.5348 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 10.4626 | 16.412 | 16312.0022 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.7186 | 19.9667 | 19866.721 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.7186 | 19.7393 | 19639.3338 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.7186 | 19.9485 | 19848.4569 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.7186 | 20.0023 | 19902.3331 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.4354 | 65.4307 | 65330.7074 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.4354 | 63.6966 | 63596.5685 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.4354 | 56.7871 | 56687.0556 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 42.4968 | 16.124 | 16024.0118 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 24.584 | 2.3581 | 2258.0535 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 24.584 | 2.3011 | 2201.0791 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 36.6005 | 2.1899 | 2089.864 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 36.6005 | 2.2494 | 2149.4011 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0171 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.7177 | 19.97 | 19869.996 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.7177 | 19.7425 | 19642.5407 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.7177 | 19.9517 | 19851.7257 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.7177 | 20.0056 | 19905.6163 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.4478 | 65.2841 | 65184.0663 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.4478 | 63.5551 | 63455.0989 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.4478 | 56.6851 | 56585.1497 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 42.4972 | 16.124 | 16024.0211 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 24.5842 | 2.3581 | 2258.0714 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 24.5842 | 2.3011 | 2201.0958 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 36.6015 | 2.19 | 2090.0097 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 36.6015 | 2.2496 | 2149.5524 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 10.4625 | 16.412 | 16312.006 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.7251 | 19.9646 | 19864.5674 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.7251 | 19.7373 | 19637.2531 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.7251 | 19.9463 | 19846.3071 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.7251 | 20.0002 | 19900.1609 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.4571 | 64.1462 | 64046.2243 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.4571 | 62.4699 | 62369.8883 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.4571 | 55.8782 | 55778.2186 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 42.4967 | 16.124 | 16024.0157 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 24.5839 | 2.3581 | 2258.067 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 24.5839 | 2.3011 | 2201.0908 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 36.6013 | 2.19 | 2089.953 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 36.6013 | 2.2495 | 2149.4932 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 10.4627 | 16.4121 | 16312.0585 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.6395 | 19.9806 | 19880.5967 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.6395 | 19.7529 | 19652.9094 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.6395 | 19.9623 | 19862.305 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.6395 | 20.0163 | 19916.2543 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.478 | 64.736 | 64635.9669 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.478 | 63.0303 | 62930.2812 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.478 | 56.2953 | 56195.3493 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 42.4971 | 16.124 | 16024.0332 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 24.584 | 2.3581 | 225809% | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 24.584 | 2.3011 | 2201.1125 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 36.5994 | 2.1901 | 2090.1435 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 36.5994 | 2.2497 | 2149.6914 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0039 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 15.6253 | 19.9835 | 19883.4619 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 15.6253 | 19.7557 | 19655.7003 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 15.6253 | 19.9652 | 19865.1638 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 15.6253 | 20.0191 | 19919.1342 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.458 | 65.2691 | 65169.1292 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.458 | 63.5393 | 63439.333 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.458 | 56.6765 | 56576.4802 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 42.4973 | 16.124 | 16024.0158 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 24.5843 | 2.3581 | 2258.0692 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 24.5843 | 2.3011 | 2201.0935 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 36.6028 | 2.19 | 2089.9918 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 36.6028 | 2.2495 | 2149.5336 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 10.4627 | 16.412 | 16311.9945 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.7307 | 19.9663 | 19866.2869 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.7307 | 19.7389 | 19638.9164 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.7307 | 19.948 | 19848.0243 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.7307 | 20.0019 | 19901.8936 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4775 | 64.6905 | 64590.4767 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4775 | 62.9871 | 62887.0638 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4775 | 56.2628 | 56162.8445 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 42.4973 | 16.124 | 16024.0137 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 24.5844 | 2.3581 | 2258.0618 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 24.5844 | 2.3011 | 2201.0863 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 36.6025 | 2.1899 | 2089.9354 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 36.6025 | 2.2495 | 2149.4751 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0023 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 15.6468 | 19.9828 | 19882.7665 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 15.6468 | 19.755 | 19654.9572 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 15.6468 | 19.9645 | 19864.4711 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 15.6468 | 20.0185 | 19918.4606 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.4614 | 65.4303 | 65330.3343 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.4614 | 63.6935 | 63593.4824 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.4614 | 56.7856 | 56685.5681 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 42.4973 | 16.124 | 16024.0155 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 24.5844 | 2.3581 | 2258.0667 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 24.5844 | 2.3011 | 2201.0909 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 36.6029 | 2.19 | 2089.971 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 36.6029 | 2.2495 | 2149.5121 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 10.4627 | 16.412 | 16311.9955 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.735 | 19.9664 | 19866.4337 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.735 | 19.7391 | 19639.0621 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.735 | 19.9482 | 19848.1695 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.735 | 20.002 | 19902.0404 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.4775 | 64.6889 | 64588.8687 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.4775 | 62.9857 | 62885.66 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.4775 | 56.2612 | 56161.2215 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 42.4973 | 16.124 | 16024.0131 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 24.5843 | 2.3581 | 2258.063 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 24.5843 | 2.3011 | 2201.0875 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 36.6029 | 2.1899 | 2089.9486 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 36.6029 | 2.2495 | 2149.4887 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 10.4627 | 16.412 | 16311.9947 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.735 | 19.9663 | 19866.3249 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.735 | 19.739 | 19638.9557 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.735 | 19.9481 | 19848.0627 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.735 | 20.0019 | 19901.9313 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.4775 | 64.6873 | 64587.3476 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.4775 | 62.9842 | 62884.1836 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.4775 | 56.2601 | 56160.0751 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 42.4973 | 16.124 | 16024.0129 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 24.5843 | 2.3581 | 2258.0627 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 24.5843 | 2.3011 | 2201.0871 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 36.6029 | 2.1899 | 2089.946 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 36.6029 | 2.2495 | 2149.4858 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 10.4626 | 16.412 | 16311.9862 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.5682 | 19.9682 | 19868.1701 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.5682 | 19.7408 | 19640.8428 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.5682 | 19.9499 | 19849.9044 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.5682 | 20.0038 | 19903.7558 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4474 | 65.0283 | 64928.293 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4474 | 63.3108 | 63210.7766 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.4474 | 56.5068 | 56406.8187 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 42.4971 | 16.124 | 16024.0132 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 24.5843 | 2.3581 | 2258.0616 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 24.5843 | 2.3011 | 2201.0863 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 36.6024 | 2.1899 | 2089.9217 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 36.6024 | 2.2495 | 2149.4607 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 10.4626 | 16.412 | 16311.9726 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.7334 | 19.9595 | 19859.4882 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.7334 | 19.7323 | 19632.2932 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.7334 | 19.9412 | 19841.2403 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.7334 | 19.9951 | 19895.0644 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.4771 | 64.5106 | 64410.5552 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.4771 | 62.8159 | 62715.8655 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.4771 | 56.1343 | 56034.293 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 42.497 | 16.124 | 16024.0034 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 24.5842 | 2.358 | 2258.0439 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 24.5842 | 2.3011 | 2201.0693 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 36.6022 | 2.1898 | 2089.8113 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 36.6022 | 2.2493 | 2149.3458 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.4599 | 16.4141 | 16314.0511 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5429 | 19.9753 | 19875.328 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5429 | 19.7476 | 19647.5811 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5429 | 19.9571 | 19857.0543 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5429 | 20.011 | 19911.042 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.4581 | 65.3546 | 65254.5518 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.4581 | 63.6221 | 63522.1449 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.4581 | 56.7272 | 56627.2151 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 42.4696 | 16.125 | 16025.0434 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 24.5641 | 2.3581 | 2258.0907 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 24.5641 | 2.3012 | 2201.1956 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 36.0159 | 2.1899 | 2089.8763 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 36.0159 | 2.2495 | 2149.474 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.462 | 16.4124 | 16312.4181 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5603 | 19.9812 | 19881.1808 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5603 | 19.7534 | 19653.4012 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5603 | 19.9629 | 19862.8911 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 15.5603 | 20.0169 | 19916.875 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4683 | 65.0456 | 64945.648 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4683 | 63.326 | 63225.9541 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.4683 | 56.5147 | 56414.6974 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 42.481 | 16.1247 | 16024.6676 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 24.5609 | 2.3587 | 2258.6877 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 24.5609 | 2.3017 | 2201.7138 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 36.048 | 2.1977 | 2097.7228 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 36.048 | 2.2576 | 2157.5865 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.4615 | 16.4137 | 16313.7326 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.6822 | 19.9661 | 19866.0688 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.6822 | 19.7387 | 19638.684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.6822 | 19.9478 | 19847.8081 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.6822 | 20.0017 | 19901.6859 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4748 | 64.7766 | 64676.5512 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4748 | 63.0695 | 62969.4769 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4748 | 56.323 | 56223.0289 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 42.4827 | 16.1246 | 16024.6471 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 24.5645 | 2.3583 | 2258.3364 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 24.5645 | 2.3014 | 2201.423 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 36.5991 | 2.1872 | 2087.218 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 36.5991 | 2.2467 | 2146.6501 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.4622 | 16.4116 | 16311.5655 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.7268 | 19.973 | 19872.965 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.7268 | 19.7455 | 19645.4606 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.7268 | 19.9547 | 19854.6883 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.7268 | 20.0086 | 19908.5893 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.4778 | 64.7295 | 64629.4803 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.4778 | 63.0238 | 62923.849 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.4778 | 56.2918 | 56191.7849 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 42.4961 | 16.1242 | 16024.2091 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 24.5813 | 2.3584 | 2258.418 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 24.5813 | 2.3014 | 2201.4183 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 36.5396 | 2.1942 | 2094.1965 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 36.5396 | 2.2539 | 2153.8946 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 10.4626 | 16.4119 | 16311.943 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7242 | 19.9555 | 19855.5415 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7242 | 19.7284 | 19628.446 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7242 | 19.9373 | 19837.3017 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.7242 | 19.9911 | 19891.1011 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.4693 | 56.7914 | 56691.3701 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.4693 | 55.4308 | 55330.8478 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.4693 | 50.524 | 50423.9649 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 42.4969 | 16.124 | 16023.9883 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 24.5842 | 2.358 | 2258.0146 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 24.5842 | 2.301 | 2201.0417 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 36.6008 | 2.1896 | 2089.607 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 36.6008 | 2.2491 | 2149.1337 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.4618 | 16.4131 | 16313.121 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.6394 | 20.2055 | 20105.5109 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.6394 | 19.9715 | 19871.45 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.6394 | 20.1869 | 20086.9262 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.6394 | 20.2427 | 20142.7157 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4529 | 65.3771 | 65277.1074 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4529 | 63.6458 | 63545.8452 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.4529 | 56.7355 | 56635.5267 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 42.4855 | 16.1245 | 16024.4572 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5732 | 2.3582 | 2258.2087 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5732 | 2.3013 | 2201.2705 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.4149 | 2.1905 | 2090.4627 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.4149 | 2.2501 | 2150.0517 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0084 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.5938 | 19.9851 | 19885.0817 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.5938 | 19.7572 | 19657.1759 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.5938 | 19.9668 | 19866.7838 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.5938 | 20.0208 | 19920.8032 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.4564 | 65.3194 | 65219.3525 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.4564 | 63.5883 | 63488.3412 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.4564 | 56.7063 | 56606.2523 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 42.4969 | 16.124 | 16024.0194 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 24.584 | 2.3581 | 2258.0593 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 24.584 | 2.3011 | 2201.0848 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 36.5947 | 2.1899 | 2089.9138 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 36.5947 | 2.2495 | 2149.4534 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 10.4627 | 16.412 | 16312.0033 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 15.6052 | 19.9736 | 19873.6116 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 15.6052 | 19.7461 | 19646.0505 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 15.6052 | 19.9553 | 19855.3364 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 15.6052 | 20.0093 | 19909.259 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.4585 | 64.933 | 64833.0242 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.4585 | 63.2198 | 63119.7555 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.4585 | 56.435 | 56334.9632 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 42.4969 | 16.124 | 16024.0168 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 24.584 | 2.3581 | 2258.059 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 24.584 | 2.3011 | 220108% | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 36.5953 | 2.1899 | 2089.9053 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 36.5953 | 2.2494 | 214944% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 10.4627 | 16.4119 | 16311.9481 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 15.6542 | 19.9665 | 19866.5274 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 15.6542 | 19.7391 | 19639.1127 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 15.6542 | 19.9483 | 19848.2686 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 15.6542 | 20.0022 | 19902.1564 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.4639 | 64.9482 | 64848.1746 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.4639 | 63.2352 | 63135.1624 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.4639 | 56.4427 | 56342.6538 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 42.4972 | 16.124 | 16024.0043 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 24.5844 | 2.358 | 2258.0341 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 24.5844 | 2.3011 | 2201.0614 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 36.6019 | 2.1897 | 2089.698 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 36.6019 | 2.2492 | 2149.2291 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 10.4628 | 16.4121 | 16312.0898 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.7232 | 19.9655 | 19865.4541 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.7232 | 19.7382 | 19638.1867 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.7232 | 19.9472 | 19847.191 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.7232 | 20.001 | 19901.0242 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.4779 | 64.4752 | 64375.1903 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.4779 | 62.7806 | 62680.6128 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.4779 | 56.1154 | 56015.3683 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 42.4969 | 16.124 | 16024.0107 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 24.5839 | 2.3581 | 2258.0641 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 24.5839 | 2.3011 | 2201.0868 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 36.6002 | 2.1901 | 2090.0817 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 36.6002 | 2.2496 | 2149.6257 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.4616 | 16.4111 | 16311.0954 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3025 | 20.5558 | 20455.846 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3025 | 20.3114 | 20211.4497 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3025 | 20.5366 | 20436.6323 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3025 | 20.5953 | 20495.3331 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.3362 | 71.2078 | 71107.8129 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.3362 | 69.2061 | 69106.1431 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.3362 | 60.7138 | 60613.7812 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 42.4943 | 16.1238 | 16023.8031 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5836 | 2.3576 | 2257.6348 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 24.5836 | 2.3007 | 2200.6869 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.5763 | 2.1874 | 2087.3638 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 36.5763 | 2.2468 | 2146.806 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 10.4565 | 16.4159 | 16315.8675 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.7347 | 19.968 | 19868.016 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.7347 | 19.7406 | 19640.6105 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.7347 | 19.9497 | 19849.7497 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.7347 | 20.0036 | 19903.6285 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.4778 | 64.71 | 64610.0498 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.4778 | 63.0056 | 62905.6153 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.4778 | 56.277 | 56176.9672 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 41.7225 | 16.1443 | 16044.3324 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 24.5619 | 2.3569 | 2256.9454 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 24.5619 | 2.3002 | 2200.1913 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 36.5854 | 2.1898 | 2089.7868 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 36.5854 | 2.2493 | 2149.3251 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 10.4615 | 16.4136 | 16313.5776 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.7351 | 19.9692 | 19869.2091 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.7351 | 19.7418 | 19641.7795 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.7351 | 19.9509 | 19850.94 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.7351 | 20.0048 | 19904.8228 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.4778 | 64.7125 | 64612.4678 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.4778 | 63.0078 | 62907.8196 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.4778 | 56.2789 | 56178.8844 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 42.2074 | 16.1272 | 16027.1743 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 24.5354 | 2.3577 | 2257.7271 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 24.5354 | 2.3007 | 2200.7302 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 36.601 | 2.1898 | 2089.7848 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 36.601 | 2.2493 | 2149.3184 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 10.4626 | 16.412 | 16311.9981 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.732 | 19.9684 | 19868.4374 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.732 | 19.741 | 19641.0252 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.732 | 19.9502 | 19850.1685 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.732 | 20.004 | 19904.049 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.4774 | 64.7094 | 64609.3893 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.4774 | 63.005 | 62904.9535 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.4774 | 56.2766 | 56176.6323 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 42.4969 | 16.124 | 16024.0154 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 24.5839 | 2.3581 | 2258.0645 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 24.5839 | 2.3011 | 2201.0887 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 36.6018 | 2.19 | 2089.9959 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 36.6018 | 2.2495 | 2149.538 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0284 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.732 | 19.9678 | 19867.8442 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.732 | 19.7404 | 19640.4434 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.732 | 19.9496 | 19849.577 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.732 | 20.0035 | 19903.4546 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.4775 | 64.7085 | 64608.5418 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.4775 | 63.0042 | 62904.1557 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.4775 | 56.2759 | 56175.8941 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 42.4972 | 16.124 | 16024.0227 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 24.5841 | 2.3581 | 2258.0802 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 24.5841 | 2.3011 | 2201.1039 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 36.6024 | 2.19 | 2090.0192 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 36.6024 | 2.2496 | 2149.5622 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 10.4626 | 16.4119 | 16311.9413 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.7329 | 19.9661 | 19866.0567 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.7329 | 19.7387 | 19638.6912 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.7329 | 19.9478 | 19847.7947 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.7329 | 20.0017 | 19901.6646 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.4776 | 64.7066 | 64606.6088 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.4776 | 63.0024 | 62902.3947 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.4776 | 56.2742 | 56174.2004 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 42.497 | 16.124 | 16023.9946 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 24.5842 | 2.358 | 2258.0272 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 24.5842 | 2.3011 | 2201.0536 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 36.602 | 2.1898 | 2089.7736 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 36.602 | 2.2493 | 2149.3068 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 10.463 | 16.4123 | 16312.2818 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7432 | 19.9768 | 19876.7571 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7432 | 19.7492 | 19649.1794 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7432 | 19.9585 | 19858.4705 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.7432 | 20.0124 | 19912.387 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4788 | 64.7171 | 64617.0981 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4788 | 63.0119 | 62911.8796 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.4788 | 56.2836 | 56183.5799 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 42.4986 | 16.1241 | 16024.111 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 24.5848 | 2.3582 | 2258.2427 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 24.5848 | 2.3013 | 2201.2564 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 36.6073 | 2.1909 | 2090.9166 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 36.6073 | 2.2505 | 2150.4941 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 10.4617 | 16.413 | 16312.9839 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 15.6655 | 19.9973 | 19897.2789 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 15.6655 | 19.7692 | 19669.1818 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 15.6655 | 19.979 | 19878.9503 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 15.6655 | 20.033 | 19933.0053 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.4744 | 64.9631 | 64863.0672 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.4744 | 63.2467 | 63146.6922 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.4744 | 56.4573 | 56357.344 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 42.487 | 16.1246 | 16024.5979 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 24.5721 | 2.3584 | 2258.4414 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 24.5721 | 2.3015 | 2201.4986 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 36.4571 | 2.192 | 2092.0206 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 36.4571 | 2.2517 | 2151.6705 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 10.4625 | 16.4127 | 16312.7211 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.7659 | 20.0034 | 19903.4259 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.7659 | 19.7752 | 19675.2166 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.7659 | 19.9851 | 19885.0824 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.7659 | 20.0392 | 19939.1604 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.4799 | 64.9283 | 64828.2808 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.4799 | 63.2132 | 63113.1984 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.4799 | 56.4337 | 56333.7113 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 42.5 | 16.1246 | 16024.5516 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 24.5862 | 2.3585 | 2258.4953 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 24.5862 | 2.3015 | 2201.5409 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 36.6266 | 2.1927 | 2092.7 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 36.6266 | 2.2524 | 2152.3739 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 10.4629 | 16.4121 | 16312.135 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.7334 | 19.9664 | 19866.4141 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.7334 | 19.739 | 19639.0398 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.7334 | 19.9481 | 19848.1497 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.7334 | 20.002 | 19902.0213 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.4776 | 64.7075 | 64607.5285 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.4776 | 63.0033 | 62903.2585 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.4776 | 56.275 | 56174.993 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 42.498 | 16.1241 | 16024.0813 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 24.5844 | 2.3582 | 2258.2192 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 24.5844 | 2.3012 | 2201.2304 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 36.6046 | 2.1912 | 2091.2341 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 36.6046 | 2.2508 | 2150.8206 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 10.4629 | 16.4121 | 16312.1345 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.7334 | 19.9664 | 19866.4147 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.7334 | 19.739 | 19639.0404 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.7334 | 19.9482 | 19848.1504 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.7334 | 20.002 | 19902.0219 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.4776 | 64.7075 | 64607.5293 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.4776 | 63.0033 | 62903.2592 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.4776 | 56.275 | 56174.9936 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 42.498 | 16.1241 | 16024.081 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 24.5844 | 2.3582 | 2258.2187 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 24.5844 | 2.3012 | 2201.2299 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 36.6046 | 2.1912 | 2091.2305 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 36.6046 | 2.2508 | 2150.8169 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 10.4626 | 16.412 | 16311.9504 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.7341 | 19.9672 | 19867.1566 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.7341 | 19.7398 | 19639.7691 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.7341 | 19.9489 | 19848.8921 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.7341 | 20.0028 | 19902.7656 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.4777 | 64.708 | 64607.9945 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.4777 | 63.0037 | 62903.7003 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.4777 | 56.2754 | 56175.4379 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 42.4965 | 16.124 | 16023.9936 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 24.5838 | 2.358 | 2258.0181 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 24.5838 | 2.301 | 2201.0442 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 36.5991 | 2.1896 | 2089.5671 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 36.5991 | 2.2491 | 2149.0911 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 10.4623 | 16.4117 | 16311.6976 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.73 | 19.963 | 19862.9861 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.73 | 19.7357 | 19635.6792 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.73 | 19.9447 | 19844.7296 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.73 | 19.9986 | 19898.586 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.4773 | 64.7055 | 64605.5466 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.4773 | 63.0015 | 62901.5487 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.4773 | 56.273 | 56173.0393 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 42.4947 | 16.1239 | 16023.8859 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 24.5826 | 2.3578 | 2257.7931 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 24.5826 | 2.3008 | 2200.8279 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 36.5827 | 2.1877 | 2087.6764 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 36.5827 | 2.2471 | 2147.1219 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.4607 | 16.4108 | 16310.7582 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7327 | 19.9689 | 1986887% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7327 | 19.7414 | 19641.4468 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7327 | 19.9506 | 1985060% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7327 | 20.0045 | 19904.4875 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 64.7173 | 64617.3288 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 63.0126 | 62912.5507 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 56.2821 | 56182.1366 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 41.9044 | 16.1357 | 16035.7139 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 21.8732 | 2.3583 | 2258.2676 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 21.8732 | 2.3049 | 2204.9478 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 36.4615 | 2.1915 | 2091.5345 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 36.4615 | 2.2512 | 2151.151 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 10.4593 | 16.4106 | 16310.5787 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.7327 | 19.9661 | 19866.0652 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.7327 | 19.7387 | 19638.6973 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.7327 | 19.9478 | 19847.8017 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.7327 | 20.0017 | 19901.6717 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4775 | 64.7072 | 64607.1573 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4775 | 63.003 | 62902.9555 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4775 | 56.2745 | 56174.5221 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 42.1235 | 16.1296 | 16029.6027 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 20.9106 | 2.3707 | 2270.7305 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 20.9106 | 2.3169 | 2216.9009 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 36.5993 | 2.1892 | 2089.1914 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 36.5993 | 2.2487 | 2148.7041 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 10.4659 | 16.4166 | 16316.5871 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.7564 | 19.9903 | 19890.3489 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.7564 | 19.7625 | 19662.5041 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.7564 | 19.972 | 19872.0298 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.7564 | 20.026 | 19926.0082 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.48 | 64.7235 | 64623.5463 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.48 | 63.0174 | 62917.4433 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.48 | 56.2901 | 56190.0932 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 42.5187 | 16.1294 | 16029.3788 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 24.6023 | 2.3667 | 2266.6729 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 24.6023 | 2.3098 | 2209.7794 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 36.6299 | 2.1959 | 2095.9403 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 36.6299 | 2.2557 | 2155.7184 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 10.4617 | 16.4131 | 16313.0583 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.735 | 19.968 | 19868.0453 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.735 | 19.7406 | 19640.6404 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.735 | 19.9498 | 19849.7776 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.735 | 20.0037 | 19903.6561 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.4778 | 64.7085 | 64608.4989 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.4778 | 63.0041 | 62904.1204 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.4778 | 56.2759 | 56175.9189 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 41.3497 | 16.1615 | 16061.4808 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 24.3417 | 2.3566 | 2256.5774 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 24.3417 | 2.2992 | 2199.246 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 36.5993 | 2.1898 | 2089.7938 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 36.5993 | 2.2493 | 2149.3267 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 10.4617 | 16.4131 | 16313.0506 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.735 | 19.968 | 19868.0469 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.735 | 19.7406 | 19640.6405 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.735 | 19.9498 | 19849.7791 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.735 | 20.0037 | 19903.6577 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.4778 | 64.7085 | 64608.5021 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.4778 | 63.0041 | 62904.1234 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.4778 | 56.2759 | 56175.9214 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 41.3574 | 16.1613 | 16061.2841 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 24.3434 | 2.3566 | 2256.6148 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 24.3434 | 2.2993 | 2199.2873 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 36.5993 | 2.1898 | 2089.7959 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 36.5993 | 2.2493 | 2149.3292 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 10.4118 | 16.4262 | 16326.1883 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.7136 | 19.9636 | 19863.569 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.7136 | 19.7362 | 19636.2291 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.7136 | 19.9453 | 19845.313 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.7136 | 19.9992 | 19899.1805 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.476 | 64.7465 | 64646.5249 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.476 | 63.0408 | 62940.825 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.476 | 56.3014 | 56201.3641 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 41.4736 | 16.144 | 16043.9594 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 23.6222 | 2.342 | 2241.9517 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 23.6222 | 2.2883 | 2188.2815 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 35.7669 | 2.1725 | 2072.5455 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 35.7669 | 2.2315 | 2131.5147 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 10.4413 | 16.4157 | 16315.6678 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.7237 | 19.9649 | 19864.8694 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.7237 | 19.7375 | 19637.5153 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.7237 | 19.9466 | 19846.6096 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.7237 | 20.0005 | 19900.478 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4768 | 64.7275 | 64627.4611 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4768 | 63.0225 | 62922.5309 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4768 | 56.2884 | 56188.4172 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 42.4218 | 16.1218 | 16021.7506 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 24.5667 | 2.3531 | 2253.0867 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 24.5667 | 2.2965 | 2196.4655 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 36.4299 | 2.1827 | 2082.6593 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 36.4299 | 2.2419 | 2141.9418 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 10.4494 | 16.4074 | 16307.4219 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.735 | 19.9678 | 19867.8285 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.735 | 19.7404 | 19640.4277 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.735 | 19.9496 | 19849.561 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.735 | 20.0034 | 19903.4388 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4778 | 64.7083 | 64608.2605 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4778 | 63.0039 | 62903.8942 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.4778 | 56.2757 | 56175.6893 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 41.3588 | 16.145 | 16044.9791 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 22.9699 | 2.3377 | 2237.7185 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 22.9699 | 2.2848 | 2184.7605 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 36.5727 | 2.1919 | 2091.9439 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 36.5727 | 2.2516 | 2151.5571 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 10.4639 | 16.4177 | 16317.747 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.7343 | 19.9678 | 19867.8189 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.7343 | 19.7404 | 19640.4186 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.7343 | 19.9496 | 19849.5514 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.7343 | 20.0034 | 19903.4292 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.4777 | 64.7086 | 64608.6324 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.4777 | 63.0043 | 62904.301 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.4777 | 56.276 | 56175.9976 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 42.4977 | 16.1248 | 16024.7906 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 24.5666 | 2.3565 | 2256.4804 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 24.5666 | 2.2995 | 2199.4998 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 36.5546 | 2.1883 | 2088.279 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 36.5546 | 2.2477 | 2147.7487 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 10.4599 | 16.4113 | 16311.2704 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6371 | 19.9748 | 19874.7661 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6371 | 19.7471 | 19647.1262 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6371 | 19.9565 | 19856.4888 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6371 | 20.0104 | 19910.4371 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4714 | 64.9265 | 64826.5249 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4714 | 63.2127 | 63112.7165 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4714 | 56.4285 | 56328.4791 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 42.4961 | 16.1237 | 16023.6594 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 24.5844 | 2.3574 | 2257.4045 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 24.5844 | 2.3005 | 2200.4651 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 18.1247 | 2.2371 | 2137.0976 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 18.1247 | 2.3021 | 2202.0746 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 10.4583 | 16.4164 | 16316.3755 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.7457 | 19.9828 | 19882.81 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.7457 | 19.7551 | 19655.1101 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.7457 | 19.9645 | 19864.5094 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.7457 | 20.0185 | 19918.4555 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.479 | 64.7254 | 64625.388 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.479 | 63.0196 | 62919.5655 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.479 | 56.29 | 56190.0209 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 42.3906 | 16.1275 | 16027.4586 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 24.4836 | 2.3584 | 2258.389 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 24.4836 | 2.3018 | 2201.7671 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 36.4476 | 2.1923 | 2092.3063 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 36.4476 | 2.252 | 2151.9675 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 10.4583 | 16.4164 | 16316.3746 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.7456 | 19.9828 | 19882.7516 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.7456 | 19.7551 | 19655.0528 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.7456 | 19.9645 | 19864.4512 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.7456 | 20.0184 | 19918.397 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.479 | 64.7253 | 64625.3038 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.479 | 63.0195 | 62919.4882 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.479 | 56.29 | 56189.9503 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 42.3902 | 16.1275 | 16027.4611 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 24.4833 | 2.3584 | 2258.3757 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 24.4833 | 2.3018 | 2201.7553 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 36.4469 | 2.1923 | 2092.2698 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 36.4469 | 2.2519 | 2151.9297 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.4564 | 16.4125 | 16312.4642 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7344 | 19.9684 | 19868.3944 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7344 | 19.741 | 19640.9795 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7344 | 19.9501 | 19850.1269 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.7344 | 20.004 | 19904.0066 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 64.7127 | 64612.6637 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 63.0081 | 62908.0971 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4777 | 56.2788 | 56178.8036 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 42.3859 | 16.1259 | 16025.8626 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 24.446 | 2.3551 | 2255.1218 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 24.446 | 2.2988 | 2198.7727 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 36.5822 | 2.1864 | 2086.3869 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 36.5822 | 2.2458 | 2145.7831 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 10.4547 | 16.414 | 16314.0244 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.735 | 19.968 | 19868.0337 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.735 | 19.7406 | 19640.628 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.735 | 19.9498 | 19849.7657 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.735 | 20.0036 | 19903.6444 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4778 | 64.7082 | 64608.2007 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4778 | 63.0038 | 62903.8429 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.4778 | 56.2757 | 56175.6996 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 42.3796 | 16.1264 | 16026.3607 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 24.5219 | 2.3552 | 2255.1562 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 24.5219 | 2.2987 | 2198.6771 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 36.4971 | 2.1875 | 2087.5454 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 36.4971 | 2.247 | 2146.9797 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 10.4656 | 16.4161 | 16316.0521 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.7561 | 19.9901 | 19890.1403 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.7561 | 19.7623 | 19662.2988 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.7561 | 19.9718 | 19871.823 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.7561 | 20.0258 | 19925.799 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.48 | 64.7239 | 64623.9051 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.48 | 63.0178 | 62917.8299 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.48 | 56.2903 | 56190.2878 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 42.5108 | 16.1263 | 16026.3267 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 24.5904 | 2.3607 | 2260.7029 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 24.5904 | 2.3037 | 2203.6853 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 36.6396 | 2.1981 | 2098.0999 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 36.6396 | 2.258 | 2157.966 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 10.4636 | 16.4168 | 16316.7943 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.7602 | 19.996 | 19896.0377 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.7602 | 19.7681 | 19668.0794 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.7602 | 19.9777 | 19877.7055 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.7602 | 20.0317 | 1993171% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.4804 | 64.7288 | 64628.8072 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.4804 | 63.0222 | 6292222% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.4804 | 56.2946 | 56194.6307 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 42.4584 | 16.1269 | 16026.8672 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 24.54 | 2.3606 | 2260.6314 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 24.54 | 2.3037 | 2203.6858 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 36.5602 | 2.1989 | 2098.9397 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 36.5602 | 2.2588 | 2158.8437 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 9.2521 | 17.8999 | 17799.8821 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.7309 | 19.9693 | 19869.3135 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.7309 | 19.7419 | 19641.8731 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.7309 | 19.951 | 19851.0438 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.7309 | 20.0049 | 19904.9311 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.4775 | 64.7254 | 64625.418 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.4775 | 63.0203 | 62920.2887 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.4775 | 56.2878 | 56187.789 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 42.4567 | 16.125 | 16025.0106 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 24.5629 | 2.3581 | 2258.0669 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 24.5629 | 2.3011 | 2201.119 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 36.5754 | 2.188 | 2087.9513 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 36.5754 | 2.2474 | 2147.4216 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 10.2722 | 16.6402 | 16540.1976 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.728 | 19.9708 | 19870.827 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.728 | 19.7434 | 19643.3531 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.728 | 19.9526 | 19852.5534 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.728 | 20.0065 | 19906.4508 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.4774 | 64.7365 | 64636.4994 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.4774 | 63.0308 | 62930.8266 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.4774 | 56.2958 | 56195.8066 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 42.4337 | 16.1256 | 16025.5955 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 24.5592 | 2.3579 | 2257.9103 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 24.5592 | 2.301 | 2201.0211 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 36.5497 | 2.1893 | 2089.2745 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 36.5497 | 2.2488 | 2148.8014 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 10.4627 | 16.412 | 16312.0036 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7351 | 19.9682 | 19868.1924 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7351 | 19.7408 | 19640.7845 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7351 | 19.9499 | 19849.9255 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7351 | 20.0038 | 19903.805 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 64.7086 | 64608.634 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 63.0042 | 62904.2487 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 56.2761 | 56176.0515 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 20.2596 | 17.5066 | 17406.6038 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 24.5039 | 2.359 | 2258.9827 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 24.5039 | 2.3021 | 2202.1098 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 36.6017 | 2.1899 | 2089.9217 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 36.6017 | 2.2495 | 2149.4609 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 10.4622 | 16.4117 | 16311.7362 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7349 | 19.968 | 19867.9695 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7349 | 19.7406 | 19640.5645 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7349 | 19.9497 | 19849.7019 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.7349 | 20.0036 | 19903.5801 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 64.7084 | 64608.4185 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 63.0041 | 62904.1046 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.4778 | 56.2758 | 56175.8282 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 27.3186 | 16.7639 | 16663.9131 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 24.4996 | 2.3574 | 2257.4208 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 24.4996 | 2.3005 | 2200.5495 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 36.6024 | 2.19 | 2090.0209 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 36.6024 | 2.2496 | 2149.5647 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 10.4617 | 16.4118 | 16311.8124 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.7349 | 19.968 | 19868.0422 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.7349 | 19.7406 | 19640.6371 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.7349 | 19.9498 | 19849.7742 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.7349 | 20.0037 | 19903.6531 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.4778 | 64.7087 | 64608.7046 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.4778 | 63.0043 | 62904.3098 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.4778 | 56.276 | 56176.0425 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 42.1498 | 16.1313 | 16031.3076 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 24.5713 | 2.358 | 2257.9768 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 24.5713 | 2.301 | 2200.9852 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 36.5998 | 2.1898 | 2089.8241 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 36.5998 | 2.2494 | 2149.3605 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 10.4601 | 16.411 | 16310.9788 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.7351 | 19.9681 | 19868.1468 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.7351 | 19.7407 | 19640.7378 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.7351 | 19.9499 | 19849.8785 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.7351 | 20.0038 | 19903.7579 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.4778 | 64.7093 | 64609.3455 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.4778 | 63.0049 | 62904.9043 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.4778 | 56.2765 | 56176.4838 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 39.9486 | 16.1896 | 16089.5738 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 24.5614 | 2.3557 | 2255.6839 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 24.5614 | 2.299 | 2198.9678 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 36.5985 | 2.1891 | 2089.1015 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 36.5985 | 2.2486 | 2148.6103 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 10.4109 | 16.4467 | 16346.662 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.7355 | 19.9685 | 19868.4993 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.7355 | 19.7411 | 19641.0853 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.7355 | 19.9502 | 19850.2317 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.7355 | 20.0041 | 19904.1111 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.4779 | 64.709 | 64608.9976 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.4779 | 63.0046 | 62904.5909 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.4779 | 56.2763 | 56176.3207 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 41.7358 | 16.1468 | 16046.8101 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 24.4735 | 2.36 | 2259.9747 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 24.4735 | 2.3031 | 2203.1417 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 36.5903 | 2.19 | 2090.0293 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 36.5903 | 2.2496 | 2149.574 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 10.4618 | 16.4125 | 16312.4829 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.7352 | 19.9682 | 19868.1705 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.7352 | 19.7408 | 19640.7628 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.7352 | 19.9499 | 19849.9036 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.7352 | 20.0038 | 19903.7816 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.4778 | 64.7086 | 64608.5717 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.4778 | 63.0042 | 62904.1901 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.4778 | 56.276 | 56175.9979 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 41.1191 | 16.1708 | 16070.7795 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 24.5099 | 2.3587 | 2258.6636 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 24.5099 | 2.3015 | 2201.5451 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 36.6019 | 2.19 | 2089.9618 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 36.6019 | 2.2495 | 2149.5021 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 10.4626 | 16.4121 | 16312.1111 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.7351 | 19.9681 | 19868.0992 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.7351 | 19.7407 | 19640.6931 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.7351 | 19.9498 | 19849.8325 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.7351 | 20.0037 | 19903.7116 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.4778 | 64.7086 | 64608.569 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.4778 | 63.0042 | 62904.1863 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.4778 | 56.276 | 56175.9785 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 42.2849 | 16.1312 | 16031.1769 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 24.5734 | 2.358 | 2258.0266 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 24.5734 | 2.3011 | 2201.0503 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 36.6029 | 2.19 | 2089.9792 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 36.6029 | 2.2495 | 2149.5203 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 10.4624 | 16.4123 | 16312.3113 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.735 | 19.9681 | 19868.0958 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.735 | 19.7407 | 19640.6896 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.735 | 19.9498 | 19849.8279 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.735 | 20.0037 | 19903.7067 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.4778 | 64.7087 | 64608.6921 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.4778 | 63.0043 | 62904.2999 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.4778 | 56.2761 | 56176.056 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 38.7689 | 16.2364 | 16136.3634 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 24.5534 | 2.3581 | 2258.1343 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 24.5534 | 2.3012 | 2201.2008 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 36.6002 | 2.19 | 2090.0235 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 36.6002 | 2.2496 | 2149.5674 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 4.4095 | 23.7187 | 23618.6564 | 81 | 93.6 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.9683 | 19868.3242 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.7409 | 19640.9126 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.9501 | 19850.0569 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 20.0039 | 19903.9358 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 64.7099 | 64609.8906 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 63.0055 | 62905.4737 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 56.2769 | 56176.9369 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 42.4923 | 16.1239 | 16023.915 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 24.5846 | 2.3581 | 2258.079 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 24.5846 | 2.3011 | 2201.1058 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 36.5969 | 2.1902 | 2090.2093 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 36.5969 | 2.2498 | 2149.762 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 8.81 | 18.2373 | 18137.2808 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.7349 | 19.968 | 19867.9909 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.7349 | 19.7406 | 19640.5867 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.7349 | 19.9497 | 19849.7244 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.7349 | 20.0036 | 19903.603 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.4778 | 64.7088 | 64608.8312 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.4778 | 63.0044 | 62904.4267 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.4778 | 56.2761 | 56176.1227 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 42.4989 | 16.1241 | 16024.1075 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 24.5833 | 2.3583 | 2258.3058 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 24.5833 | 2.3013 | 2201.3154 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 36.6037 | 2.1901 | 2090.0781 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 36.6037 | 2.2496 | 2149.6232 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 9.3478 | 17.162 | 17061.9953 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.7351 | 19.9682 | 19868.1645 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.7351 | 19.7408 | 19640.7571 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.7351 | 19.9499 | 19849.8976 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.7351 | 20.0038 | 19903.7756 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.4778 | 64.7086 | 64608.6227 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.4778 | 63.0042 | 62904.2373 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.4778 | 56.276 | 56176.0314 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 42.4908 | 16.1241 | 16024.0882 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 24.5832 | 2.3581 | 2258.0847 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 24.5832 | 2.3011 | 2201.1114 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 36.5975 | 2.1901 | 2090.0655 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 36.5975 | 2.2496 | 2149.6112 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 9.8066 | 16.6961 | 16596.1478 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.7348 | 19.9679 | 19867.9274 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.7348 | 19.7405 | 19640.5247 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.7348 | 19.9497 | 19849.6614 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.7348 | 20.0035 | 19903.538 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.4777 | 64.7084 | 64608.4381 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.4777 | 63.0041 | 62904.1233 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.4777 | 56.2759 | 56175.8942 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 42.4943 | 16.1239 | 16023.883 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 24.5835 | 2.3579 | 2257.9067 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 24.5835 | 2.3009 | 2200.9407 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 36.6021 | 2.1899 | 2089.9047 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 36.6021 | 2.2494 | 2149.443 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 6.0898 | 20.6355 | 20535.4936 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.9683 | 19868.2836 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.7409 | 19640.8722 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 19.95 | 19850.0152 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.735 | 20.0039 | 19903.895 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 64.7091 | 64609.1003 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 63.0047 | 62904.6828 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.4778 | 56.2764 | 5617639% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 42.4853 | 16.1238 | 1602380% | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 24.5827 | 2.3574 | 2257.4374 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 24.5827 | 2.3005 | 2200.5094 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 36.5958 | 2.1899 | 2089.8858 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 36.5958 | 2.2494 | 2149.424 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.4513 | 16.4121 | 16312.0969 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.6204 | 19.9915 | 19891.482 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.6204 | 19.7635 | 19663.4738 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.6204 | 19.9732 | 19873.1684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.6204 | 20.0272 | 19927.2081 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4709 | 65.0218 | 64921.7523 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4709 | 63.303 | 63202.9788 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.4709 | 56.4978 | 56397.8097 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 42.0495 | 16.1387 | 16038.7183 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 24.1381 | 2.3592 | 2259.209 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 24.1381 | 2.3033 | 2203.2744 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 34.8225 | 2.1956 | 2095.6228 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 34.8225 | 2.2556 | 2155.5877 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.4602 | 16.4123 | 16312.3272 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.7077 | 19.9702 | 19870.2431 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.7077 | 19.7428 | 19642.7683 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.7077 | 19.952 | 19851.973 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.7077 | 20.0059 | 19905.8706 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4758 | 64.7729 | 64672.8554 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4758 | 63.0657 | 62965.7047 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.4758 | 56.3211 | 56221.0913 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 42.453 | 16.1252 | 16025.2045 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 24.55 | 2.3576 | 2257.559 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 24.55 | 2.3007 | 2200.698 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 36.2646 | 2.1848 | 2084.8309 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 36.2646 | 2.2442 | 2144.1855 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 10.4582 | 16.4115 | 16311.4667 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.7344 | 19.9676 | 19867.5728 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.7344 | 19.7402 | 19640.1789 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.7344 | 19.9493 | 19849.3073 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.7344 | 20.0032 | 19903.1822 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.4777 | 64.707 | 64606.9837 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.4777 | 63.0027 | 62902.7066 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.4777 | 56.2748 | 56174.7648 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 42.4905 | 16.124 | 16023.9733 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 24.5767 | 2.3579 | 2257.9019 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 24.5767 | 2.3009 | 2200.9161 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 36.4916 | 2.1889 | 2088.859 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 36.4916 | 2.2483 | 2148.3353 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 10.4589 | 16.4115 | 16311.5369 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.7348 | 19.9676 | 19867.6016 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.7348 | 19.7402 | 19640.2056 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.7348 | 19.9493 | 19849.3347 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.7348 | 20.0032 | 19903.2111 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.4778 | 64.7071 | 64607.1238 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.4778 | 63.0028 | 62902.8386 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.4778 | 56.2749 | 56174.8667 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 42.4918 | 16.124 | 16023.9726 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 24.5777 | 2.3579 | 2257.9073 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 24.5777 | 2.3009 | 2200.9224 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 36.5011 | 2.1889 | 2088.893 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 36.5011 | 2.2484 | 2148.3723 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 10.4566 | 16.409 | 16309.0162 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6472 | 19.9853 | 19885.3371 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6472 | 19.7575 | 19657.471 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6472 | 19.967 | 19867.036 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 15.6472 | 20.021 | 19921.0385 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4722 | 64.9631 | 64863.1234 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4722 | 63.2473 | 63147.2978 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.4722 | 56.4553 | 56355.3289 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 42.4874 | 16.1231 | 16023.1073 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 24.5804 | 2.3561 | 2256.0546 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 24.5804 | 2.2992 | 2199.2184 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 21.4092 | 2.275 | 2175.0177 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 21.4092 | 2.3394 | 2239.356 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.4607 | 16.4136 | 16313.6349 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5194 | 19.9853 | 19885.2529 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5194 | 19.7573 | 19657.2933 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5194 | 19.967 | 19866.9598 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 15.5194 | 20.021 | 19921.0002 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.46 | 65.4576 | 65357.591 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.46 | 63.7203 | 63620.3464 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.46 | 56.8012 | 56701.1786 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 42.4765 | 16.1246 | 16024.633 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 24.5703 | 2.3581 | 2258.0503 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 24.5703 | 2.3011 | 2201.1264 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 36.1301 | 2.1896 | 2089.6386 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 36.1301 | 2.2492 | 2149.216 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.4608 | 16.4109 | 16310.9139 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 15.4697 | 20.007 | 19906.9704 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 15.4697 | 19.7784 | 19678.3861 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 15.4697 | 19.9886 | 19888.6363 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 15.4697 | 20.0429 | 19942.8506 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.4572 | 65.8046 | 65704.5816 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.4572 | 64.0517 | 63951.7075 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.4572 | 57.043 | 56942.9944 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 42.493 | 16.1238 | 16023.7609 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 24.5786 | 2.3575 | 2257.4642 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 24.5786 | 2.3005 | 2200.5259 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 36.529 | 2.188 | 2088.0198 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 36.529 | 2.2475 | 2147.5035 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.4627 | 16.412 | 16312.0006 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.7337 | 19.9672 | 19867.2068 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.7337 | 19.7398 | 19639.8248 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.7337 | 19.9489 | 19848.9426 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.7337 | 20.0028 | 19902.8143 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.4765 | 64.7737 | 64673.6592 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.4765 | 63.0665 | 62966.5439 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.4765 | 56.3214 | 56221.4008 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 42.4971 | 16.124 | 16024.0109 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 24.5841 | 2.3581 | 2258.0629 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 24.5841 | 2.3011 | 2201.0867 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 36.5999 | 2.19 | 2089.9946 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 36.5999 | 2.2495 | 2149.5362 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.4627 | 16.412 | 16312.0024 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.7337 | 19.9672 | 19867.2171 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.7337 | 19.7398 | 19639.8334 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.7337 | 19.949 | 19848.9514 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.7337 | 20.0028 | 19902.8247 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.4765 | 64.773 | 64673.016 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.4765 | 63.0659 | 62965.8867 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.4765 | 56.3209 | 56220.9245 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 42.4971 | 16.124 | 16024.011 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 24.5841 | 2.3581 | 2258.0627 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 24.5841 | 2.3011 | 2201.0868 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 36.5999 | 2.19 | 2089.9948 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 36.5999 | 2.2495 | 2149.5362 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.4627 | 16.412 | 16312.0009 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.7331 | 19.9669 | 19866.8681 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.7331 | 19.7395 | 19639.4938 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.7331 | 19.9486 | 19848.6031 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.7331 | 20.0025 | 19902.4729 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.4758 | 64.8042 | 64704.1764 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.4758 | 63.0958 | 62995.7831 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.4758 | 56.3426 | 56242.6364 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 42.4969 | 16.124 | 16024.0095 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 24.5839 | 2.3581 | 2258.0611 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 24.5839 | 2.3011 | 2201.0851 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 36.5985 | 2.19 | 2090.0062 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 36.5985 | 2.2495 | 2149.5477 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.4744 | 16.4275 | 16327.4909 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.8214 | 20.0582 | 19958.1632 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.8214 | 19.829 | 19728.9801 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.8214 | 20.0397 | 19939.6898 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.8214 | 20.094 | 19993.97 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4868 | 64.7695 | 64669.4768 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4868 | 63.058 | 62958.0492 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4868 | 56.3333 | 56233.2831 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 42.5841 | 16.1414 | 16041.3586 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6995 | 2.2112 | 2111.2418 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6995 | 2.2716 | 2171.6264 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.4654 | 16.4154 | 16315.3735 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.9869 | 19886.9133 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.7591 | 19659.1364 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.9686 | 19868.602 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 20.0226 | 19922.565 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 64.7211 | 64621.0635 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 63.0152 | 62915.2125 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 56.2878 | 56187.8181 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 42.5181 | 16.1276 | 16027.6215 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.622 | 2.374 | 2274.0126 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.622 | 2.3174 | 2217.4103 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6253 | 2.1948 | 2094.8203 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6253 | 2.2546 | 2154.5526 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 10.4655 | 16.4155 | 16315.4841 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.7531 | 19.9869 | 19886.9338 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.7531 | 19.7592 | 19659.1566 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.7531 | 19.9686 | 19868.6228 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.7531 | 20.0226 | 19922.5856 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.4797 | 64.7211 | 64621.1327 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.4797 | 63.0153 | 62915.2771 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.4797 | 56.2879 | 56187.8699 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 42.5189 | 16.1278 | 16027.7778 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 24.619 | 2.3756 | 2275.6299 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 24.619 | 2.3189 | 2218.9492 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 36.6253 | 2.1949 | 2094.8892 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 36.6253 | 2.2546 | 2154.6241 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.4654 | 16.4154 | 16315.3735 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.9869 | 19886.9133 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.7591 | 19659.1364 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 19.9686 | 19868.602 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.7531 | 20.0226 | 19922.565 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 64.7211 | 64621.0635 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 63.0152 | 62915.2125 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 56.2878 | 56187.8181 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 42.5181 | 16.1276 | 16027.6215 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.622 | 2.374 | 2274.0126 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.622 | 2.3174 | 2217.4103 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6253 | 2.1948 | 2094.8203 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6253 | 2.2546 | 2154.5526 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 10.4655 | 16.4155 | 16315.4841 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.7531 | 19.9869 | 19886.9338 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.7531 | 19.7592 | 19659.1566 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.7531 | 19.9686 | 19868.6228 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.7531 | 20.0226 | 19922.5856 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.4797 | 64.7211 | 64621.1327 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.4797 | 63.0153 | 62915.2771 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.4797 | 56.2879 | 56187.8699 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 42.5189 | 16.1278 | 16027.7778 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 24.619 | 2.3756 | 2275.6299 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 24.619 | 2.3189 | 2218.9492 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 36.6253 | 2.1949 | 209489% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 36.6253 | 2.2546 | 2154.6241 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.4654 | 16.4154 | 1631535% | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.753 | 19.9868 | 19886.8027 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.753 | 19.759 | 19659.0281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.753 | 19.9685 | 19868.4932 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.753 | 20.0225 | 19922.4542 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 64.721 | 64620.9936 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 63.0152 | 62915.2074 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.4797 | 56.2878 | 56187.7923 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 42.5179 | 16.1276 | 16027.5975 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.6217 | 2.3739 | 2273.86 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 24.6217 | 2.3173 | 2217.2609 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6252 | 2.1948 | 2094.7899 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 36.6252 | 2.2545 | 2154.5208 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 10.4655 | 16.4155 | 16315.4625 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.753 | 19.9868 | 19886.8232 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.753 | 19.759 | 19659.0482 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.753 | 19.9685 | 19868.5136 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.753 | 20.0225 | 19922.4748 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.4797 | 64.7211 | 64621.0599 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.4797 | 63.0152 | 62915.2097 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.4797 | 56.2878 | 56187.7981 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 42.5187 | 16.1278 | 16027.7537 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 24.6186 | 2.3755 | 2275.4771 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 24.6186 | 2.3188 | 2218.7997 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 36.6252 | 2.1949 | 2094.8587 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 36.6252 | 2.2546 | 2154.5923 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 10.4631 | 16.4123 | 16312.3239 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.7811 | 20.0041 | 19904.1366 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.7811 | 19.7759 | 19675.9186 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.7811 | 19.9858 | 19885.7929 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.7811 | 20.0399 | 19939.8727 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.4811 | 64.9084 | 64808.3898 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.4811 | 63.1939 | 63093.8783 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.4811 | 56.4208 | 56320.7624 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 42.4993 | 16.1242 | 16024.1621 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 24.5853 | 2.3583 | 2258.3199 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 24.5853 | 2.3013 | 2201.3308 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 36.612 | 2.1916 | 2091.6083 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 36.612 | 2.2512 | 2151.214 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 10.4627 | 16.412 | 16312.0299 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7372 | 19.9687 | 19868.7495 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7372 | 19.7413 | 19641.3326 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7372 | 19.9505 | 19850.48 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.7372 | 20.0044 | 19904.3596 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.146 | 79.7036 | 79603.6131 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.146 | 77.2659 | 77165.922 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.146 | 66.2943 | 66194.2504 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 42.4972 | 16.124 | 16024.0228 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 24.5842 | 2.3581 | 2258.0754 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 24.5842 | 2.3011 | 2201.0993 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 36.6024 | 2.19 | 2090.0425 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 36.6024 | 2.2496 | 2149.5864 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 10.4625 | 16.412 | 16312.0103 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.217 | 19.9889 | 19888.8905 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.217 | 19.7609 | 19660.9226 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.217 | 19.9706 | 19870.5942 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 15.217 | 20.0246 | 19924.6323 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.3999 | 65.5254 | 65425.3986 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.3999 | 63.7891 | 63689.1402 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.3999 | 56.8546 | 56754.6043 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 42.4956 | 16.124 | 16024.0274 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 24.5829 | 2.358 | 2258.0411 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 24.5829 | 2.3011 | 2201.0683 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 36.5713 | 2.1897 | 2089.7343 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25SP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 36.5713 | 2.2493 | 2149.2671 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | Base | 10.3211 | 16.4124 | 16312.3848 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.0639 | 19.7698 | 19669.846 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.0639 | 19.5468 | 19446.7721 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.0639 | 19.752 | 19652.0257 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | Base | 15.0639 | 19.8049 | 19704.8631 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.276 | 51.8947 | 51794.7245 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.276 | 50.7216 | 50621.5567 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | Base | 5.276 | 46.828 | 46727.9748 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | Base | 40.7414 | 16.163 | 16062.9683 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | Base | 23.4678 | 2.359 | 2259.0193 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | Base | 23.4678 | 2.3043 | 2204.2931 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | Base | 35.2003 | 2.1465 | 2046.5149 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | Base | 35.2003 | 2.2045 | 2104.5387 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.3121 | 16.4069 | 16306.9317 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4811 | 20.3608 | 20260.8182 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4811 | 20.1244 | 20024.4407 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4811 | 20.3418 | 20241.7966 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.4811 | 20.398 | 20297.9587 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.2032 | 54.0201 | 53920.0663 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.2032 | 52.7615 | 52661.5291 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 5.2032 | 48.4931 | 48393.0676 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 40.6911 | 16.1609 | 16060.9354 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 23.437 | 2.3544 | 2254.4224 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 23.437 | 2.3 | 2200.041 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 34.9285 | 2.1173 | 2017.2799 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 34.9285 | 2.1742 | 2074.1993 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.3154 | 16.4158 | 16315.7724 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 14.9842 | 19.6974 | 19597.4344 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 14.9842 | 19.4758 | 19375.7643 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 14.9842 | 19.6798 | 19579.7794 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 14.9842 | 19.7323 | 19632.305 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2671 | 51.842 | 51742.0217 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2671 | 50.6738 | 50573.8235 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2671 | 46.7818 | 46681.759 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 40.6639 | 16.1667 | 16066.6758 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.397 | 2.3604 | 2260.3702 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.397 | 2.3059 | 2205.8735 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.5427 | 2.1491 | 2049.1368 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.5427 | 2.2074 | 2107.3537 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 10.3209 | 16.4124 | 16312.3919 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 14.9091 | 19.7098 | 19609.7842 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 14.9091 | 19.4873 | 19387.3378 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 14.9091 | 19.6921 | 19592.1341 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 14.9091 | 19.7449 | 19644.9333 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.2624 | 52.1667 | 52066.6538 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.2624 | 50.9888 | 50888.8324 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 5.2624 | 47.0316 | 46931.6054 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 40.7424 | 16.1631 | 16063.1164 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 23.468 | 2.3592 | 2259.1889 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 23.468 | 2.3045 | 2204.4608 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 35.2028 | 2.1473 | 2047.3036 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 587350 [GEN-2016-050345.00] CKT 1 | 35.2028 | 2.2054 | 2105.3614 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 10.3216 | 16.4129 | 16312.8557 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.1079 | 19.7817 | 19681.6641 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.1079 | 19.5582 | 19458.2312 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.1079 | 19.7638 | 19663.8259 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 15.1079 | 19.8168 | 19716.7677 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.2773 | 52.0086 | 51908.6491 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.2773 | 50.8318 | 50731.8001 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 5.2773 | 46.9163 | 46816.2909 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 40.7445 | 16.1632 | 16063.2034 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 23.4693 | 2.3594 | 2259.4096 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 23.4693 | 2.3047 | 2204.6641 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 35.2151 | 2.1488 | 2048.8398 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 640374 [SWEET W3 345.00] CKT 1 | 35.2151 | 2.207 | 2106.955 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.2909 | 16.427 | 16326.9598 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0661 | 19.7731 | 19673.1388 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0661 | 19.55 | 19449.9997 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0661 | 19.7553 | 19655.3122 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0661 | 19.8082 | 19708.1653 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2765 | 51.9015 | 51801.4854 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2765 | 50.7278 | 50627.8488 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2765 | 46.8336 | 46733.6107 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 39.478 | 16.1954 | 16095.3968 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.889 | 2.368 | 2268.0131 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.889 | 2.3327 | 2232.6669 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 34.889 | 2.1401 | 2040.0609 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 34.889 | 2.1979 | 2097.8845 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 10.32 | 16.4122 | 16312.213 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 14.877 | 19.7873 | 19687.3307 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 14.877 | 19.5638 | 19463.7852 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 14.877 | 19.7695 | 19669.4852 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 14.877 | 19.8225 | 19722.4564 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 2.9566 | 21.7151 | 21615.1018 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 2.9566 | 21.4276 | 21327.6366 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 2.9566 | 21.944 | 21844.0303 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 40.7379 | 16.1629 | 16062.9321 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 23.4659 | 2.3589 | 2258.9402 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 23.4659 | 2.3042 | 2204.22 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 35.1939 | 2.146 | 2045.9512 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 35.1939 | 2.204 | 2103.9539 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 10.3209 | 16.4124 | 16312.3677 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 14.5427 | 19.7928 | 19692.8152 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 14.5427 | 19.5693 | 19469.2897 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 14.5427 | 19.775 | 19674.9613 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 14.5427 | 19.8279 | 19727.9108 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.2045 | 52.3984 | 52298.4041 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.2045 | 51.2092 | 51109.1614 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 5.2045 | 47.2257 | 47125.7351 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 40.7409 | 16.163 | 16062.966 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 23.4676 | 2.359 | 2259.0225 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 23.4676 | 2.3043 | 2204.2962 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 35.1982 | 2.1464 | 2046.439 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640250 [KEARNEY7 115.00] CKT 1 | 35.1982 | 2.2045 | 2104.46 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.376 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 14.9119 | 19.7647 | 19664.6761 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 14.9119 | 19.5418 | 19441.797 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 14.9119 | 19.7469 | 19646.8692 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 14.9119 | 19.7997 | 19699.6505 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.2472 | 51.9154 | 51815.4414 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.2472 | 50.7427 | 50642.6816 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 5.2472 | 46.8464 | 46746.389 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 40.7413 | 16.163 | 16062.9674 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 23.4678 | 2.359 | 2259.0177 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 23.4678 | 2.3043 | 2204.2918 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 35.2001 | 2.1465 | 2046.4794 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640275 [MINDEN 7 115.00] CKT 1 | 35.2001 | 2.2045 | 2104.5018 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.3089 | 16.4121 | 16312.1056 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0235 | 19.7287 | 19628.7298 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0235 | 19.5065 | 19406.4574 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0235 | 19.711 | 19611.0035 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0235 | 19.7637 | 19663.6614 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2707 | 51.8549 | 51754.9451 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2707 | 50.6852 | 50585.1596 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2707 | 46.7937 | 46693.6872 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 40.5883 | 16.168 | 16068.0246 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.3389 | 2.3592 | 2259.2345 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.3389 | 2.3049 | 2204.8928 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.3453 | 2.1451 | 2045.073 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.3453 | 2.2032 | 2103.175 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 10.3206 | 16.4127 | 16312.6656 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 14.3987 | 19.8471 | 1974711% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 14.3987 | 19.622 | 19522.0016 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 14.3987 | 19.8292 | 1972915% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 14.3987 | 19.8825 | 19782.544 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.2582 | 52.207 | 52106.9605 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.2582 | 51.0237 | 50923.6942 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 5.2582 | 47.0696 | 46969.5604 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 40.736 | 16.1631 | 16063.1125 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 23.462 | 2.3591 | 2259.0756 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 23.462 | 2.3044 | 2204.3639 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 35.1552 | 2.147 | 2046.9776 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640374 [SWEET W3 345.00] CKT 2 | 35.1552 | 2.205 | 2105.0261 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.3206 | 16.4128 | 16312.8356 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.1634 | 19.8562 | 19756.155 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.1634 | 19.6309 | 19530.9127 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.1634 | 19.8382 | 19738.1775 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.1634 | 19.8916 | 19791.5944 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2534 | 52.2266 | 52126.6313 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2534 | 51.0418 | 50941.8083 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2534 | 47.0864 | 46986.4015 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 40.7341 | 16.1632 | 16063.1568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 23.4595 | 2.3591 | 2259.1466 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 23.4595 | 2.3044 | 2204.4308 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 35.1379 | 2.1474 | 2047.4077 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 35.1379 | 2.2055 | 2105.473 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3767 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.0451 | 19.7611 | 19661.0617 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.0451 | 19.5382 | 19438.1604 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.0451 | 19.7433 | 19643.2614 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 15.0451 | 19.7961 | 19696.0599 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.2062 | 71.3954 | 71295.4314 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.2062 | 69.5242 | 69424.1572 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 4.2062 | 61.107 | 61006.9757 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 40.7411 | 16.163 | 16062.9811 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 23.4675 | 2.359 | 2259.0136 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 23.4675 | 2.3043 | 2204.2894 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 35.1974 | 2.1465 | 2046.5438 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640224 [HOLDREG7 115.00] CKT 1 | 35.1974 | 2.2046 | 2104.5696 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3983 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.0515 | 19.7652 | 19665.2458 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.0515 | 19.5423 | 19442.2553 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.0515 | 19.7474 | 19647.4357 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 15.0515 | 19.8003 | 19700.2563 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.2165 | 86.6913 | 86591.2592 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.2165 | 84.0374 | 83937.4394 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 4.2165 | 70.8475 | 70747.4519 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 40.7411 | 16.163 | 16062.9809 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 23.4675 | 2.359 | 2259.0216 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 23.4675 | 2.3043 | 2204.2958 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 35.1974 | 2.1466 | 2046.5853 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640313 [PAULINE7 115.00] CKT 1 | 35.1974 | 2.2046 | 2104.612 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 10.321 | 16.4123 | 16312.3439 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 14.9162 | 19.762 | 19661.9871 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 14.9162 | 19.539 | 19439.0451 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 14.9162 | 19.7442 | 19644.1877 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 14.9162 | 19.797 | 19697.0012 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.8697 | 79.9757 | 79875.6978 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.8697 | 77.7662 | 77666.2349 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 3.8697 | 66.7962 | 66696.1524 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 40.7408 | 16.163 | 16062.9547 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 23.4674 | 2.359 | 2258.99 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 23.4674 | 2.3043 | 2204.2656 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 35.194 | 2.1461 | 2046.1459 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640242 [JOHN.2 7 115.00] CKT 1 | 35.194 | 2.2042 | 2104.1557 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 10.3211 | 16.4124 | 16312.3821 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.0645 | 19.7694 | 19669.3573 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.0645 | 19.5463 | 19446.2941 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.0645 | 19.7515 | 19651.5383 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 15.0645 | 19.8044 | 19704.3733 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.2779 | 51.8054 | 51705.4336 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.2779 | 50.6358 | 50535.8455 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 5.2779 | 46.7576 | 46657.59 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 40.7414 | 16.163 | 16062.967 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 23.4678 | 2.359 | 2259.0173 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 23.4678 | 2.3043 | 2204.2912 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 35.2004 | 2.1465 | 2046.5014 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643080 [HOLDREDGET1913.800] CKT 1 | 35.2004 | 2.2045 | 2104.5248 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 10.3211 | 16.4124 | 16312.3821 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.0645 | 19.7694 | 19669.356 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.0645 | 19.5463 | 19446.2942 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.0645 | 19.7515 | 19651.537 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 15.0645 | 19.8044 | 19704.372 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.2779 | 51.8053 | 51705.2729 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.2779 | 50.6357 | 50535.6947 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 5.2779 | 46.7575 | 46657.4655 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 40.7414 | 16.163 | 16062.967 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 23.4678 | 2.359 | 2259.0173 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 23.4678 | 2.3043 | 2204.2912 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 35.2004 | 2.1465 | 2046.5013 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640225 [HOLDREG9 34.500] TO BUS 643081 [HOLDREDGET2913.800] CKT 1 | 35.2004 | 2.2045 | 2104.5248 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 10.3209 | 16.4123 | 16312.332 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.0573 | 19.7654 | 19665.4468 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.0573 | 19.5425 | 19442.4842 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.0573 | 19.7476 | 19647.6361 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 15.0573 | 19.8004 | 19700.4458 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.2668 | 50.3366 | 50236.5995 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.2668 | 49.2185 | 49118.5432 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 5.2668 | 45.6138 | 45513.7659 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 40.7407 | 16.1629 | 16062.9485 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 23.4674 | 2.359 | 2258.9795 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 23.4674 | 2.3043 | 2204.2555 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 35.1983 | 2.1462 | 2046.2497 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 640448 [HOLDREGE 869.000] TO BUS 643177 [HOLDREGET3 913.800] CKT 1 | 35.1983 | 2.2043 | 2104.2636 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.312 | 16.4148 | 16314.8122 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.0265 | 19.7911 | 19691.1036 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.0265 | 19.5668 | 19466.8286 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.0265 | 19.7733 | 19673.3065 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 13.0265 | 19.8266 | 19726.5722 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1589 | 53.1215 | 53021.4601 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1589 | 51.9088 | 51808.8329 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1589 | 47.7764 | 47676.3713 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 40.6798 | 16.1651 | 16065.0999 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 23.4177 | 2.3582 | 2258.2271 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 23.4177 | 2.3039 | 2203.8574 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 34.5781 | 2.1385 | 2038.5158 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 34.5781 | 2.1964 | 2096.3688 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.3184 | 16.4161 | 16316.0861 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 14.9048 | 19.7802 | 19680.2131 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 14.9048 | 19.5568 | 19456.8288 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 14.9048 | 19.7624 | 19662.3763 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 14.9048 | 19.8153 | 19715.3035 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2644 | 52.0473 | 51947.3389 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2644 | 50.8693 | 50769.2637 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2644 | 46.9464 | 46846.3939 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 40.6622 | 16.1665 | 16066.5387 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 23.3973 | 2.3605 | 2260.5121 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 23.3973 | 2.3059 | 2205.9103 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 32.2239 | 2.1642 | 2064.2194 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 32.2239 | 2.2232 | 2123.1671 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 10.3206 | 16.4122 | 16312.2119 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.0524 | 19.7532 | 19653.2072 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.0524 | 19.5305 | 19430.5272 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.0524 | 19.7354 | 19635.4232 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 15.0524 | 19.7882 | 19688.1608 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.2724 | 47.2296 | 47129.5563 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.2724 | 46.2208 | 46120.8253 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 5.2724 | 43.1408 | 43040.78 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 40.7395 | 16.1629 | 16062.9087 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 23.4668 | 2.3589 | 2258.903 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 23.4668 | 2.3042 | 2204.1833 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 35.1955 | 2.1457 | 2045.7256 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 640311 [ORLEANS8 69.000] TO BUS 643120 [ORLEANS T1 913.800] CKT 1 | 35.1955 | 2.2037 | 2103.7189 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 10.3182 | 16.4144 | 16314.4442 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.5707 | 20.0653 | 19965.3213 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.5707 | 19.834 | 19733.9982 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.5707 | 20.047 | 19946.9962 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 12.5707 | 20.1021 | 20002.1407 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1258 | 55.1275 | 55027.4712 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1258 | 53.8415 | 53741.4556 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 5.1258 | 49.318 | 49217.979 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 40.7079 | 16.1639 | 16063.9225 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 23.4392 | 2.3591 | 2259.0757 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 23.4392 | 2.3044 | 2204.4413 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 34.8019 | 2.145 | 2044.995 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640525 [TOBIAS 3345.00] CKT 1 | 34.8019 | 2.203 | 2103.0022 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 10.3209 | 16.4126 | 16312.6044 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 14.5294 | 19.7725 | 19672.5129 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 14.5294 | 19.5496 | 19449.6335 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 14.5294 | 19.7547 | 19654.699 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 14.5294 | 19.8075 | 19707.4638 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.211 | 53.3258 | 53225.812 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.211 | 52.1039 | 52003.9137 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 5.211 | 47.9383 | 47838.2634 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 40.7385 | 16.1631 | 16063.0547 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 23.4651 | 2.3591 | 2259.076 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 23.4651 | 2.3043 | 2204.3495 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 35.1601 | 2.1469 | 2046.9358 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640313 [PAULINE7 115.00] TO BUS 640315 [PAULINE9 13.800] CKT 1 | 35.1601 | 2.205 | 2104.9761 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 10.3196 | 16.4128 | 16312.7609 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 13.8669 | 19.7839 | 19683.8881 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 13.8669 | 19.5603 | 19460.2733 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 13.8669 | 19.7661 | 19666.0828 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 13.8669 | 19.8191 | 19719.1085 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.2586 | 52.0311 | 51931.1225 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.2586 | 50.8552 | 50755.2244 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 5.2586 | 46.9312 | 46831.1607 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 40.7282 | 16.1633 | 16063.3011 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 23.4524 | 2.359 | 2259.0316 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 23.4524 | 2.3044 | 2204.3648 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 35.1289 | 2.1451 | 2045.1099 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 653571 [GR ISLD3 345.00] CKT 1 | 35.1289 | 2.2031 | 2103.0945 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 10.3201 | 16.4124 | 16312.4301 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.2322 | 19.8362 | 19736.1657 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.2322 | 19.6111 | 19511.1367 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.2322 | 19.8182 | 19718.2451 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 14.2322 | 19.8716 | 19771.6459 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2511 | 52.3024 | 52202.402 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2511 | 51.1175 | 51017.5175 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 5.2511 | 47.1409 | 47040.8729 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 40.7338 | 16.1631 | 16063.0954 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 23.4605 | 2.3589 | 2258.9455 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 23.4605 | 2.3042 | 2204.2493 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 35.1416 | 2.1462 | 2046.1604 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 763410 [G18-125-TAP 345.00] CKT 1 | 35.1416 | 2.2042 | 2104.1801 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 10.3184 | 16.4139 | 16313.8715 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.0644 | 19.7703 | 19670.3365 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.0644 | 19.5473 | 19447.2544 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.0644 | 19.7525 | 19652.5152 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 15.0644 | 19.8054 | 1970535% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.276 | 51.8953 | 51795.3269 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.276 | 50.7221 | 5062209% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 5.276 | 46.8285 | 46728.5128 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 39.2521 | 16.2011 | 16101.0772 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 23.359 | 2.3593 | 2259.2983 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 23.359 | 2.3048 | 2204.8014 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 35.1664 | 2.1463 | 2046.2848 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 646226 [S1226 5 161.00] CKT 1 | 35.1664 | 2.2043 | 2104.3052 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 10.3217 | 16.4129 | 16312.9439 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.076 | 19.7826 | 19682.5924 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.076 | 19.5593 | 19459.2701 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.076 | 19.7647 | 19664.7449 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 15.076 | 19.8176 | 19717.637 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.2776 | 51.9088 | 51808.8446 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.2776 | 50.7346 | 50634.5559 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 5.2776 | 46.84 | 46740.0005 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 40.7439 | 16.1632 | 16063.1638 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 23.4687 | 2.3594 | 2259.4029 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 23.4687 | 2.3047 | 2204.6532 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 35.2095 | 2.1485 | 2048.4968 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640394 [VALTN.W7 115.00] CKT 1 | 35.2095 | 2.2066 | 2106.5969 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 10.321 | 16.4124 | 16312.3591 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.0633 | 19.7693 | 19669.2606 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.0633 | 19.5462 | 19446.2 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.0633 | 19.7514 | 19651.4436 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 15.0633 | 19.8043 | 19704.2784 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.2759 | 51.894 | 51794.0329 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.2759 | 50.7209 | 50620.907 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 5.2759 | 46.8274 | 46727.4095 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 40.7412 | 16.163 | 16062.9591 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 23.4677 | 2.359 | 2259.0011 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 23.4677 | 2.3043 | 2204.2761 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 35.1998 | 2.1464 | 2046.4226 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 640395 [VALTN.W9 12.500] CKT 1 | 35.1998 | 2.2044 | 2104.4429 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.3152 | 16.4205 | 16320.461 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1119 | 19.8389 | 19738.8815 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1119 | 19.6144 | 19514.4388 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1119 | 19.8209 | 19720.9055 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1119 | 19.8741 | 19774.0528 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2819 | 51.9722 | 51872.171 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2819 | 50.7936 | 50693.6006 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2819 | 46.8928 | 46792.8096 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 40.5905 | 16.168 | 16068.0413 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.3295 | 2.3599 | 2259.9305 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.3295 | 2.3057 | 2205.6505 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.9761 | 2.15 | 2049.9774 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.9761 | 2.2083 | 2108.3146 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.3115 | 16.42 | 16319.9824 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1094 | 19.84 | 19740.0451 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1094 | 19.6156 | 19515.5754 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1094 | 19.8221 | 19722.066 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.1094 | 19.8752 | 19775.2198 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2817 | 51.9766 | 51876.588 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2817 | 50.7979 | 50697.8714 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2817 | 46.8962 | 46796.2216 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 40.5486 | 16.1682 | 16068.2193 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.2971 | 2.3584 | 2258.398 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.2971 | 2.3043 | 2204.3173 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.6732 | 2.1369 | 2036.8977 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 645458 [S3458 3 345.00] CKT 1 | 33.6732 | 2.1948 | 2094.7668 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 10.2994 | 16.4504 | 16350.3989 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0511 | 19.7583 | 19658.3145 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0511 | 19.5355 | 19435.4557 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0511 | 19.7405 | 19640.5212 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 15.0511 | 19.7933 | 19693.3131 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2734 | 51.8846 | 51784.5792 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2734 | 50.7127 | 50612.7069 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 5.2734 | 46.8184 | 46718.4354 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 39.5476 | 16.2278 | 16127.8067 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 8.1641 | 2.4906 | 2390.6249 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 8.1641 | 2.4683 | 2368.319 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 34.9647 | 2.1564 | 2056.3549 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762779 [G18-043-TAP 345.00] CKT 1 | 34.9647 | 2.2149 | 2114.8508 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 10.3099 | 16.4222 | 16322.2287 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0615 | 19.7699 | 19669.8569 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0615 | 19.5468 | 19446.7855 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0615 | 19.752 | 19652.0367 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 15.0615 | 19.8049 | 19704.8738 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2758 | 51.8946 | 51794.5867 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2758 | 50.7214 | 50621.3925 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 5.2758 | 46.8279 | 46727.8822 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 40.3983 | 16.1762 | 16076.2409 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.187 | 2.3609 | 2260.8718 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 23.187 | 2.3072 | 2207.1878 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.2293 | 2.1482 | 2048.1507 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645458 [S3458 3 345.00] CKT 1 | 34.2293 | 2.2062 | 2106.2157 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 10.309 | 16.4192 | 16319.2365 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.0604 | 19.767 | 19666.9735 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.0604 | 19.544 | 19443.958 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.0604 | 19.7492 | 19649.1612 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 15.0604 | 19.802 | 19701.9858 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.2755 | 51.8913 | 51791.2779 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.2755 | 50.7184 | 50618.377 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 5.2755 | 46.8251 | 46725.0779 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 40.4864 | 16.1714 | 16071.363 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 23.2502 | 2.3591 | 2259.0979 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 23.2502 | 2.3051 | 2205.1368 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 34.3951 | 2.1517 | 2051.6885 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 645740 [S3740 3 345.00] CKT 1 | 34.3951 | 2.2099 | 2109.913 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 6.6391 | 31.9315 | 31831.4919 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.0639 | 19.7702 | 19670.1886 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.0639 | 19.5471 | 19447.1078 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.0639 | 19.7524 | 19652.3677 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 15.0639 | 19.8052 | 19705.2066 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.276 | 51.8955 | 51795.5148 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.276 | 50.7223 | 50622.3 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 5.276 | 46.8287 | 46728.6605 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 40.7416 | 16.1629 | 16062.9431 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 23.4695 | 2.359 | 2259.0494 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 23.4695 | 2.3043 | 2204.3125 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 35.1975 | 2.1472 | 2047.2499 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 647014 [S914A 8 69.000] TO BUS 648214 [S1214T19 13.800] CKT 1 | 35.1975 | 2.2053 | 2105.3018 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 10.3206 | 16.412 | 16312.0228 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.0637 | 19.7697 | 19669.7391 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.0637 | 19.5467 | 19446.6687 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.0637 | 19.7519 | 19651.9206 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 15.0637 | 19.8048 | 19704.7578 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.2759 | 51.8946 | 51794.5838 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.2759 | 50.7214 | 50621.4239 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 5.2759 | 46.8279 | 46727.8775 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 39.8864 | 16.1768 | 16076.8124 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 23.3966 | 2.3576 | 2257.56 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 23.3966 | 2.303 | 2202.9534 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 35.1987 | 2.1465 | 2046.5299 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646252 [S1252 5 161.00] CKT 1 | 35.1987 | 2.2046 | 2104.5549 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 10.2377 | 16.4784 | 16378.372 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.0648 | 19.7707 | 19670.7343 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.0648 | 19.5476 | 19447.643 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.0648 | 19.7529 | 19652.9121 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 15.0648 | 19.8058 | 19705.7534 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.2761 | 51.8959 | 51795.8872 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.2761 | 50.7226 | 50622.6499 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 5.2761 | 46.829 | 46728.9568 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 40.0736 | 16.1822 | 16082.203 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 23.3692 | 2.3606 | 2260.5702 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 23.3692 | 2.3059 | 2205.9121 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 35.1884 | 2.1464 | 2046.4431 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646291 [S1291 5 161.00] CKT 1 | 35.1884 | 2.2045 | 2104.4649 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 10.3198 | 16.4138 | 16313.8057 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.0639 | 19.7699 | 19669.8536 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.0639 | 19.5468 | 19446.7809 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.0639 | 19.752 | 19652.0333 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 15.0639 | 19.8049 | 19704.8708 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.2759 | 51.8948 | 51794.7504 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.2759 | 50.7216 | 50621.581 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 5.2759 | 46.828 | 46728.0234 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 38.9219 | 16.2306 | 16130.5802 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 23.3792 | 2.3585 | 2258.5291 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 23.3792 | 2.3039 | 2203.8802 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 35.199 | 2.1464 | 2046.4196 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 1 | 35.199 | 2.2044 | 2104.4401 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 10.3198 | 16.4138 | 16313.8057 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.0639 | 19.7699 | 19669.8536 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.0639 | 19.5468 | 19446.7809 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.0639 | 19.752 | 19652.0333 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 15.0639 | 19.8049 | 19704.8708 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.2759 | 51.8948 | 51794.7504 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.2759 | 50.7216 | 50621.581 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 5.2759 | 46.828 | 46728.0234 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 38.9219 | 16.2306 | 16130.5802 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 23.3792 | 2.3585 | 2258.5291 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 23.3792 | 2.3039 | 2203.8802 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 35.199 | 2.1464 | 2046.4196 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 646298 [S1298 5 161.00] CKT 2 | 35.199 | 2.2044 | 2104.4401 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 10.3208 | 16.4122 | 16312.1843 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.7698 | 19669.7931 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.5467 | 19446.7216 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.752 | 19651.973 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.8048 | 19704.8102 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.2759 | 51.8947 | 51794.6716 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.2759 | 50.7215 | 50621.5054 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.2759 | 46.828 | 46727.9541 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 38.2059 | 16.2417 | 16141.7497 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 23.4674 | 2.3589 | 2258.8797 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 23.4674 | 2.3042 | 2204.1609 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 35.2001 | 2.1464 | 2046.4452 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 35.2001 | 2.2045 | 2104.4664 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 10.3207 | 16.4124 | 16312.3786 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.0638 | 19.7698 | 19669.7987 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.0638 | 19.5467 | 19446.727 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.0638 | 19.752 | 19651.9786 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 15.0638 | 19.8048 | 19704.8158 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.2759 | 51.8947 | 51794.6897 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.2759 | 50.7215 | 50621.5235 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 5.2759 | 46.828 | 46727.9642 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 37.1772 | 16.2756 | 16175.6431 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 23.431 | 2.3592 | 2259.215 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 23.431 | 2.3045 | 2204.5122 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 35.1985 | 2.1465 | 2046.4805 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 646367 [S1367 5 161.00] CKT 1 | 35.1985 | 2.2045 | 2104.5038 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 10.3208 | 16.4122 | 16312.2213 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.7698 | 19669.8118 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.5467 | 19446.7399 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.752 | 19651.9917 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 15.0639 | 19.8048 | 19704.8289 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.276 | 51.8947 | 51794.7017 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.276 | 50.7215 | 50621.5337 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 5.276 | 46.828 | 46727.9787 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 38.209 | 16.2448 | 16144.7787 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 23.4676 | 2.3589 | 225887% | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 23.4676 | 2.3042 | 2204.1537 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 35.2001 | 2.1464 | 2046.4387 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646345 [S1345 5 161.00] CKT 1 | 35.2001 | 2.2045 | 2104.4597 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 9.6742 | 16.5168 | 16416.7697 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.0634 | 19.7694 | 19669.3828 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.0634 | 19.5463 | 19446.3194 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.0634 | 19.7516 | 19651.5651 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 15.0634 | 19.8044 | 19704.4004 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.2759 | 51.8942 | 51794.1785 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.2759 | 50.721 | 50621.0419 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 5.2759 | 46.8275 | 46727.5246 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 40.7361 | 16.1625 | 16062.4525 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 23.4671 | 2.3584 | 2258.3995 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 23.4671 | 2.3037 | 2203.7128 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 35.1989 | 2.146 | 2046.0354 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647914 [S914 8 69.000] CKT 1 | 35.1989 | 2.204 | 2104.0409 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 10.3222 | 16.3989 | 16298.8927 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.0634 | 19.7693 | 19669.2878 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.0634 | 19.5462 | 19446.2263 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.0634 | 19.7515 | 19651.4689 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 15.0634 | 19.8043 | 19704.3038 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.2759 | 51.8942 | 51794.2256 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.2759 | 50.7211 | 50621.0846 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 5.2759 | 46.8276 | 46727.5641 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 40.7412 | 16.163 | 16062.9899 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 23.4673 | 2.3591 | 2259.0713 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 23.4673 | 2.3043 | 2204.3372 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 35.1993 | 2.1465 | 2046.4553 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647988 [S988 8 69.000] CKT 1 | 35.1993 | 2.2045 | 2104.4766 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 6.0728 | 21.591 | 21490.9896 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.0639 | 19.77 | 19670.0362 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.0639 | 19.547 | 19446.9597 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.0639 | 19.7522 | 19652.217 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 15.0639 | 19.8051 | 19705.0552 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.276 | 51.8952 | 51795.1614 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.276 | 50.722 | 50621.9674 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 5.276 | 46.8284 | 46728.3603 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 40.727 | 16.1631 | 16063.0967 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 23.4663 | 2.3585 | 2258.5432 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 23.4663 | 2.3039 | 2203.8577 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 35.1942 | 2.1464 | 2046.399 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647983 [S983 8 69.000] CKT 1 | 35.1942 | 2.2044 | 2104.4193 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 10.3135 | 16.4208 | 16320.7536 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.0432 | 19.7696 | 19669.6427 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.0432 | 19.5466 | 19446.5757 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.0432 | 19.7518 | 19651.8242 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 15.0432 | 19.8047 | 19704.6599 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2747 | 51.9024 | 51802.3823 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2747 | 50.729 | 50628.9897 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 5.2747 | 46.834 | 46733.989 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 40.6511 | 16.1669 | 16066.9038 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 23.3808 | 2.3598 | 2259.7644 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 23.3808 | 2.3054 | 2205.403 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 32.0142 | 2.1547 | 2054.6977 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650189 [103&ROKEBY3 345.00] CKT 1 | 32.0142 | 2.2132 | 2113.1516 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 10.3251 | 16.4174 | 16317.3705 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.0893 | 19.7966 | 19696.6011 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.0893 | 19.573 | 19473.0051 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.0893 | 19.7787 | 19678.7204 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 15.0893 | 19.8317 | 19731.6757 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.2789 | 51.9195 | 51819.5488 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.2789 | 50.7444 | 50644.38 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 5.2789 | 46.8492 | 46749.2291 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 40.7666 | 16.1676 | 16067.5568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 23.5043 | 2.3758 | 2275.7574 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 23.5043 | 2.3215 | 2221.5274 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 35.2385 | 2.1548 | 2054.7687 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762782 [G18-043-GSU134.500] CKT 1 | 35.2385 | 2.2131 | 2113.1141 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 10.3251 | 16.4174 | 16317.3705 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.0893 | 19.7966 | 19696.6011 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.0893 | 19.573 | 19473.0051 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.0893 | 19.7787 | 19678.7204 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 15.0893 | 19.8317 | 19731.6757 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.2789 | 51.9195 | 51819.5488 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.2789 | 50.7444 | 50644.38 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 5.2789 | 46.8492 | 46749.2291 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 40.7666 | 16.1676 | 16067.5568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 23.5043 | 2.3758 | 2275.7574 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 23.5043 | 2.3215 | 2221.5274 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 35.2385 | 2.1548 | 2054.7687 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762785 [G18-043-GSU234.500] CKT 1 | 35.2385 | 2.2131 | 2113.1141 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 10.325 | 16.4173 | 16317.3384 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.0891 | 19.7965 | 19696.46 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.0891 | 19.5729 | 19472.8666 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.0891 | 19.7786 | 19678.5796 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 15.0891 | 19.8315 | 19731.534 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.2789 | 51.9194 | 51819.4095 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.2789 | 50.7442 | 50644.2487 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 5.2789 | 46.8491 | 46749.1079 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 40.7664 | 16.1675 | 16067.5279 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 23.5039 | 2.3756 | 2275.5973 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 23.5039 | 2.3214 | 2221.3697 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 35.2382 | 2.1547 | 2054.7192 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762788 [G18-043-GSU334.500] CKT 1 | 35.2382 | 2.2131 | 2113.0627 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 10.3196 | 16.4116 | 16311.599 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 14.4172 | 19.8981 | 19798.1081 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 14.4172 | 19.672 | 19572.0319 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 14.4172 | 19.88 | 19780.0328 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 14.4172 | 19.9336 | 19833.635 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.2614 | 52.3495 | 52249.5354 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.2614 | 51.1582 | 51058.2417 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 5.2614 | 47.1857 | 47085.7069 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 40.7324 | 16.1626 | 16062.6022 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 23.4622 | 2.3582 | 2258.1964 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 23.4622 | 2.3035 | 2203.5329 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 35.1484 | 2.141 | 2041.0388 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 35.1484 | 2.1989 | 2098.8558 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 10.3194 | 16.4113 | 16311.2554 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 14.5129 | 19.8523 | 19752.3154 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 14.5129 | 19.6274 | 19527.4414 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 14.5129 | 19.8343 | 19734.3352 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 14.5129 | 19.8876 | 19787.6187 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.2624 | 52.2578 | 52157.834 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.2624 | 51.0703 | 50970.2914 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 5.2624 | 47.1141 | 47014.0965 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 40.7327 | 16.1625 | 16062.5286 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 23.4629 | 2.3581 | 2258.092 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 23.4629 | 2.3034 | 2203.4302 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 35.1562 | 2.1408 | 2040.8258 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 35.1562 | 2.1986 | 2098.6327 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 10.3106 | 16.4096 | 16309.5712 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 14.936 | 19.6507 | 19550.729 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 14.936 | 19.43 | 19329.9714 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 14.936 | 19.6332 | 19533.1787 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 14.936 | 19.6855 | 19585.4998 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.2616 | 51.7956 | 51695.6264 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.2616 | 50.6311 | 50531.092 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 5.2616 | 46.7421 | 46642.1454 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 40.6463 | 16.1638 | 16063.8343 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 23.3895 | 2.3572 | 2257.2068 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 23.3895 | 2.3028 | 2202.7685 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 34.4507 | 2.1299 | 2029.9178 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541197 [MULLNCR7 345.00] CKT 1 | 34.4507 | 2.1873 | 2087.348 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 10.32 | 16.4126 | 16312.5787 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.0903 | 19.7975 | 19697.4631 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.0903 | 19.5738 | 19473.847 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.0903 | 19.7796 | 19679.5804 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 15.0903 | 19.8325 | 19732.54 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.2788 | 51.921 | 51820.9767 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.2788 | 50.7458 | 50645.812 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 5.2788 | 46.8503 | 46750.2634 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 40.7354 | 16.1632 | 16063.1658 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 23.4662 | 2.3579 | 2257.9391 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 23.4662 | 2.3034 | 2203.3548 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 35.1844 | 2.1392 | 2039.1863 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541511 [ROCKCK7 345.00] CKT 1 | 35.1844 | 2.197 | 2096.9545 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 10.3216 | 16.4129 | 16312.8811 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.0647 | 19.7709 | 19670.8748 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.0647 | 19.5478 | 19447.7821 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.0647 | 19.7531 | 19653.0522 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 15.0647 | 19.8059 | 19705.8944 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.2761 | 51.8959 | 51795.9034 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.2761 | 50.7226 | 50622.6326 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 5.2761 | 46.829 | 46729.0033 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 40.7429 | 16.1632 | 16063.1953 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 23.4677 | 2.3594 | 2259.4279 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 23.4677 | 2.3047 | 2204.6794 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 35.2041 | 2.1495 | 2049.5373 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 541517 [HOLT_REACT7 345.00] CKT Z1 | 35.2041 | 2.2077 | 2107.6789 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 10.3207 | 16.412 | 16312.0379 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.0636 | 19.7692 | 19669.169 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.0636 | 19.5461 | 19446.1102 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.0636 | 19.7514 | 19651.3504 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 15.0636 | 19.8042 | 19704.1849 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.2759 | 51.8939 | 51793.92 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.2759 | 50.7208 | 50620.8316 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 5.2759 | 46.8273 | 46727.3316 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 40.7399 | 16.1628 | 16062.8104 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 23.4676 | 2.3587 | 2258.7298 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 23.4676 | 2.304 | 2204.0195 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 35.1981 | 2.1444 | 2044.3746 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 541510 [HOLT 7 345.00] TO BUS 760746 [GEN-2017-115345.00] CKT 1 | 35.1981 | 2.2023 | 2102.3154 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3142 | 16.4089 | 16308.8964 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.4549 | 20.3848 | 20284.8244 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.4549 | 20.1469 | 20046.9228 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.4549 | 20.3658 | 20265.8112 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 12.4549 | 20.4225 | 20322.4985 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1986 | 54.6921 | 54592.1006 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1986 | 53.4118 | 53311.7677 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1986 | 49.0035 | 48903.54 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 40.6998 | 16.1617 | 16061.6812 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4404 | 2.3557 | 2255.7136 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4404 | 2.3013 | 2201.2637 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 34.9683 | 2.1251 | 2025.1299 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 560082 [G16-050-TAP 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 34.9683 | 2.1824 | 2082.3543 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 10.321 | 16.4124 | 16312.4045 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.0239 | 19.7208 | 19620.805 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.0239 | 19.4982 | 19398.2439 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.0239 | 19.7031 | 19603.1238 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 15.0239 | 19.7559 | 19655.9305 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.2675 | 52.119 | 52019.0455 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.2675 | 50.942 | 50841.9866 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 5.2675 | 46.9961 | 46896.0616 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 40.7426 | 16.1631 | 16063.0938 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 23.4684 | 2.3592 | 2259.1677 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 23.4684 | 2.3044 | 220444% | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 35.2058 | 2.1472 | 2047.2242 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 587351 [G16-050XFMR134.500] CKT 1 | 35.2058 | 2.2053 | 210528% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 10.3211 | 16.4125 | 16312.4804 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 14.9437 | 19.7776 | 19677.5796 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 14.9437 | 19.5543 | 19454.2509 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 14.9437 | 19.7597 | 19659.7481 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 14.9437 | 19.8127 | 19712.6621 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.2717 | 51.9591 | 51859.0563 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.2717 | 50.7839 | 50683.9034 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 5.2717 | 46.8777 | 46777.6941 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 40.7413 | 16.163 | 16063.0173 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 23.4673 | 2.3591 | 2259.0961 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 23.4673 | 2.3044 | 2204.3665 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 35.1983 | 2.147 | 2047.0033 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587350 [GEN-2016-050345.00] TO BUS 762955 [G18-060-XFM134.500] CKT 1 | 35.1983 | 2.205 | 2105.0464 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 10.322 | 16.4132 | 16313.2407 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.1061 | 19.8258 | 19725.8287 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.1061 | 19.6015 | 19501.4847 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.1061 | 19.8079 | 19707.8921 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 15.1061 | 19.861 | 19761.0463 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.2795 | 52.078 | 51977.9883 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.2795 | 50.8972 | 50797.2027 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 5.2795 | 46.9728 | 46872.7737 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 40.7451 | 16.1633 | 16063.3024 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 23.4691 | 2.3596 | 2259.5868 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 23.4691 | 2.3048 | 2204.8316 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 35.2174 | 2.1501 | 2050.1206 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 587680 [GEN-2016-074345.00] TO BUS 587681 [G16-074XFMR134.500] CKT 1 | 35.2174 | 2.2083 | 2108.2855 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 10.3193 | 16.4139 | 16313.9449 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.0577 | 19.767 | 19666.9545 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.0577 | 19.5439 | 19443.932 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.0577 | 19.7491 | 19649.142 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 15.0577 | 19.802 | 19701.9684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.2753 | 51.8992 | 51799.1553 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.2753 | 50.726 | 50625.957 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 5.2753 | 46.8312 | 46731.1641 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 40.688 | 16.166 | 16065.9545 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 23.2551 | 2.3621 | 2262.114 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 23.2551 | 2.3081 | 2208.1034 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 35.176 | 2.1454 | 2045.4217 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 87487 [J748POI 345.00] CKT 1 | 35.176 | 2.2034 | 2103.411 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 10.3209 | 16.4125 | 16312.4721 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.0635 | 19.7693 | 19669.3461 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.0635 | 19.5463 | 19446.2834 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.0635 | 19.7515 | 19651.527 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 15.0635 | 19.8044 | 19704.3622 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.2759 | 51.8942 | 51794.1564 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.2759 | 50.7211 | 50621.0554 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 5.2759 | 46.8275 | 46727.5113 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 40.7281 | 16.1633 | 16063.3264 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 23.4609 | 2.3581 | 2258.1134 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 23.4609 | 2.3033 | 2203.335 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 35.2002 | 2.1463 | 2046.3436 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] CKT 2 | 35.2002 | 2.2044 | 2104.3607 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 10.325 | 16.4203 | 16320.2894 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.1239 | 19.8415 | 19741.4633 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.1239 | 19.617 | 19516.9835 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.1239 | 19.8235 | 19723.4807 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 15.1239 | 19.8766 | 19776.6348 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.2835 | 51.9674 | 51867.4297 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.2835 | 50.7886 | 50688.608 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 5.2835 | 46.8898 | 46789.8172 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 40.6371 | 16.1684 | 16068.3902 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 23.0033 | 2.3675 | 2267.5073 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 23.0033 | 2.3134 | 2213.4218 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 35.22 | 2.1639 | 2063.8628 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635213 [NEAL 3G 22.000] CKT 1 | 35.22 | 2.2226 | 2122.5634 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 10.3255 | 16.4225 | 16322.5128 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.1385 | 19.86 | 19760.0325 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.1385 | 19.6352 | 19535.1878 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.1385 | 19.842 | 19742.0077 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 15.1385 | 19.8952 | 19795.2444 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.2853 | 51.987 | 51887.0239 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.2853 | 50.8067 | 50706.7273 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 5.2853 | 46.9064 | 46806.4161 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 40.5939 | 16.1702 | 16070.1563 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 22.8298 | 2.3701 | 2270.0523 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 22.8298 | 2.3163 | 2216.3163 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 35.2173 | 2.1681 | 2068.1493 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635214 [NEAL 4G 24.000] CKT 1 | 35.2173 | 2.227 | 2127.0188 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 10.3197 | 16.412 | 16311.9745 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.0558 | 19.7629 | 19662.9202 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.0558 | 19.54 | 19439.9793 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.0558 | 19.7451 | 19645.1155 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 15.0558 | 19.7979 | 19697.9234 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.2749 | 51.891 | 51791.0472 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.2749 | 50.7184 | 50618.372 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 5.2749 | 46.8245 | 46724.5476 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 40.7213 | 16.1636 | 16063.6071 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 23.3473 | 2.3594 | 2259.3721 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 23.3473 | 2.305 | 2205.0201 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 35.1923 | 2.1447 | 2044.7264 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635252 [J412 POI 3 345.00] CKT 1 | 35.1923 | 2.2027 | 2102.6833 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 10.3209 | 16.4123 | 16312.2581 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 14.9842 | 19.7679 | 19667.935 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 14.9842 | 19.5448 | 19444.8496 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 14.9842 | 19.7501 | 19650.122 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 14.9842 | 19.803 | 19702.971 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.2682 | 51.959 | 51859.0032 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.2682 | 50.784 | 50683.9734 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 5.2682 | 46.8774 | 46777.4205 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 40.7321 | 16.1634 | 16063.3708 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 23.2563 | 2.3603 | 2260.2984 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 23.2563 | 2.3057 | 2205.7072 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 35.1396 | 2.1461 | 2046.08 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 640226 [HOSKINS3 345.00] CKT 1 | 35.1396 | 2.2041 | 2104.0943 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 10.3189 | 16.4115 | 16311.4904 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.0675 | 19.7738 | 19673.7762 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.0675 | 19.5506 | 19450.6274 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.0675 | 19.7559 | 19655.9471 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 15.0675 | 19.8088 | 19708.8019 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.2766 | 51.8996 | 51799.6296 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.2766 | 50.726 | 50626.0475 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 5.2766 | 46.8322 | 46732.2337 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 40.6871 | 16.1626 | 16062.5722 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 23.1847 | 2.3564 | 2256.4401 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 23.1847 | 2.3019 | 2201.864 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 35.1793 | 2.1447 | 2044.7429 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 652564 [SIOUXCY3 345.00] CKT 1 | 35.1793 | 2.2027 | 2102.699 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 10.3209 | 16.4125 | 16312.4723 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.0635 | 19.7693 | 19669.3436 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.0635 | 19.5463 | 19446.281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.0635 | 19.7515 | 19651.5246 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 15.0635 | 19.8044 | 19704.3597 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.2759 | 51.8942 | 51794.1519 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.2759 | 50.721 | 50621.0172 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 5.2759 | 46.8275 | 46727.5076 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 40.7281 | 16.1633 | 16063.3283 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 23.4609 | 2.3581 | 2258.1147 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 23.4609 | 2.3033 | 2203.3359 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 35.2002 | 2.1463 | 2046.3434 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 635200 [RAUN 3 345.00] TO BUS 635201 [RAUN 5 161.00] TO BUS 635205 [RAUN1XT9 13.800] CKT 1 | 35.2002 | 2.2044 | 2104.3608 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 10.321 | 16.4124 | 16312.3961 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 13.5445 | 19.8145 | 19714.478 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 13.5445 | 19.5911 | 19491.053 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 13.5445 | 19.7966 | 19696.6016 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 13.5445 | 19.8495 | 19749.468 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.4895 | 485.2378 | 485137.8381 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.4895 | 396.0736 | 395973.6249 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 4.4895 | 153.6953 | 153595.3251 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 40.7411 | 16.163 | 16062.9701 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 23.4677 | 2.359 | 2259.0365 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 23.4677 | 2.3043 | 2204.3079 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 35.1983 | 2.1467 | 2046.7129 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640066 [AXTELL 7 115.00] TO BUS 640065 [AXTELL 3 345.00] TO BUS 640067 [AXTELL 9 13.800] CKT 1 | 35.1983 | 2.2047 | 2104.7435 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3707 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0636 | 19.7695 | 19669.4798 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0636 | 19.5464 | 19446.4142 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0636 | 19.7517 | 19651.6619 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0636 | 19.8045 | 19704.4977 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2759 | 51.8943 | 51794.2626 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2759 | 50.7211 | 50621.1215 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2759 | 46.8276 | 46727.603 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 40.7412 | 16.163 | 16062.9638 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 23.4677 | 2.359 | 2259.0092 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 23.4677 | 2.3043 | 2204.2836 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 35.2 | 2.1465 | 2046.4625 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640117 [CODY 7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 35.2 | 2.2045 | 2104.4844 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 10.3188 | 16.4136 | 16313.5982 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.0013 | 19.7153 | 19615.2658 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.0013 | 19.4933 | 19393.2549 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.0013 | 19.6976 | 19597.5696 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 15.0013 | 19.7502 | 19650.1713 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.2693 | 51.8545 | 51754.5277 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.2693 | 50.685 | 50585.0362 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 5.2693 | 46.7929 | 46692.919 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 40.7068 | 16.1638 | 16063.7659 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 23.437 | 2.359 | 2258.9926 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 23.437 | 2.3043 | 2204.3472 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 34.9333 | 2.1428 | 2042.8023 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 300039 [7FAIRPT 345.00] CKT 1 | 34.9333 | 2.2007 | 2100.6978 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 10.3173 | 16.4143 | 16314.3435 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 14.9413 | 19.6618 | 19561.849 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 14.9413 | 19.4409 | 19340.8746 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 14.9413 | 19.6443 | 19544.2737 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 14.9413 | 19.6966 | 19596.6437 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.263 | 51.8127 | 51712.7284 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.263 | 50.6469 | 50546.9239 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 5.263 | 46.7567 | 46656.6577 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 40.682 | 16.1643 | 16064.3052 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 23.4141 | 2.3591 | 2259.103 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 23.4141 | 2.3045 | 2204.4981 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 34.7795 | 2.1421 | 2042.1439 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 541199 [ST JOE 7 345.00] CKT 1 | 34.7795 | 2.2 | 2100.0216 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 10.3182 | 16.4103 | 16310.3151 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.0511 | 19.7644 | 19664.4174 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.0511 | 19.5414 | 19441.4384 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.0511 | 19.7466 | 19646.61 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 15.0511 | 19.7994 | 19699.428 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.2746 | 51.902 | 51801.9861 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.2746 | 50.7289 | 50628.9182 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 5.2746 | 46.8331 | 46733.0713 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 40.7241 | 16.162 | 16062.0249 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 23.455 | 2.3571 | 2257.0615 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 23.455 | 2.3025 | 2202.4544 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 34.9626 | 2.1332 | 2033.219 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 635017 [ATCHSN 3 345.00] CKT 1 | 34.9626 | 2.1908 | 2090.7565 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 10.3099 | 16.4146 | 1631459% | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.1087 | 19.849 | 19749.0494 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.1087 | 19.6244 | 1952439% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.1087 | 19.8311 | 19731.0508 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 15.1087 | 19.8842 | 19784.2494 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.2816 | 51.9918 | 51891.7682 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.2816 | 50.8123 | 50712.3484 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 5.2816 | 46.9083 | 46808.3224 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 40.6038 | 16.1655 | 16065.5496 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 23.3473 | 2.3573 | 2257.2559 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 23.3473 | 2.3031 | 2203.057 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 34.3382 | 2.1336 | 2033.634 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640009 [COOPER1G 22.000] CKT 1 | 34.3382 | 2.1913 | 2091.2927 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.3201 | 16.4159 | 16315.8631 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8766 | 19.7661 | 19666.1237 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8766 | 19.543 | 19442.9603 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8766 | 19.7483 | 19648.3206 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8766 | 19.8012 | 19701.208 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.2616 | 52.0852 | 51985.1811 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.2616 | 50.9063 | 50806.3068 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.2616 | 46.9747 | 46874.7161 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 40.7314 | 16.1633 | 16063.2966 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 23.4565 | 2.359 | 2259.0276 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 23.4565 | 2.3044 | 2204.372 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 34.8963 | 2.1475 | 2047.5382 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 34.8963 | 2.2057 | 2105.6689 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 10.3201 | 16.4122 | 16312.2187 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.0637 | 19.7697 | 19669.6613 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.0637 | 19.5466 | 19446.5925 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.0637 | 19.7518 | 19651.8416 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 15.0637 | 19.8047 | 19704.6784 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.2759 | 51.8946 | 51794.6124 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.2759 | 50.7215 | 50621.451 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 5.2759 | 46.8279 | 46727.9033 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 40.7392 | 16.1629 | 16062.9447 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 23.4671 | 2.3589 | 2258.9225 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 23.4671 | 2.3042 | 2204.2064 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 35.198 | 2.1466 | 2046.6499 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 640142 [COOPER T2 913.800] CKT 1 | 35.198 | 2.2047 | 2104.6782 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 10.3202 | 16.4122 | 16312.2311 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.0637 | 19.7697 | 19669.6638 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.0637 | 19.5466 | 19446.5949 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.0637 | 19.7518 | 19651.844 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 15.0637 | 19.8047 | 19704.6808 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.2759 | 51.8946 | 51794.6083 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.2759 | 50.7214 | 50621.4471 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 5.2759 | 46.8279 | 46727.9 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 40.7393 | 16.1629 | 16062.9466 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 23.4671 | 2.3589 | 2258.9278 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 23.4671 | 2.3042 | 2204.2111 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 35.1981 | 2.1466 | 2046.6231 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640139 [COOPER 3 345.00] TO BUS 640140 [COOPER 5 161.00] TO BUS 643172 [COOPER T5 913.800] CKT 1 | 35.1981 | 2.2047 | 2104.6503 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 10.3253 | 16.4169 | 16316.8526 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 14.6409 | 19.9878 | 19887.7642 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 14.6409 | 19.7599 | 19659.8751 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 14.6409 | 19.9695 | 19869.4778 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 14.6409 | 20.0235 | 19923.4928 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.2483 | 52.8881 | 52788.1145 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.2483 | 51.6729 | 51572.9121 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 5.2483 | 47.6126 | 47512.6462 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 40.7507 | 16.1647 | 16064.7413 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 23.4607 | 2.3621 | 2262.1309 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 23.4607 | 2.3072 | 2207.2395 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 35.2179 | 2.1651 | 2065.1395 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640011 [GENTLM2G 24.000] CKT 1 | 35.2179 | 2.2239 | 2123.8893 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 10.321 | 16.4124 | 16312.4361 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 14.9827 | 19.7767 | 19676.7177 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 14.9827 | 19.5535 | 19453.4841 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 14.9827 | 19.7589 | 19658.885 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 14.9827 | 19.8118 | 19711.7649 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.2729 | 51.9451 | 51845.0589 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.2729 | 50.7699 | 50669.9322 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 5.2729 | 46.8676 | 46767.6071 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 40.7401 | 16.163 | 16062.994 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 23.4661 | 2.359 | 2259.026 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 23.4661 | 2.3043 | 2204.3026 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 35.1919 | 2.1466 | 2046.6225 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640252 [KEYSTON3 345.00] CKT 1 | 35.1919 | 2.2047 | 2104.6513 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 10.3159 | 16.4083 | 16308.3491 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 14.8328 | 19.5439 | 19443.916 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 14.8328 | 19.3253 | 19225.2621 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 14.8328 | 19.5266 | 19426.6035 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 14.8328 | 19.5785 | 19478.4524 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.2366 | 51.6417 | 51541.6595 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.2366 | 50.4924 | 50392.3577 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 5.2366 | 46.6059 | 46505.8549 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 40.7213 | 16.1617 | 16061.682 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 23.4589 | 2.3563 | 2256.3103 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 23.4589 | 2.3018 | 2201.7666 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 35.1163 | 2.1298 | 2029.7911 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 35.1163 | 2.1872 | 2087.1756 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 10.321 | 16.4127 | 16312.733 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.038 | 19.7607 | 19660.7379 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.038 | 19.5379 | 19437.8522 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.038 | 19.7429 | 19642.9395 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 15.038 | 19.7957 | 19695.7342 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.2743 | 51.8953 | 51795.2961 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.2743 | 50.7226 | 50622.5671 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 5.2743 | 46.8279 | 46727.8622 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 40.7348 | 16.1631 | 16063.1366 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 23.4537 | 2.3592 | 2259.2177 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 23.4537 | 2.3045 | 2204.5022 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 35.1896 | 2.1469 | 2046.8526 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640500 [THEDFRD3 345.00] CKT 1 | 35.1896 | 2.2049 | 2104.8907 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 10.321 | 16.4124 | 16312.3589 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.0323 | 19.7687 | 19668.7294 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.0323 | 19.5457 | 19445.6743 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.0323 | 19.7509 | 19650.9123 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 15.0323 | 19.8037 | 19703.7465 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.275 | 51.8887 | 51788.6647 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.275 | 50.716 | 50616.0361 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 5.275 | 46.8228 | 46722.757 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 40.7409 | 16.163 | 16062.9649 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 23.4672 | 2.359 | 2259.0046 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 23.4672 | 2.3043 | 2204.2802 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 35.1974 | 2.1464 | 2046.3971 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 640185 [G.GENT19 13.800] CKT 1 | 35.1974 | 2.2044 | 2104.4168 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 10.321 | 16.4124 | 16312.362 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.0354 | 19.7688 | 19668.81 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.0354 | 19.5458 | 19445.7547 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.0354 | 19.751 | 19650.9927 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 15.0354 | 19.8038 | 19703.8285 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.2751 | 51.8893 | 51789.3196 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.2751 | 50.7166 | 50616.6217 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 5.2751 | 46.8233 | 46723.3212 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 40.7409 | 16.163 | 16062.966 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 23.4672 | 2.359 | 2259.006 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 23.4672 | 2.3043 | 2204.2813 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 35.1977 | 2.1464 | 2046.4085 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640184 [GENTLMN4 230.00] TO BUS 643066 [GENTLEMANT2913.800] CKT 2 | 35.1977 | 2.2044 | 2104.4286 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 10.3208 | 16.4123 | 16312.3033 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.0544 | 19.7629 | 19662.9137 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.0544 | 19.54 | 19440.0174 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.0544 | 19.7451 | 19645.1077 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 15.0544 | 19.7979 | 19697.8988 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.2693 | 50.6335 | 50533.4563 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.2693 | 49.5046 | 49404.5768 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 5.2693 | 45.847 | 45746.9876 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 40.7402 | 16.1629 | 16062.9346 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 23.4671 | 2.359 | 2258.9528 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 23.4671 | 2.3042 | 2204.2304 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 35.1969 | 2.1461 | 2046.0727 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640222 [HILDRTH7 115.00] TO BUS 640223 [HILDRTH8 69.000] TO BUS 643079 [HILDRETH T1913.800] CKT 1 | 35.1969 | 2.2041 | 2104.0793 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 10.3229 | 16.414 | 16314.0303 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.1307 | 19.8782 | 19778.1675 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.1307 | 19.6526 | 19552.6294 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.1307 | 19.8601 | 19760.1174 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.1307 | 19.9136 | 19813.5687 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 40.7488 | 16.1636 | 16063.6157 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 23.4702 | 2.3602 | 2260.1771 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 23.4702 | 2.3054 | 2205.3846 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 35.2348 | 2.1542 | 2054.2145 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640224 [HOLDREG7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 35.2348 | 2.2125 | 2112.5369 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 10.3214 | 16.4126 | 16312.5572 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.0474 | 19.7794 | 19679.3659 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.0474 | 19.5561 | 19456.0693 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.0474 | 19.7615 | 19661.5262 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 15.0474 | 19.8144 | 19714.4214 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.2594 | 52.3159 | 52215.9134 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.2594 | 51.1281 | 51028.1306 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 5.2594 | 47.1557 | 47055.7147 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 40.7426 | 16.163 | 16063.0353 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 23.468 | 2.3591 | 2259.1378 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 23.468 | 2.3044 | 2204.4056 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 35.2014 | 2.1472 | 2047.2459 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640015 [JOHN.2 G 6.9000] CKT 1 | 35.2014 | 2.2053 | 2105.2987 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 10.3211 | 16.4124 | 16312.3913 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0638 | 19.7699 | 19669.9099 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0638 | 19.5468 | 19446.8359 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0638 | 19.7521 | 19652.091 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0638 | 19.8049 | 19704.9275 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.2613 | 52.1594 | 52059.3619 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.2613 | 50.9774 | 50877.4044 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.2613 | 47.0343 | 46934.2659 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 40.7414 | 16.163 | 16062.971 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 23.4677 | 2.359 | 2259.0212 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 23.4677 | 2.3043 | 2204.295 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 35.2001 | 2.1465 | 2046.5233 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 35.2001 | 2.2045 | 2104.5477 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 10.3211 | 16.4124 | 16312.3913 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.0638 | 19.7699 | 19669.9099 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.0638 | 19.5468 | 19446.8359 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.0638 | 19.7521 | 19652.091 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 15.0638 | 19.8049 | 19704.9275 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.2613 | 52.1594 | 52059.3619 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.2613 | 50.9774 | 50877.4044 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 5.2613 | 47.0343 | 46934.2659 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 40.7414 | 16.163 | 16062.971 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 23.4677 | 2.359 | 2259.0212 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 23.4677 | 2.3043 | 2204.295 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 35.2001 | 2.1465 | 2046.5233 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 2 | 35.2001 | 2.2045 | 2104.5477 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 10.3208 | 16.4123 | 16312.3398 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.0409 | 19.7673 | 19667.29 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.0409 | 19.5443 | 19444.2549 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.0409 | 19.7495 | 19649.4773 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 15.0409 | 19.8023 | 19702.3089 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.2226 | 52.3096 | 52209.6382 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.2226 | 51.1244 | 5102444% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 5.2226 | 47.1529 | 47052.8757 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 40.7401 | 16.163 | 16062.9547 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 23.4669 | 2.359 | 2258.9763 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 23.4669 | 2.3043 | 2204.254 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 35.1952 | 2.1462 | 2046.1684 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640194 [GOSPER 7 115.00] CKT 1 | 35.1952 | 2.2042 | 2104.1795 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3989 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.0342 | 19.7725 | 19672.5008 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.0342 | 19.5493 | 19449.3477 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.0342 | 19.7547 | 19654.6772 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 15.0342 | 19.8075 | 19707.5383 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.2342 | 52.3793 | 52279.2609 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.2342 | 51.1905 | 51090.4755 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 5.2342 | 47.2065 | 47106.4847 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 40.7408 | 16.163 | 16062.9777 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 23.4672 | 2.359 | 2259.0195 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 23.4672 | 2.3043 | 2204.2949 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 35.1967 | 2.1465 | 2046.5072 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640244 [JOHN.LK7 115.00] CKT 1 | 35.1967 | 2.2045 | 2104.5315 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 10.3211 | 16.4124 | 16312.4192 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.0492 | 19.7687 | 19668.6621 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.0492 | 19.5456 | 19445.6399 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.0492 | 19.7508 | 19650.8452 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 15.0492 | 19.8037 | 19703.6664 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.251 | 51.5725 | 51472.5005 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.251 | 50.4115 | 50311.5081 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 5.251 | 46.5806 | 46480.6075 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 40.7412 | 16.163 | 16062.9784 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 23.4675 | 2.359 | 2259.036 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 23.4675 | 2.3043 | 2204.3085 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 35.1985 | 2.1466 | 2046.591 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640407 [WESTMIN7 115.00] CKT 1 | 35.1985 | 2.2046 | 2104.6177 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.4 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.0018 | 19.7738 | 19673.8225 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.0018 | 19.5507 | 19450.6623 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.0018 | 19.756 | 19655.9953 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 15.0018 | 19.8089 | 19708.8553 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.275 | 51.857 | 51756.9548 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.275 | 50.6854 | 50585.4191 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 5.275 | 46.7983 | 46698.2898 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 40.7411 | 16.163 | 16062.9737 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 23.4675 | 2.359 | 2259.0217 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 23.4675 | 2.3043 | 2204.2959 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 35.1979 | 2.1465 | 2046.5331 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640161 [ELMCRK_7 115.00] CKT 1 | 35.1979 | 2.2046 | 2104.5578 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3724 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 14.9627 | 19.7784 | 19678.38 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 14.9627 | 19.5551 | 19455.1157 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 14.9627 | 19.7605 | 19660.5454 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 14.9627 | 19.8134 | 19713.4317 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.2567 | 52.0485 | 51948.5436 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.2567 | 50.8703 | 50770.3115 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 5.2567 | 46.9497 | 46849.6658 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 40.7412 | 16.163 | 16062.9661 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 23.4677 | 2.359 | 2259.0171 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 23.4677 | 2.3043 | 2204.2913 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 35.1999 | 2.1465 | 2046.4735 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640248 [KEAR.NE7 115.00] CKT 1 | 35.1999 | 2.2045 | 2104.496 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3776 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.0616 | 19.7687 | 19668.659 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.0616 | 19.5456 | 19445.6142 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.0616 | 19.7508 | 19650.8403 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 15.0616 | 19.8037 | 19703.671 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2752 | 51.8913 | 51791.3174 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2752 | 50.7184 | 50618.4098 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2752 | 46.8251 | 46725.1484 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 40.7413 | 16.163 | 16062.9665 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 23.4678 | 2.359 | 2259.0151 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 23.4678 | 2.3043 | 2204.289 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 35.1999 | 2.1465 | 2046.481 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 35.1999 | 2.2045 | 2104.5035 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 10.3211 | 16.4124 | 16312.3839 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 14.9828 | 19.7801 | 19680.1289 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 14.9828 | 19.5568 | 19456.7675 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 14.9828 | 19.7623 | 19662.2913 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 14.9828 | 19.8152 | 19715.2103 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.2602 | 52.1741 | 52074.1229 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.2602 | 50.9916 | 50891.5524 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 5.2602 | 47.0458 | 46945.8128 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 40.7414 | 16.163 | 16062.9674 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 23.4678 | 2.359 | 2259.0188 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 23.4678 | 2.3043 | 2204.2928 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 35.2002 | 2.1465 | 2046.4984 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640383 [TOWER 7 115.00] CKT 1 | 35.2002 | 2.2045 | 2104.5217 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 10.321 | 16.4124 | 16312.3748 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.064 | 19.7687 | 19668.7106 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.064 | 19.5457 | 19445.6607 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.064 | 19.7509 | 19650.8931 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 15.064 | 19.8037 | 19703.725 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.2758 | 51.886 | 51786.0496 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.2758 | 50.7133 | 50613.3102 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 5.2758 | 46.821 | 46720.9632 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 40.7413 | 16.163 | 16062.9654 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 23.4677 | 2.359 | 2259.0146 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 23.4677 | 2.3043 | 2204.2886 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 35.2002 | 2.1465 | 2046.4816 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643091 [KEARNEY T1 913.800] CKT 1 | 35.2002 | 2.2045 | 2104.5043 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 10.321 | 16.4124 | 16312.3737 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.064 | 19.7686 | 19668.6354 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.064 | 19.5456 | 19445.5872 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.064 | 19.7508 | 19650.818 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 15.064 | 19.8036 | 19703.6496 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.2758 | 51.8854 | 51785.3781 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.2758 | 50.7127 | 50612.6818 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 5.2758 | 46.8204 | 46720.433 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 40.7413 | 16.163 | 16062.9653 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 23.4677 | 2.359 | 2259.0143 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 23.4677 | 2.3043 | 2204.2885 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 35.2002 | 2.1465 | 2046.4793 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640250 [KEARNEY7 115.00] TO BUS 640251 [KEARNEY9 34.500] TO BUS 643092 [KEARNEY T2 913.800] CKT 1 | 35.2002 | 2.2045 | 2104.5018 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.3782 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 14.9138 | 19.7679 | 19667.8711 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 14.9138 | 19.5449 | 19444.8928 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 14.9138 | 19.7501 | 19650.0584 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 14.9138 | 19.8029 | 19702.8672 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2475 | 52.0016 | 51901.5811 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2475 | 50.8258 | 50725.7609 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 5.2475 | 46.9131 | 46813.1335 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 40.7414 | 16.163 | 16062.9674 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 23.4678 | 2.359 | 2259.0183 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 23.4678 | 2.3043 | 2204.2923 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 35.2001 | 2.1465 | 2046.4882 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640261 [LOWELL 7 115.00] CKT 1 | 35.2001 | 2.2045 | 2104.5111 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 10.321 | 16.4124 | 16312.359 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.0598 | 19.7675 | 19667.5366 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.0598 | 19.5445 | 19444.5431 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.0598 | 19.7497 | 19649.7202 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 15.0598 | 19.8025 | 19702.5347 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.2759 | 51.8142 | 51714.1722 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.2759 | 50.6436 | 50543.6489 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 5.2759 | 46.766 | 46666.0262 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 40.7409 | 16.163 | 16062.9549 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 23.4675 | 2.359 | 2258.9933 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 23.4675 | 2.3043 | 2204.2683 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 35.199 | 2.1464 | 2046.3505 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640275 [MINDEN 7 115.00] TO BUS 640276 [MINDEN 9 34.500] TO BUS 643102 [MINDEN T1 913.800] CKT 1 | 35.199 | 2.2044 | 2104.3679 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.3154 | 16.4137 | 16313.6759 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.8328 | 19.769 | 19668.9987 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.8328 | 19.5458 | 19445.7814 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.8328 | 19.7512 | 19651.1904 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.8328 | 19.8041 | 19704.0895 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2486 | 52.219 | 52118.9672 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2486 | 51.0356 | 50935.6491 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2486 | 47.079 | 46978.9782 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 40.7003 | 16.1641 | 16064.1049 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 23.4411 | 2.3582 | 2258.2316 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 23.4411 | 2.3037 | 2203.6892 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.5999 | 2.1406 | 2040.6309 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.5999 | 2.1985 | 2098.5069 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 10.3191 | 16.412 | 16311.9631 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8786 | 19.7722 | 19672.1968 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8786 | 19.549 | 19448.9913 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8786 | 19.7544 | 19654.3788 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 14.8786 | 19.8073 | 19707.2628 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.264 | 52.053 | 51953.0463 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.264 | 50.8745 | 50774.4742 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 5.264 | 46.9514 | 46851.4438 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 40.7199 | 16.1635 | 16063.4916 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 23.4419 | 2.3593 | 2259.3267 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 23.4419 | 2.3046 | 2204.6174 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 34.6753 | 2.1536 | 2053.6065 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640590 [MONOLITH 3 345.00] CKT 1 | 34.6753 | 2.2119 | 2111.9165 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.3195 | 16.4148 | 16314.7983 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.0123 | 19.7669 | 19666.9177 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.0123 | 19.5439 | 19443.8886 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.0123 | 19.7491 | 19649.1054 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.0123 | 19.8019 | 19701.9363 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2726 | 51.9186 | 51818.5552 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2726 | 50.7449 | 50644.9046 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2726 | 46.8461 | 46746.1205 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 40.7229 | 16.1638 | 16063.8176 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 23.4452 | 2.3594 | 2259.3533 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 23.4452 | 2.3047 | 2204.7072 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 35.1974 | 2.1436 | 2043.573 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 35.1974 | 2.2015 | 2101.482 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 10.3203 | 16.4117 | 16311.7076 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.0577 | 19.7745 | 19674.5415 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.0577 | 19.5514 | 19451.3774 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.0577 | 19.7567 | 19656.7106 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 15.0577 | 19.8096 | 19709.5692 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.276 | 51.9063 | 51806.3261 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.276 | 50.7325 | 50632.4877 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 5.276 | 46.8375 | 46737.4834 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 40.7403 | 16.1631 | 16063.1415 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 23.465 | 2.3594 | 2259.3515 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 23.465 | 2.3046 | 2204.5996 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 35.1533 | 2.1505 | 2050.522 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640277 [MOORE 3 345.00] TO BUS 640278 [SHELDON7 115.00] TO BUS 640280 [MOORE 9 13.800] CKT 1 | 35.1533 | 2.2087 | 2108.6912 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 10.3206 | 16.4122 | 16312.2032 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.0531 | 19.7522 | 19652.1926 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.0531 | 19.5295 | 19429.533 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.0531 | 19.7344 | 19634.4092 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 15.0531 | 19.7871 | 19687.1428 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.2756 | 47.0581 | 46958.0702 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.2756 | 46.0557 | 45955.682 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 5.2756 | 43.0016 | 42901.5991 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 40.7394 | 16.1629 | 1606291% | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 23.4668 | 2.3589 | 2258.899 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 23.4668 | 2.3042 | 220418% | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 35.1955 | 2.1457 | 2045.6982 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640310 [ORLEANS7 115.00] TO BUS 764445 [G20-013-TAP 115.00] CKT 1 | 35.1955 | 2.2037 | 2103.6903 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3199 | 16.414 | 16313.9934 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.1635 | 19.9865 | 19886.4568 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.1635 | 19.7573 | 19657.2752 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.1635 | 19.9684 | 19868.3694 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 11.1635 | 20.023 | 19922.9832 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.2478 | 52.2566 | 52156.6302 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.2478 | 51.074 | 50973.9792 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.2478 | 47.1039 | 47003.9349 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 40.7251 | 16.1636 | 16063.6252 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4536 | 2.3592 | 2259.2368 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4536 | 2.3046 | 2204.5641 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 35.0059 | 2.147 | 2047.0258 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640312 [PAULINE3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 35.0059 | 2.2051 | 2105.1023 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 10.3209 | 16.4124 | 16312.3917 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.9259 | 19.7893 | 19689.2513 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.9259 | 19.5656 | 19465.6339 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.9259 | 19.7714 | 19671.3959 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.9259 | 19.8244 | 19724.3854 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.2537 | 52.1647 | 52064.6536 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.2537 | 50.9825 | 50882.5393 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.2537 | 47.039 | 46938.963 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 40.7405 | 16.163 | 16062.9769 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 23.4671 | 2.359 | 2259.0138 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 23.4671 | 2.3043 | 2204.2892 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 35.1908 | 2.1465 | 2046.5109 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 35.1908 | 2.2045 | 2104.5356 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 10.321 | 16.4124 | 16312.3922 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 14.9382 | 19.7785 | 19678.4622 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 14.9382 | 19.5552 | 19455.175 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 14.9382 | 19.7606 | 19660.6279 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 14.9382 | 19.8135 | 19713.5227 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.2565 | 51.9417 | 51841.65 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.2565 | 50.7674 | 50667.3839 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 5.2565 | 46.866 | 46766.004 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 40.7408 | 16.163 | 16062.9765 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 23.4673 | 2.359 | 2259.0173 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 23.4673 | 2.3043 | 2204.292 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 35.1917 | 2.1465 | 2046.5346 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 2 | 35.1917 | 2.2046 | 2104.5597 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 10.3208 | 16.4122 | 16312.2128 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 14.995 | 19.7646 | 19664.579 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 14.995 | 19.5416 | 19441.5886 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 14.995 | 19.7468 | 19646.7743 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 14.995 | 19.7996 | 19699.5987 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.2627 | 51.8994 | 51799.371 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.2627 | 50.7278 | 50627.7945 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 5.2627 | 46.8311 | 46731.1191 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 40.7408 | 16.1629 | 16062.9282 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 23.4676 | 2.3589 | 2258.9333 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 23.4676 | 2.3042 | 2204.213 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 35.1972 | 2.146 | 2045.9532 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640583 [ROSEMONT 7115.00] CKT 1 | 35.1972 | 2.204 | 2103.9558 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 10.3209 | 16.4123 | 16312.2802 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.0555 | 19.7618 | 19661.8247 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.0555 | 19.539 | 19438.9655 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.0555 | 19.744 | 19644.022 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 15.0555 | 19.7968 | 19696.8025 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.2753 | 51.7923 | 51692.3215 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.2753 | 50.6229 | 50522.8718 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 5.2753 | 46.7485 | 46648.4731 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 40.7405 | 16.1629 | 16062.9189 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 23.4673 | 2.3589 | 2258.9302 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 23.4673 | 2.3042 | 2204.2081 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 35.196 | 2.1459 | 2045.9223 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640314 [PAULINE8 69.000] TO BUS 643121 [PAULINE T2 913.800] CKT 1 | 35.196 | 2.2039 | 2103.9226 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 10.3191 | 16.4108 | 16310.8171 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 9.9044 | 20.2573 | 20157.3051 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 9.9044 | 20.0199 | 19919.8577 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 9.9044 | 20.2388 | 20138.7677 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 9.9044 | 20.2958 | 20195.7643 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1249 | 54.6975 | 54597.4672 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1249 | 53.4366 | 53336.5924 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 5.1249 | 48.9686 | 48868.6016 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 40.7358 | 16.1626 | 16062.5586 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4661 | 2.3582 | 2258.1564 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 23.4661 | 2.3035 | 2203.4856 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 35.1641 | 2.1422 | 2042.1896 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640374 [SWEET W3 345.00] TO BUS 640065 [AXTELL 3 345.00] CKT 1 | 35.1641 | 2.2 | 2100.0499 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 10.3108 | 16.4169 | 16316.857 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.0633 | 19.7696 | 19669.6267 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.0633 | 19.5466 | 19446.5568 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.0633 | 19.7518 | 19651.8084 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 15.0633 | 19.8046 | 19704.6455 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.2759 | 51.8956 | 51795.627 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.2759 | 50.7225 | 50622.4646 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 5.2759 | 46.8287 | 46728.6522 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 39.9278 | 16.1834 | 16083.4295 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 23.436 | 2.3563 | 2256.3473 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 23.436 | 2.302 | 2201.9941 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 35.1763 | 2.146 | 2046.0497 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 762069 [G17-105TAP 161.00] CKT 1 | 35.1763 | 2.2041 | 2104.0621 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 10.3166 | 16.4122 | 16312.1534 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.0646 | 19.7714 | 19671.3846 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.0646 | 19.5483 | 19448.2806 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.0646 | 19.7536 | 19653.561 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 15.0646 | 19.8064 | 19706.4055 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.276 | 51.8978 | 51797.7887 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.276 | 50.7245 | 50624.4694 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 5.276 | 46.8305 | 46730.48 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 40.4785 | 16.1691 | 16069.1182 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 23.4156 | 2.3604 | 2260.3705 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 23.4156 | 2.3055 | 2205.5019 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 35.1979 | 2.1465 | 2046.5436 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640377 [TEKAMAH5 161.00] TO BUS 640378 [TEKAMAH7 115.00] TO BUS 643151 [TEKAMAH T1 913.800] CKT 1 | 35.1979 | 2.2046 | 2104.5683 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 10.321 | 16.4124 | 16312.383 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.0602 | 19.7696 | 19669.6144 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.0602 | 19.5465 | 19446.5484 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.0602 | 19.7518 | 19651.7949 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 15.0602 | 19.8046 | 19704.6307 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.2756 | 51.8931 | 51793.0775 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.2756 | 50.72 | 50619.9774 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 5.2756 | 46.8267 | 46726.7169 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 40.741 | 16.163 | 16062.9673 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 23.4673 | 2.359 | 2259.0161 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 23.4673 | 2.3043 | 2204.2894 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 35.1989 | 2.1465 | 2046.5083 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640051 [AINSWRT7 115.00] CKT 1 | 35.1989 | 2.2045 | 2104.532 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 10.3211 | 16.4124 | 16312.4072 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.0593 | 19.7686 | 19668.5652 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.0593 | 19.5455 | 19445.5172 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.0593 | 19.7507 | 19650.748 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 15.0593 | 19.8036 | 19703.5795 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.2754 | 51.8922 | 51792.2377 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.2754 | 50.7192 | 50619.2484 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 5.2754 | 46.8259 | 46725.9262 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 40.7413 | 16.163 | 16062.9745 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 23.4676 | 2.359 | 2259.0446 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 23.4676 | 2.3043 | 2204.317 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 35.1992 | 2.1465 | 2046.5183 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640210 [HARMONY7 115.00] CKT 1 | 35.1992 | 2.2045 | 2104.5425 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 10.3208 | 16.4122 | 16312.2004 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.0593 | 19.7653 | 19665.3056 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.0593 | 19.5423 | 19442.3225 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.0593 | 19.7475 | 19647.4957 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 15.0593 | 19.8003 | 19700.313 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.2754 | 51.8894 | 51789.3552 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.2754 | 50.7166 | 50616.567 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 5.2754 | 46.8234 | 46723.4232 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 40.7405 | 16.1629 | 16062.903 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 23.4673 | 2.3589 | 2258.8913 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 23.4673 | 2.3042 | 2204.1728 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 35.197 | 2.1459 | 2045.855 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640392 [VALENTN7 115.00] TO BUS 640393 [VALENTN9 34.500] TO BUS 643160 [VALENTINET1913.800] CKT 1 | 35.197 | 2.2039 | 2103.8537 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 10.3218 | 16.413 | 16312.9705 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0766 | 19.7832 | 19683.1635 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0766 | 19.5598 | 19459.8285 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0766 | 19.7653 | 19665.3133 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 15.0766 | 19.8182 | 19718.2096 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2776 | 51.9095 | 51809.4776 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2776 | 50.7352 | 50635.1872 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 5.2776 | 46.8406 | 46740.5658 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 40.7441 | 16.1632 | 16063.174 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 23.4688 | 2.3594 | 2259.4224 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 23.4688 | 2.3047 | 2204.6713 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 35.21 | 2.1486 | 2048.5948 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640394 [VALTN.W7 115.00] TO BUS 764475 [G20-069-TAP 115.00] CKT 1 | 35.21 | 2.2067 | 2106.6988 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 10.3203 | 16.4146 | 16314.5657 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 14.9962 | 19.8092 | 19709.2046 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 14.9962 | 19.5852 | 19485.2483 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 14.9962 | 19.7913 | 19691.3029 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 14.9962 | 19.8444 | 19744.3582 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.2726 | 52.0501 | 51950.0822 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.2726 | 50.8706 | 50770.6164 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 5.2726 | 46.9505 | 46850.4972 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 40.7276 | 16.164 | 16064.0499 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 23.4511 | 2.3599 | 2259.903 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 23.4511 | 2.3052 | 2205.2051 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 35.0484 | 2.152 | 2051.9638 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 585241 [GEN-2015-088345.00] CKT 1 | 35.0484 | 2.2102 | 2110.2323 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 10.3215 | 16.4141 | 16314.1391 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.1044 | 19.8152 | 19715.1663 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.1044 | 19.5911 | 19491.1 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.1044 | 19.7972 | 19697.2492 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 15.1044 | 19.8503 | 19750.3281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.2794 | 52.0356 | 51935.556 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.2794 | 50.8564 | 50756.368 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 5.2794 | 46.9395 | 46839.4846 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 40.7475 | 16.164 | 16063.9678 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 23.4709 | 2.3599 | 2259.9454 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 23.4709 | 2.3052 | 2205.2321 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 35.2412 | 2.1527 | 2052.6741 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640525 [TOBIAS 3345.00] TO BUS 761292 [GEN-2017-181345.00] CKT 1 | 35.2412 | 2.211 | 2110.9667 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 10.3212 | 16.4125 | 16312.487 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.0613 | 19.7673 | 19667.3235 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.0613 | 19.5443 | 19444.299 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.0613 | 19.7495 | 19649.509 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 15.0613 | 19.8023 | 19702.3355 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.2757 | 51.8925 | 51792.4879 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.2757 | 50.7195 | 50619.4812 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 5.2757 | 46.8261 | 46726.0742 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 40.7416 | 16.163 | 16063.0267 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 23.4675 | 2.3592 | 2259.1644 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 23.4675 | 2.3044 | 2204.4247 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 35.1999 | 2.1475 | 2047.506 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648601 [NC1GA1X9 4.2000] TO BUS 648602 [NC1GA1Y9 4.2000] CKT 1 | 35.1999 | 2.2056 | 210556% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 10.3212 | 16.4125 | 16312.4862 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.0613 | 19.7673 | 1966732% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.0613 | 19.5443 | 19444.298 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.0613 | 19.7495 | 19649.5079 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 15.0613 | 19.8023 | 19702.3344 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.2757 | 51.8925 | 51792.4855 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.2757 | 50.7195 | 50619.4788 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 5.2757 | 46.8261 | 46726.0722 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 40.7416 | 16.163 | 16063.0264 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 23.4675 | 2.3592 | 2259.1637 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 23.4675 | 2.3044 | 2204.4241 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 35.1999 | 2.1475 | 2047.5016 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645011 [NEBCTY1G 18.000] TO BUS 648603 [NC1GA2X9 4.2000] TO BUS 648604 [NC1GA2Y9 4.2000] CKT 1 | 35.1999 | 2.2056 | 2105.5598 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 10.3208 | 16.4123 | 16312.2797 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.0626 | 19.7685 | 19668.4788 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.0626 | 19.5454 | 19445.433 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.0626 | 19.7507 | 19650.6631 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 15.0626 | 19.8035 | 19703.4945 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.2758 | 51.8935 | 51793.5007 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.2758 | 50.7204 | 50620.4008 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 5.2758 | 46.8269 | 46726.9212 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 40.7401 | 16.1629 | 16062.9291 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 23.4671 | 2.3589 | 2258.946 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 23.4671 | 2.3042 | 2204.2228 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 35.1953 | 2.1459 | 2045.9072 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648611 [NC2GA1X9 4.2000] TO BUS 648612 [NC2GA1Y9 4.2000] CKT 1 | 35.1953 | 2.2039 | 2103.9064 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 10.3203 | 16.4118 | 16311.7892 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.056 | 19.7617 | 19661.6673 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.056 | 19.5388 | 19438.7549 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.056 | 19.7439 | 19643.866 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 15.056 | 19.7967 | 19696.6674 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.275 | 51.8873 | 51787.3435 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.275 | 50.7148 | 50614.7662 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 5.275 | 46.8216 | 46721.6431 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 40.7371 | 16.1627 | 16062.7479 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 23.4653 | 2.3586 | 2258.607 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 23.4653 | 2.3039 | 2203.8979 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 35.1738 | 2.1431 | 2043.1409 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645012 [NEBCTY2G 23.000] TO BUS 648613 [NC2GA2X9 13.800] TO BUS 648614 [NC2GA2Y9 13.800] CKT 1 | 35.1738 | 2.201 | 2101.0279 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.3188 | 16.4104 | 16310.3966 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0615 | 19.7706 | 19670.591 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0615 | 19.5475 | 19447.4984 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0615 | 19.7528 | 19652.769 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0615 | 19.8056 | 19705.611 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2757 | 51.8994 | 51799.424 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2757 | 50.7261 | 50626.0903 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2757 | 46.8316 | 46731.6184 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 40.1382 | 16.176 | 16075.9765 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 20.9002 | 2.3608 | 2260.8466 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 20.9002 | 2.3099 | 2209.898 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 35.0769 | 2.1481 | 2048.0673 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 35.0769 | 2.2062 | 2106.165 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 10.3171 | 16.4111 | 16311.08 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0607 | 19.7667 | 19666.6965 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0607 | 19.5437 | 19443.6855 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0607 | 19.7489 | 19648.8834 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0607 | 19.8017 | 19701.707 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2754 | 51.8909 | 51790.909 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2754 | 50.718 | 50618.0262 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2754 | 46.8247 | 46724.6907 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 40.4369 | 16.1665 | 16066.4685 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 20.1698 | 2.3706 | 2270.574 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 20.1698 | 2.3187 | 2218.6752 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 35.1941 | 2.1456 | 2045.6045 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 35.1941 | 2.2036 | 2103.5972 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 10.3257 | 16.4191 | 16319.1365 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.0935 | 19.8011 | 19701.0632 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.0935 | 19.5774 | 19477.3792 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.0935 | 19.7832 | 19683.1724 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 15.0935 | 19.8361 | 19736.1475 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.2794 | 51.9238 | 51823.8133 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.2794 | 50.7483 | 50648.3303 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 5.2794 | 46.8529 | 46752.8584 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 40.7669 | 16.1698 | 16069.755 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 23.4854 | 2.3684 | 2268.449 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 23.4854 | 2.3139 | 2213.8843 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 35.2466 | 2.1567 | 2056.6868 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 762603 [GEN-2018-025345.00] CKT 1 | 35.2466 | 2.2151 | 2115.1096 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 10.319 | 16.4141 | 16314.0728 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.0639 | 19.7698 | 19669.7996 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.0639 | 19.5467 | 19446.7267 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.0639 | 19.752 | 19651.9795 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 15.0639 | 19.8048 | 19704.8169 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.2759 | 51.8946 | 51794.6278 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.2759 | 50.7215 | 50621.4658 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 5.2759 | 46.8279 | 46727.9232 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 39.5998 | 16.2038 | 16103.8038 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 23.2723 | 2.3575 | 2257.4533 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 23.2723 | 2.3023 | 2202.3468 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 35.1984 | 2.1463 | 2046.3043 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648251 [S3451T39 13.800] CKT 1 | 35.1984 | 2.2043 | 2104.3194 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 10.319 | 16.4141 | 16314.0612 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.0639 | 19.7698 | 19669.8009 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.0639 | 19.5467 | 19446.7281 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.0639 | 19.752 | 19651.9809 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 15.0639 | 19.8048 | 19704.8183 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.2759 | 51.8947 | 51794.667 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.2759 | 50.7215 | 50621.4684 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 5.2759 | 46.8279 | 46727.9254 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 39.6075 | 16.2036 | 16103.5901 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 23.2737 | 2.3575 | 2257.4891 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 23.2737 | 2.3024 | 2202.3866 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 35.1984 | 2.1463 | 2046.3066 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645451 [S3451 3 345.00] TO BUS 646251 [S1251 5 161.00] TO BUS 648351 [S3451T49 13.800] CKT 1 | 35.1984 | 2.2043 | 2104.322 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 10.2512 | 16.4249 | 16324.9249 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.0302 | 19.7584 | 19658.3763 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.0302 | 19.5355 | 19435.4999 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.0302 | 19.7406 | 19640.5832 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 15.0302 | 19.7934 | 19693.381 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.2725 | 51.9099 | 51809.9273 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.2725 | 50.737 | 50636.985 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 5.2725 | 46.8386 | 46738.5757 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 39.5325 | 16.1843 | 16084.2803 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 22.4413 | 2.3351 | 2235.0897 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 22.4413 | 2.2845 | 2184.469 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 34.2569 | 2.12 | 2020.0228 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 635000 [CBLUFFS3 345.00] CKT 1 | 34.2569 | 2.1771 | 2077.1484 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 10.2986 | 16.4135 | 16313.5482 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0494 | 19.7641 | 19664.0902 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0494 | 19.5411 | 19441.1184 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0494 | 19.7463 | 19646.2839 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0494 | 19.7991 | 19699.1 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.2745 | 51.9001 | 51800.1173 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.2745 | 50.7271 | 50627.1018 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.2745 | 46.8316 | 46731.5884 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 40.6675 | 16.1595 | 16059.5402 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 23.4512 | 2.3529 | 2252.8935 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 23.4512 | 2.2986 | 2198.5711 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 35.0314 | 2.1375 | 2037.4653 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 35.0314 | 2.1952 | 2095.1638 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 10.3021 | 16.4077 | 16307.6515 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0635 | 19.769 | 19669.0421 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0635 | 19.546 | 19445.9854 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0635 | 19.7512 | 19651.2237 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 15.0635 | 19.8041 | 19704.0575 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2759 | 51.8937 | 51793.7426 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2759 | 50.7206 | 50620.6304 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 5.2759 | 46.8271 | 46727.1324 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 39.4426 | 16.1896 | 16089.5578 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 21.8 | 2.3382 | 2238.1802 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 21.8 | 2.288 | 2188.0117 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 35.1908 | 2.148 | 2048.0399 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 645459 [S3459 3 345.00] CKT 1 | 35.1908 | 2.2061 | 2106.1172 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 10.3199 | 16.4207 | 16320.6504 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.0636 | 19.7696 | 19669.5836 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.0636 | 19.5465 | 19446.5168 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.0636 | 19.7518 | 19651.7641 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 15.0636 | 19.8046 | 19704.6001 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.2759 | 51.8942 | 51794.2001 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.2759 | 50.7211 | 50621.0627 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 5.2759 | 46.8276 | 46727.5506 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 40.7231 | 16.1652 | 16065.1952 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 23.466 | 2.358 | 2258.033 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 23.466 | 2.3033 | 2203.3018 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 35.1752 | 2.1451 | 2045.0934 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645456 [S3456 3 345.00] TO BUS 646206 [S1206 5 161.00] TO BUS 648256 [S3456T49 13.800] CKT 1 | 35.1752 | 2.2031 | 2103.0562 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 10.3181 | 16.4124 | 16312.4323 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.948 | 19.7747 | 19674.7076 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.948 | 19.5514 | 19451.4323 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.948 | 19.7569 | 19656.8817 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.948 | 19.8098 | 19709.7837 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.267 | 52.0188 | 51918.7983 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.267 | 50.8417 | 50741.7301 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.267 | 46.9239 | 46823.9066 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 40.7408 | 16.1626 | 16062.5689 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 23.4677 | 2.3584 | 2258.3765 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 23.4677 | 2.3037 | 2203.6878 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 17.5157 | 2.2095 | 2109.5413 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645458 [S3458 3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 17.5157 | 2.2737 | 2173.7158 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 10.3155 | 16.4191 | 16319.0903 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.0788 | 19.7909 | 19690.9137 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.0788 | 19.5674 | 19467.423 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.0788 | 19.773 | 19673.0456 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 15.0788 | 19.826 | 19725.9775 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.2778 | 51.9192 | 51819.2037 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.2778 | 50.7443 | 50644.3238 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 5.2778 | 46.8484 | 46748.4407 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 40.6025 | 16.1679 | 16067.9409 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 23.3436 | 2.3599 | 2259.8976 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 23.3436 | 2.3056 | 2205.617 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 35.0275 | 2.1515 | 2051.5321 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645041 [CASS 1G 15.000] CKT 1 | 35.0275 | 2.2098 | 2109.786 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 10.3155 | 16.4191 | 16319.0799 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.0787 | 19.7908 | 19690.828 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.0787 | 19.5673 | 19467.3389 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.0787 | 19.773 | 19672.9615 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 15.0787 | 19.8259 | 19725.8933 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.2778 | 51.9191 | 51819.1231 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.2778 | 50.7442 | 50644.2466 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 5.2778 | 46.8484 | 46748.3975 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 40.6019 | 16.1679 | 16067.9421 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 23.3431 | 2.3599 | 2259.8739 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 23.3431 | 2.3056 | 2205.596 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 35.0266 | 2.1515 | 2051.4703 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645042 [CASS 2G 15.000] CKT 1 | 35.0266 | 2.2097 | 2109.7218 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.3137 | 16.4138 | 16313.7968 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0628 | 19.7703 | 19670.2784 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0628 | 19.5472 | 1944719% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0628 | 19.7525 | 19652.4585 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 15.0628 | 19.8053 | 1970530% | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2758 | 51.8977 | 51797.6875 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2758 | 50.7244 | 50624.4313 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2758 | 46.8303 | 46730.2577 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 40.6134 | 16.1657 | 16065.7371 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 23.3193 | 2.3565 | 2256.4852 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 23.3193 | 2.3025 | 2202.452 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 35.1868 | 2.1427 | 2042.7331 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 35.1868 | 2.2006 | 2100.6062 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 10.3117 | 16.4162 | 16316.1584 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0641 | 19.7696 | 19669.6426 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0641 | 19.5466 | 19446.5732 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0641 | 19.7518 | 19651.8229 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 15.0641 | 19.8047 | 19704.6592 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.276 | 51.8942 | 51794.1504 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.276 | 50.721 | 50621.0175 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 5.276 | 46.8275 | 46727.5397 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 40.5949 | 16.1668 | 16066.8335 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 23.3897 | 2.3565 | 2256.5088 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 23.3897 | 2.3024 | 2202.3631 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 35.1196 | 2.1433 | 2043.3456 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 645455 [S3455 3 345.00] CKT 1 | 35.1196 | 2.2012 | 2101.2332 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 10.3254 | 16.4184 | 16318.3855 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.0932 | 19.8009 | 19700.8688 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.0932 | 19.5772 | 19477.1882 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.0932 | 19.783 | 19682.9785 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 15.0932 | 19.836 | 19735.9529 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.2793 | 51.9237 | 51823.7364 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.2793 | 50.7483 | 50648.2552 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 5.2793 | 46.8528 | 46752.768 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 40.7593 | 16.1662 | 16066.1635 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 23.4746 | 2.3624 | 2262.3597 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 23.4746 | 2.3076 | 2207.5907 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 35.2577 | 2.1591 | 2059.1398 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 762691 [GEN-2018-033345.00] CKT 1 | 35.2577 | 2.2177 | 2117.6618 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 10.3233 | 16.4201 | 16320.0506 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.104 | 19.8147 | 19714.7066 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.104 | 19.5908 | 19490.7539 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.104 | 19.7968 | 19696.7849 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 15.104 | 19.8498 | 19749.8202 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.2807 | 51.9368 | 51836.8058 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.2807 | 50.7603 | 50660.3345 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 5.2807 | 46.8639 | 46763.8846 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 40.6918 | 16.1671 | 16067.0769 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 23.4126 | 2.3625 | 2262.5412 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 23.4126 | 2.3078 | 2207.85 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 35.1782 | 2.1631 | 2063.1494 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 645740 [S3740 3 345.00] TO BUS 764705 [GEN-2020-038345.00] CKT 1 | 35.1782 | 2.2218 | 2121.8329 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 9.0939 | 17.9284 | 17828.3529 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.057 | 19.7716 | 19671.5807 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.057 | 19.5485 | 19448.4607 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.057 | 19.7538 | 19653.7573 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 15.057 | 19.8066 | 19706.6083 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.2753 | 51.909 | 51808.9608 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.2753 | 50.7353 | 50635.3266 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 5.2753 | 46.839 | 46739.0326 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 40.7053 | 16.1636 | 16063.6373 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 23.4503 | 2.3589 | 2258.8673 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 23.4503 | 2.3042 | 2204.1529 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 35.1564 | 2.1439 | 2043.9094 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 646287 [S1287 5 161.00] CKT 1 | 35.1564 | 2.2018 | 2101.8466 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 10.1401 | 16.6391 | 16539.0852 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.0527 | 19.7737 | 19673.6503 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.0527 | 19.5505 | 19450.4822 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.0527 | 19.7558 | 19655.8219 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 15.0527 | 19.8087 | 19708.6842 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.2751 | 51.9184 | 51818.3968 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.2751 | 50.7444 | 50644.3761 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 5.2751 | 46.8465 | 46746.5221 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 40.6772 | 16.1646 | 16064.5533 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 23.4444 | 2.3588 | 2258.848 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 23.4444 | 2.3042 | 2204.1914 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 35.1215 | 2.1456 | 2045.5686 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646214 [S1214 5 161.00] TO BUS 650169 [70&BLUFF 5 161.00] CKT 1 | 35.1215 | 2.2036 | 2103.5772 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 10.3207 | 16.4122 | 16312.1696 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.064 | 19.77 | 19669.9894 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.064 | 19.5469 | 19446.9128 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.064 | 19.7522 | 19652.1689 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.064 | 19.805 | 19705.0069 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.276 | 51.8949 | 51794.904 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.276 | 50.7217 | 50621.7259 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.276 | 46.8281 | 46728.1335 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 19.7798 | 17.5594 | 17459.4151 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 23.4008 | 2.3594 | 2259.4165 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 23.4008 | 2.3048 | 2204.8318 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 35.1976 | 2.1464 | 2046.3936 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646226 [S1226 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 35.1976 | 2.2044 | 2104.4134 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 10.3205 | 16.4123 | 16312.2542 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.0636 | 19.7697 | 19669.6895 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.0636 | 19.5466 | 19446.6199 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.0636 | 19.7519 | 19651.8697 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 15.0636 | 19.8047 | 19704.7064 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.2759 | 51.8945 | 51794.5299 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.2759 | 50.7214 | 50621.3709 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 5.2759 | 46.8278 | 46727.8237 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 26.6143 | 16.8 | 16700.0139 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 23.3971 | 2.3581 | 2258.131 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 23.3971 | 2.3035 | 2203.518 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 35.1986 | 2.1466 | 2046.6358 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646237 [S1237 5 161.00] TO BUS 764775 [G20-078-TAP 161.00] CKT 1 | 35.1986 | 2.2047 | 2104.6658 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 10.3207 | 16.4122 | 16312.2496 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.0638 | 19.7698 | 19669.7987 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.0638 | 19.5467 | 19446.7271 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.0638 | 19.752 | 19651.98 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 15.0638 | 19.8048 | 19704.8172 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.2759 | 51.8947 | 51794.6712 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.2759 | 50.7215 | 50621.505 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 5.2759 | 46.828 | 46727.9503 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 40.365 | 16.1724 | 16072.3526 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 23.4491 | 2.3591 | 2259.0699 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 23.4491 | 2.3043 | 2204.3436 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 35.1991 | 2.1464 | 2046.446 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646236 [S1236 5 161.00] CKT 1 | 35.1991 | 2.2045 | 2104.4678 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 10.32 | 16.4117 | 16311.6704 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.064 | 19.7698 | 19669.8438 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.064 | 19.5468 | 19446.7712 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.064 | 19.752 | 19652.0233 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 15.064 | 19.8049 | 19704.8613 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.276 | 51.8948 | 51794.8053 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.276 | 50.7216 | 50621.6319 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 5.276 | 46.828 | 46728.0266 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 38.6622 | 16.2186 | 16118.5695 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 23.4617 | 2.3578 | 2257.8084 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 23.4617 | 2.3032 | 2203.1817 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 35.1992 | 2.1461 | 2046.1297 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646252 [S1252 5 161.00] TO BUS 646347 [S1347 5 161.00] CKT 1 | 35.1992 | 2.2041 | 2104.1389 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 10.2379 | 16.4787 | 16378.6514 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.0648 | 19.7708 | 19670.774 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.0648 | 19.5477 | 19447.6832 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.0648 | 19.753 | 19652.9518 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 15.0648 | 19.8058 | 19705.7935 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.2761 | 51.8959 | 51795.9473 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.2761 | 50.7227 | 50622.7077 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 5.2761 | 46.829 | 46729.0357 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 40.0757 | 16.1833 | 16083.3472 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 23.3687 | 2.3611 | 2261.0828 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 23.3687 | 2.3064 | 2206.4011 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 35.1884 | 2.1466 | 2046.5517 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646291 [S1291 5 161.00] TO BUS 647291 [S991 E 8 69.000] TO BUS 648291 [S1291T29 13.800] CKT 1 | 35.1884 | 2.2046 | 2104.5778 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 10.3196 | 16.4131 | 16313.1405 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.064 | 19.7699 | 19669.9437 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.064 | 19.5469 | 19446.8696 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.064 | 19.7521 | 19652.1233 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 15.064 | 19.805 | 19704.9614 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.276 | 51.8948 | 51794.819 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.276 | 50.7216 | 50621.6458 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 5.276 | 46.8281 | 46728.0865 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 39.4462 | 16.2118 | 16111.7992 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 23.4029 | 2.3594 | 2259.3833 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 23.4029 | 2.3045 | 2204.5227 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 35.1993 | 2.1465 | 2046.4752 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646251 [S1251 5 161.00] CKT 1 | 35.1993 | 2.2045 | 2104.4971 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 10.3209 | 16.4125 | 16312.5235 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.0639 | 19.7699 | 19669.8526 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.0639 | 19.5468 | 19446.78 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.0639 | 19.752 | 19652.0324 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 15.0639 | 19.8049 | 19704.8698 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.276 | 51.8947 | 51794.7396 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.276 | 50.7216 | 50621.5709 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 5.276 | 46.828 | 46728.0145 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 40.5414 | 16.1703 | 16070.2859 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 23.4582 | 2.359 | 2259.0028 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 23.4582 | 2.3043 | 2204.2711 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 35.2002 | 2.1465 | 2046.505 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646298 [S1298 5 161.00] TO BUS 646305 [S1305 5 161.00] CKT 1 | 35.2002 | 2.2045 | 2104.5285 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 10.3209 | 16.4125 | 16312.4994 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.0639 | 19.7698 | 19669.8425 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.0639 | 19.5468 | 19446.77 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.0639 | 19.752 | 19652.0237 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 15.0639 | 19.8049 | 19704.8611 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.2759 | 51.8948 | 51794.7566 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.2759 | 50.7216 | 50621.553 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 5.2759 | 46.828 | 46727.9978 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 37.1799 | 16.2783 | 16178.3273 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 23.4321 | 2.3591 | 2259.1111 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 23.4321 | 2.3044 | 2204.4446 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 35.1988 | 2.1466 | 2046.5511 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 646367 [S1367 5 161.00] TO BUS 646253 [S1253 5 161.00] CKT 1 | 35.1988 | 2.2046 | 2104.577 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 4.3289 | 23.9395 | 23839.4592 | 81 | 93.6 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.7701 | 19670.1327 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.5471 | 19447.052 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.7523 | 19652.3118 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.8052 | 19705.1507 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.2759 | 51.8957 | 51795.7383 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.2759 | 50.7225 | 50622.5053 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.2759 | 46.8288 | 46728.7718 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 40.732 | 16.1628 | 16062.8421 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 23.4676 | 2.359 | 2258.9506 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 23.4676 | 2.3042 | 2204.2315 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 35.1948 | 2.1468 | 2046.762 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647014 [S914A 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 35.1948 | 2.2048 | 2104.7982 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 8.6466 | 18.2893 | 18189.3119 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.0637 | 19.7698 | 19669.7593 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.0637 | 19.5467 | 19446.6884 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.0637 | 19.7519 | 19651.9393 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 15.0637 | 19.8048 | 19704.7766 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.2759 | 51.8949 | 5179487% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.2759 | 50.7217 | 50621.6958 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 5.2759 | 46.8281 | 4672810% | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 40.7436 | 16.1631 | 16063.0633 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 23.4671 | 2.3593 | 2259.2889 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 23.4671 | 2.3045 | 2204.5361 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 35.2011 | 2.1466 | 2046.6017 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647937 [S937 8 69.000] CKT 1 | 35.2011 | 2.2046 | 2104.6287 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 9.2653 | 17.0925 | 16992.4832 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.0642 | 19.7701 | 19670.1179 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.0642 | 19.547 | 19447.0401 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.0642 | 19.7523 | 19652.2971 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 15.0642 | 19.8051 | 19705.1357 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.276 | 51.895 | 51795.0223 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.276 | 50.7218 | 50621.8035 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 5.276 | 46.8282 | 46728.2375 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 40.7255 | 16.1633 | 16063.2835 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 23.4669 | 2.3589 | 2258.9007 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 23.4669 | 2.3042 | 2204.1797 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 35.1949 | 2.1466 | 2046.5828 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647902 [S902 8 69.000] TO BUS 647984 [S984 8 69.000] CKT 1 | 35.1949 | 2.2046 | 2104.61 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 9.6764 | 16.6749 | 16574.8802 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.0636 | 19.7696 | 19669.5563 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.0636 | 19.5465 | 19446.4881 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.0636 | 19.7517 | 19651.7369 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 15.0636 | 19.8046 | 19704.5732 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.2759 | 51.8944 | 51794.3971 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.2759 | 50.7213 | 50621.2822 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 5.2759 | 46.8277 | 46727.7177 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 40.739 | 16.1628 | 16062.7782 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 23.4674 | 2.3588 | 2258.7909 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 23.4674 | 2.3041 | 2204.0799 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 35.1996 | 2.1464 | 2046.3525 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647914 [S914 8 69.000] TO BUS 647900 [S900 8 69.000] CKT 1 | 35.1996 | 2.2044 | 2104.3701 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 6.0457 | 20.407 | 20307.0419 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.7701 | 19670.1119 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.547 | 19447.0339 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.7523 | 19652.2911 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 15.0639 | 19.8051 | 19705.1297 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.276 | 51.8952 | 51795.2462 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.276 | 50.722 | 50622.0121 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 5.276 | 46.8284 | 46728.4076 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 40.7236 | 16.1629 | 16062.8764 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 23.4657 | 2.3582 | 2258.242 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 23.4657 | 2.3036 | 2203.5823 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 35.1931 | 2.1463 | 2046.3227 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 647983 [S983 8 69.000] TO BUS 647846 [S6846 8 69.000] CKT 1 | 35.1931 | 2.2043 | 2104.3399 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 10.308 | 16.4123 | 16312.2818 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 14.9306 | 19.7941 | 19694.0937 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 14.9306 | 19.5704 | 19470.3987 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 14.9306 | 19.7762 | 19676.2258 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 14.9306 | 19.8292 | 19729.2292 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2662 | 52.0828 | 51982.7984 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2662 | 50.9029 | 50802.9289 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 5.2662 | 46.9748 | 46874.7551 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 40.2359 | 16.1814 | 16081.3658 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 22.9972 | 2.3625 | 2262.5214 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 22.9972 | 2.3089 | 2208.8501 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 33.4329 | 2.1475 | 2047.476 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 645454 [S3454 3 345.00] CKT 1 | 33.4329 | 2.2058 | 2105.7553 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 10.3181 | 16.4129 | 16312.9022 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.034 | 19.7708 | 19670.8064 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.034 | 19.5477 | 19447.6924 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.034 | 19.753 | 19652.9853 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 15.034 | 19.8058 | 19705.8366 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2734 | 51.9252 | 51825.2234 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2734 | 50.7511 | 50651.1144 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 5.2734 | 46.8516 | 46751.5568 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 40.6891 | 16.1646 | 16064.6097 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 23.4296 | 2.3587 | 2258.7402 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 23.4296 | 2.3041 | 2204.1397 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 34.8793 | 2.1422 | 2042.1535 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650114 [NW68HOLDRG3 345.00] CKT 1 | 34.8793 | 2.2 | 2100.0244 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 10.3154 | 16.4127 | 16312.7132 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.0637 | 19.7695 | 19669.4652 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.0637 | 19.5464 | 19446.3996 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.0637 | 19.7516 | 19651.6458 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 15.0637 | 19.8045 | 19704.4819 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.2758 | 51.895 | 51794.9833 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.2758 | 50.7218 | 50621.8286 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 5.2758 | 46.8281 | 46728.1294 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 40.7364 | 16.1628 | 16062.8121 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 23.4631 | 2.3588 | 2258.7841 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 23.4631 | 2.304 | 2204.045 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 35.1296 | 2.1451 | 2045.0942 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650385 [WAGENER1 9 13.800] CKT 1 | 35.1296 | 2.203 | 2103.0412 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 10.3159 | 16.4127 | 16312.7107 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.0637 | 19.7695 | 19669.4914 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.0637 | 19.5464 | 19446.424 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.0637 | 19.7517 | 19651.672 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 15.0637 | 19.8045 | 19704.508 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.2758 | 51.895 | 51794.9878 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.2758 | 50.7218 | 50621.8349 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 5.2758 | 46.8281 | 46728.1402 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 40.7368 | 16.1628 | 16062.8216 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 23.4635 | 2.3588 | 2258.7972 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 23.4635 | 2.3041 | 2204.0594 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 35.1353 | 2.1452 | 2045.1675 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650185 [WAGENER 3 345.00] TO BUS 650285 [WAGENER 7 115.00] TO BUS 650485 [WAGENER2 9 13.800] CKT 2 | 35.1353 | 2.2031 | 2103.1192 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 10.3144 | 16.4101 | 16310.1272 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.9604 | 19.7878 | 19687.7968 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.9604 | 19.5642 | 19464.247 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.9604 | 19.7699 | 19669.9432 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 14.9604 | 19.8229 | 19722.9093 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.268 | 52.0478 | 51947.8159 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.268 | 50.8694 | 50769.3932 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 5.268 | 46.9471 | 46847.0659 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 40.7326 | 16.1621 | 16062.0951 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 23.4644 | 2.3572 | 2257.1829 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 23.4644 | 2.3026 | 2202.5965 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 20.979 | 2.2237 | 2123.721 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 650189 [103&ROKEBY3 345.00] TO BUS 764805 [G20-094-TAP 345.00] CKT 1 | 20.979 | 2.2861 | 2186.1046 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 10.317 | 16.4138 | 16313.7515 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.825 | 19.7759 | 19675.8662 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.825 | 19.5525 | 19452.4971 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.825 | 19.758 | 19658.0454 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 14.825 | 19.811 | 19710.9833 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2524 | 52.2802 | 52180.1601 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2524 | 51.0946 | 50994.6288 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 5.2524 | 47.1268 | 47026.8477 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 40.7098 | 16.1638 | 16063.7688 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 23.4478 | 2.3587 | 2258.6976 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 23.4478 | 2.3041 | 2204.0759 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.706 | 2.1452 | 2045.1694 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640271 [MCCOOL 3 345.00] CKT 1 | 34.706 | 2.2032 | 2103.2014 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 10.3188 | 16.4113 | 16311.342 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 14.7706 | 19.8139 | 19713.9404 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 14.7706 | 19.5896 | 19489.5923 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 14.7706 | 19.796 | 19696.0442 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 14.7706 | 19.8492 | 19749.2416 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.249 | 52.5212 | 52421.25 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.249 | 51.3273 | 51227.2757 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 5.249 | 47.3136 | 47213.6026 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 40.7357 | 16.1627 | 16062.6975 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 23.463 | 2.3582 | 2258.1522 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 23.463 | 2.3035 | 2203.4832 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 35.1124 | 2.1451 | 2045.0926 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 653871 [GR ISLD-LNX3345.00] CKT Z | 35.1124 | 2.2031 | 2103.0845 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 10.3211 | 16.4124 | 16312.3834 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.0638 | 19.7695 | 19669.5226 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.0638 | 19.5465 | 19446.4576 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.0638 | 19.7517 | 19651.7033 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 15.0638 | 19.8045 | 19704.5388 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.2741 | 51.9322 | 51832.2174 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.2741 | 50.7579 | 50657.8696 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 5.2741 | 46.8571 | 46757.1342 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 40.7412 | 16.163 | 16062.9647 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 23.4676 | 2.359 | 2259.0161 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 23.4676 | 2.3043 | 2204.2896 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 35.198 | 2.1465 | 2046.508 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653314 [GR ISL19 13.800] CKT 1 | 35.198 | 2.2045 | 2104.5314 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 10.3211 | 16.4124 | 16312.3837 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.0638 | 19.7695 | 19669.5264 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.0638 | 19.5465 | 19446.4616 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.0638 | 19.7517 | 19651.7071 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 15.0638 | 19.8045 | 19704.5426 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.2741 | 51.9319 | 51831.8502 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.2741 | 50.7575 | 50657.4916 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 5.2741 | 46.8569 | 46756.8596 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 40.7412 | 16.163 | 16062.9648 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 23.4676 | 2.359 | 2259.0161 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 23.4676 | 2.3043 | 2204.2897 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 35.198 | 2.1465 | 2046.5082 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 653316 [GR ISL29 13.800] CKT 2 | 35.198 | 2.2045 | 2104.5315 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 10.3211 | 16.4124 | 16312.3849 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.0637 | 19.7694 | 19669.4001 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.0637 | 19.5463 | 19446.3385 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.0637 | 19.7516 | 19651.5811 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 15.0637 | 19.8044 | 19704.4155 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.2733 | 51.9506 | 51850.5909 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.2733 | 50.7756 | 50675.6092 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 5.2733 | 46.8714 | 46771.371 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 40.7411 | 16.163 | 16062.9638 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 23.4675 | 2.359 | 2259.0154 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 23.4675 | 2.3043 | 2204.2888 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 35.197 | 2.1465 | 2046.5112 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 653571 [GR ISLD3 345.00] TO BUS 640200 [GR ISLD4 230.00] TO BUS 643071 [GR ISLD T6 913.800] CKT 3 | 35.197 | 2.2045 | 2104.5345 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.3383 | 16.4353 | 16335.3193 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.1749 | 19.8872 | 19787.2009 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.1749 | 19.6618 | 19561.828 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.1749 | 19.8691 | 19769.1145 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.1749 | 19.9225 | 19822.4684 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2891 | 52.0057 | 51905.6648 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2891 | 50.8236 | 50723.6295 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2891 | 46.9228 | 46822.8364 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 40.8478 | 16.1852 | 16085.1659 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.3624 | 2.1822 | 2082.2212 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762779 [G18-043-TAP 345.00] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.3624 | 2.2416 | 2141.648 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.3251 | 16.4174 | 16317.3705 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.7966 | 19696.6011 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.573 | 19473.005 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.7787 | 19678.7204 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.8317 | 19731.6757 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 51.9195 | 51819.5486 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 50.7444 | 50644.3798 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 46.8492 | 46749.229 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 40.7666 | 16.1676 | 16067.5568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5043 | 2.3758 | 227576% | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5043 | 2.3215 | 2221.5274 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2385 | 2.1548 | 205477% | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762781 [G18-043-XFM134.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2385 | 2.2131 | 2113.1141 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 10.3252 | 16.4175 | 16317.5083 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.0893 | 19.7966 | 19696.6257 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.0893 | 19.573 | 19473.0292 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.0893 | 19.7787 | 19678.745 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 15.0893 | 19.8317 | 19731.7001 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.2789 | 51.9196 | 51819.6028 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.2789 | 50.7444 | 50644.4321 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 5.2789 | 46.8493 | 46749.2744 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 40.7673 | 16.1677 | 16067.7338 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 23.5011 | 2.3774 | 2277.3902 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 23.5011 | 2.3231 | 2223.0858 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 35.2384 | 2.1548 | 2054.8459 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762782 [G18-043-GSU134.500] TO BUS 762783 [G18-043-GEN10.6600] CKT 1 | 35.2384 | 2.2132 | 2113.1945 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.3251 | 16.4174 | 16317.3705 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.7966 | 19696.6011 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.573 | 19473.005 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.7787 | 19678.7204 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0893 | 19.8317 | 19731.6757 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 51.9195 | 51819.5486 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 50.7444 | 50644.3798 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 46.8492 | 46749.229 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 40.7666 | 16.1676 | 16067.5568 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5043 | 2.3758 | 2275.7574 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5043 | 2.3215 | 2221.5274 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2385 | 2.1548 | 2054.7687 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762784 [G18-043-XFM234.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2385 | 2.2131 | 2113.1141 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 10.3252 | 16.4175 | 16317.5083 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.0893 | 19.7966 | 19696.6257 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.0893 | 19.573 | 19473.0292 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.0893 | 19.7787 | 19678.745 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 15.0893 | 19.8317 | 19731.7001 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.2789 | 51.9196 | 51819.6028 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.2789 | 50.7444 | 50644.4321 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 5.2789 | 46.8493 | 46749.2744 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 40.7673 | 16.1677 | 16067.7338 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 23.5011 | 2.3774 | 2277.3902 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 23.5011 | 2.3231 | 2223.0858 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 35.2384 | 2.1548 | 2054.8459 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762785 [G18-043-GSU234.500] TO BUS 762786 [G18-043-GEN20.6600] CKT 1 | 35.2384 | 2.2132 | 2113.1945 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 10.325 | 16.4173 | 16317.3384 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0891 | 19.7965 | 19696.4599 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0891 | 19.5729 | 19472.8666 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0891 | 19.7786 | 19678.5795 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 15.0891 | 19.8315 | 19731.534 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 51.9194 | 51819.4456 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 50.7443 | 50644.2826 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 5.2789 | 46.8491 | 46749.1352 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 40.7664 | 16.1675 | 16067.5279 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5039 | 2.3756 | 2275.5973 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 23.5039 | 2.3214 | 2221.3697 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2382 | 2.1547 | 2054.7192 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762787 [G18-043-XFM334.500] TO BUS 762780 [GEN-2018-043345.00] CKT 1 | 35.2382 | 2.2131 | 2113.0627 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 10.3252 | 16.4175 | 16317.4749 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.0891 | 19.7965 | 19696.4857 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.0891 | 19.5729 | 19472.8905 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.0891 | 19.7786 | 19678.6054 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 15.0891 | 19.8316 | 19731.5587 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.2789 | 51.9195 | 51819.4635 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.2789 | 50.7443 | 50644.3007 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 5.2789 | 46.8492 | 46749.1533 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 40.7671 | 16.1677 | 16067.7031 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 23.5007 | 2.3772 | 2277.2298 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 23.5007 | 2.3229 | 2222.9282 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 35.2382 | 2.1548 | 2054.7962 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 762788 [G18-043-GSU334.500] TO BUS 762789 [G18-043-GEN30.6600] CKT 1 | 35.2382 | 2.2131 | 2113.1428 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 10.3221 | 16.4133 | 16313.2918 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.1217 | 19.8164 | 19716.3816 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.1217 | 19.5923 | 19492.3024 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.1217 | 19.7985 | 19698.4613 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 15.1217 | 19.8515 | 19751.5425 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.2811 | 52.0293 | 51929.2584 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.2811 | 50.85 | 50749.9671 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 5.2811 | 46.9352 | 46835.2266 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 40.7458 | 16.1633 | 16063.3172 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 23.4696 | 2.3596 | 2259.6462 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 23.4696 | 2.3049 | 2204.8842 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 35.2205 | 2.1504 | 2050.4369 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 763410 [G18-125-TAP 345.00] TO BUS 763406 [GEN-2018-125345.00] CKT 1 | 35.2205 | 2.2086 | 2108.6129 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 10.3211 | 16.4125 | 16312.5224 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0612 | 19.7727 | 19672.6539 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0612 | 19.5495 | 19449.5276 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0612 | 19.7548 | 19654.8273 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 15.0612 | 19.8077 | 19707.676 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.0213 | 55.3749 | 55274.93 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.0213 | 54.0885 | 53988.5216 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 5.0213 | 49.5171 | 49417.1445 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 40.7407 | 16.163 | 16063.0132 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 23.4667 | 2.3591 | 2259.0642 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 23.4667 | 2.3043 | 2204.3384 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 35.1961 | 2.1468 | 2046.7567 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640242 [JOHN.2 7 115.00] TO BUS 640103 [CANADAY7 115.00] CKT 1 | 35.1961 | 2.2048 | 2104.7908 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-002 | 6846 Substation 69 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 10.3208 | 16.4124 | 16312.4103 | 81 | 93.6 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.5593 | 19.7998 | 19699.8014 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.5593 | 19.576 | 19476.0095 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.5593 | 19.7819 | 19681.9325 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-011 | Axtell-Sweetwater Substation 345kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 14.5593 | 19.835 | 19734.9634 | 80 | 91.35 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.1971 | 51.9877 | 51887.7444 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.1971 | 50.8137 | 50713.7196 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-013 | Orleans-Holdrege Substation 115kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 5.1971 | 46.9066 | 46806.5868 | 71.67 | 81.9 | FAIL | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-078 | Substation 1226 to Substation 1237, 161kV Tap | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 40.7385 | 16.163 | 16063.0013 | 100 | 117 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 23.4653 | 2.359 | 2259.0106 | 157.5 | 189 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-084 | Raun - Fort Calhoun 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 23.4653 | 2.3043 | 2204.2885 | 192.5 | 231 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 35.1643 | 2.1466 | 2046.578 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 02 NEBRASKA | 25WP | GEN-2020-094 | Neb. City - 103rd & Rokeby 345 kV | OPEN LINE FROM BUS 640313 [PAULINE7 115.00] TO BUS 640215 [HASTING7 115.00] CKT 1 | 35.1643 | 2.2046 | 2104.606 | 124.95 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | Base | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | Base | 13.3379 | 24.8477 | 24747.699 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | Base | 33.9415 | 246.7522 | 246652.2307 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 12.5059 | 8.9024 | 8802.4313 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | Base | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | Base | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | Base | 13.2782 | 26.6674 | 26567.4468 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | Base | 13.2782 | 41.9813 | 41881.3275 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.2503 | 19.3566 | 19256.571 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.2503 | 18.8805 | 18780.5264 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | Base | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | Base | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.4591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.4591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.4591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 18.0301 | 17930.0681 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 19.0606 | 18960.6266 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 19.0606 | 18960.6266 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 19.0606 | 18960.6266 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 21.7379 | 20.4498 | 20349.7803 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4834 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.7125 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 33.9415 | 246.7505 | 246650.539 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 13.8106 | 13710.5606 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 12.5216 | 12421.6212 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 11.1993 | 11099.2581 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 9.1708 | 9070.8385 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 8.9028 | 8802.765 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.5032 | 8.651 | 8551.013 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 6.0765 | 16.5603 | 16460.2859 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 6.0765 | 12.5231 | 12423.0936 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 13.2773 | 26.6701 | 26570.0552 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 13.2773 | 41.9691 | 41869.054 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.2495 | 21.116 | 21015.9652 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.2495 | 21.0472 | 20947.2371 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.2495 | 19.3568 | 19256.797 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.2495 | 18.8808 | 18780.8418 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 9.1673 | 20.1785 | 20078.5414 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 27.206 | 0.2211 | 121.1091 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 18.2951 | 18195.0618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 18.2951 | 18195.0618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 18.2951 | 18195.0618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 18.0297 | 17929.6715 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 19.0602 | 18960.2485 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 19.0602 | 18960.2485 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 19.0602 | 18960.2485 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 21.7431 | 20.4494 | 20349.4221 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.3379 | 19.1095 | 19009.4588 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.3379 | 24.8477 | 24747.6553 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 33.9414 | 246.7517 | 246651.6686 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 13.8104 | 13710.4392 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 12.5215 | 12421.5233 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 11.1992 | 11099.173 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 9.1706 | 9070.6408 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 8.9026 | 8802.5778 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.5057 | 8.6508 | 8550.8354 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.4584 | 46.7091 | 46609.112 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.4584 | 22.3225 | 22222.492 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.2782 | 26.6677 | 26567.6863 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.2782 | 41.9802 | 41880.1658 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.2502 | 21.1156 | 21015.644 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.2502 | 21.0468 | 20946.7674 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.2502 | 19.3565 | 19256.541 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.2502 | 18.8805 | 18780.4658 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 9.1679 | 20.1779 | 20077.898 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 27.2088 | 0.2211 | 121.133 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 18.2948 | 18194.7809 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 18.2948 | 18194.7809 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 18.2948 | 18194.7809 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 18.0294 | 17929.3948 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 19.06 | 18959.9607 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 19.06 | 18959.9607 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 19.06 | 18959.9607 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 21.7403 | 20.4491 | 20349.117 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 13.3383 | 19.1097 | 19009.6711 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 13.3383 | 24.8481 | 24748.1405 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 33.9413 | 246.7526 | 246652.6337 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 13.8098 | 13709.7958 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 12.521 | 12420.9806 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 11.1987 | 11098.7244 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 9.1697 | 9069.675 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 8.9016 | 8801.6456 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.5041 | 8.6499 | 854993% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 9.8936 | 74.642 | 74541.9539 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 9.8936 | 18.9359 | 1883594% | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 13.2775 | 26.667 | 26567.0167 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 13.2775 | 41.9834 | 41883.4413 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.2492 | 21.1156 | 21015.5983 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.2492 | 21.0467 | 20946.6501 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.2492 | 19.3565 | 19256.4856 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.2492 | 18.8803 | 18780.3322 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 9.1671 | 20.1776 | 20077.5783 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 27.2073 | 0.2211 | 121.1016 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0142 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0142 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0142 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6234 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2012 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2012 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2012 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7432 | 20.4494 | 20349.377 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4508 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.3379 | 24.8476 | 24747.6387 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 33.9415 | 246.751 | 246651.0497 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3479 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4474 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1102 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.5004 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4423 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.7059 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.615 | 45.7963 | 45696.3454 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.615 | 22.4462 | 22346.2441 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.446 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3315 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 21.1156 | 21015.6003 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 21.0467 | 20946.7174 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 19.3565 | 19256.5086 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 18.8804 | 18780.4335 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 9.1673 | 20.1765 | 20076.5265 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 27.2087 | 0.2211 | 121.0959 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 18.2998 | 18199.7856 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 18.2998 | 18199.7856 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 18.2998 | 18199.7856 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 18.0345 | 17934.4535 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 19.0644 | 18964.4166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 19.0644 | 18964.4166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 19.0644 | 18964.4166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.602 | 20.4528 | 20352.7922 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.3339 | 19.1074 | 19007.4089 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.3339 | 24.8428 | 24742.8134 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 33.9387 | 246.6205 | 246520.5107 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 13.8101 | 13710.1027 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 12.5212 | 12421.2126 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 11.1989 | 11098.9278 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 9.1703 | 9070.2552 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 8.9022 | 8802.1866 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.4925 | 8.6504 | 8550.4405 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.6093 | 45.8669 | 45766.939 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.6093 | 22.4349 | 22334.931 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.2755 | 26.6737 | 26573.6857 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.2755 | 41.9515 | 41851.5409 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.1898 | 21.1245 | 21024.5293 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.1898 | 21.056 | 20955.9778 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.1898 | 19.3623 | 19262.2958 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.1898 | 18.8849 | 18784.9433 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 9.1588 | 20.1784 | 20078.4495 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 25.4842 | 0.2231 | 123.0827 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 18.2934 | 18193.4022 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 18.2934 | 18193.4022 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 18.2934 | 18193.4022 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 18.0282 | 17928.1601 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 19.058 | 18958.0493 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 19.058 | 18958.0493 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 19.058 | 18958.0493 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.5758 | 20.4463 | 20346.3048 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.3387 | 19.1106 | 19010.6095 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.3387 | 24.8499 | 24749.8838 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 33.9406 | 246.6523 | 246552.3056 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 13.803 | 13703.0222 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 12.5152 | 12415.2375 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 11.194 | 11093.9885 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 9.1597 | 9059.6697 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 8.892 | 8791.9612 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.4895 | 8.6406 | 8540.5505 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.5813 | 46.2765 | 46176.4926 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.5813 | 22.3706 | 22270.57 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.277 | 26.6686 | 26568.5947 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.277 | 41.9758 | 41875.8232 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.2158 | 21.12 | 21019.9597 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.2158 | 21.0511 | 20951.128 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.2158 | 19.3592 | 19259.155 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.2158 | 18.8823 | 18782.2761 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 9.1242 | 20.1932 | 20093.2044 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 24.845 | 0.2204 | 120.3598 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 18.299 | 18199.0368 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 18.299 | 18199.0368 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 18.299 | 18199.0368 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 18.0337 | 17933.6757 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 19.064 | 18963.9584 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 19.064 | 18963.9584 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 19.064 | 18963.9584 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.6074 | 20.4528 | 20352.8061 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.3376 | 19.1095 | 19009.5308 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.3376 | 24.8477 | 24747.7059 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 33.9411 | 246.7088 | 246608.8072 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 13.8102 | 13710.1582 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 12.5213 | 12421.2773 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 11.199 | 11098.9784 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 9.1703 | 9070.2531 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 8.9022 | 8802.1953 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.496 | 8.6505 | 8550.4589 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.6108 | 45.8514 | 45751.3655 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.6108 | 22.4375 | 22337.4553 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.2741 | 26.672 | 26572.0074 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.2741 | 41.9605 | 41860.4727 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.9823 | 21.2047 | 21104.735 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.9823 | 21.1627 | 21062.6953 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.9823 | 19.4229 | 19322.9171 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.9823 | 18.9627 | 18862.679 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 9.1666 | 20.1756 | 20075.6141 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 24.2687 | 0.2245 | 124.4831 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 18.295 | 18195.0371 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 18.295 | 18195.0371 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 18.295 | 18195.0371 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 18.0296 | 17929.6462 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 19.0602 | 18960.2245 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 19.0602 | 18960.2245 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 19.0602 | 18960.2245 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7425 | 20.4494 | 20349.3992 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.3376 | 19.1093 | 19009.3185 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.3376 | 24.8473 | 24747.3306 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 33.9411 | 246.7476 | 246647.5808 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 13.8104 | 13710.3789 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 12.5215 | 12421.4732 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 11.1991 | 11099.1313 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 9.1705 | 9070.5468 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 8.9025 | 8802.4878 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5057 | 8.6507 | 8550.749 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.6145 | 45.7972 | 45697.1693 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.6145 | 22.4461 | 22346.1233 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.2778 | 26.6683 | 26568.2549 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.2778 | 41.9775 | 41877.4768 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2369 | 21.1133 | 21013.2996 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2369 | 21.0429 | 20942.9216 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2369 | 19.3544 | 19254.4083 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2369 | 18.8769 | 18776.9152 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 8.8858 | 20.3737 | 20273.655 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 27.2071 | 0.2211 | 121.1225 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 18.0297 | 17929.7096 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2965 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2965 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2965 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 21.7431 | 20.4495 | 20349.4865 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.3374 | 19.1091 | 19009.1473 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.3374 | 24.8469 | 24746.9359 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 33.9412 | 246.7452 | 246645.2111 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 13.8103 | 13710.3104 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.4153 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 11.1991 | 11099.0837 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.4452 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 8.9024 | 8802.3889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.5058 | 8.6507 | 8550.6534 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.6144 | 45.7978 | 45697.8285 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.6144 | 22.446 | 22346.0397 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4688 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.2782 | 41.9812 | 41881.2038 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.9959 | 21.1552 | 21055.2003 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.9959 | 21.0993 | 20999.2563 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.9959 | 19.384 | 19284.0451 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.9959 | 18.9154 | 18815.4344 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 9.1599 | 20.1626 | 20062.5535 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 27.2075 | 0.2212 | 121.1619 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9721 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9721 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9721 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.5847 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1512 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1512 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1512 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 21.7432 | 20.4493 | 20349.3112 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5095 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.7733 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 33.9415 | 246.7533 | 246653.2712 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 13.8103 | 13710.2728 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3827 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 11.1991 | 11099.0568 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.3896 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.3352 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.6012 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.6141 | 45.7998 | 45699.8102 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.6141 | 22.4457 | 22345.7409 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.351 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.2782 | 41.9818 | 41881.7884 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2365 | 21.1045 | 21004.5098 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2365 | 21.0318 | 20931.786 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2365 | 19.3475 | 19247.482 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.2365 | 18.8686 | 18768.6046 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 9.1429 | 20.1382 | 20038.1957 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 27.2066 | 0.2212 | 121.1855 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.0655 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.0655 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 18.2951 | 18195.0655 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 18.0297 | 17929.6753 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 19.0603 | 18960.2546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 21.7431 | 20.4494 | 20349.4331 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.4982 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.338 | 24.8477 | 24747.7478 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 33.9415 | 246.7529 | 246652.9201 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 13.8103 | 13710.3024 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.4087 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 11.1991 | 1109908% | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.4324 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 8.9024 | 880238% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.6421 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.6144 | 45.7992 | 45699.2049 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.6144 | 22.4458 | 22345.7984 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4387 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3242 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.8147 | 21.2056 | 21105.559 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.8147 | 21.1683 | 21068.2904 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.8147 | 19.4211 | 19321.0778 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.8147 | 18.965 | 18864.996 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 8.4612 | 20.5983 | 20498.2965 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 27.2086 | 0.2211 | 121.1336 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 18.0298 | 17929.8008 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 19.0604 | 18960.3638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 19.0604 | 18960.3638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 19.0604 | 18960.3638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 21.7394 | 20.4495 | 20349.5203 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4304 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.3378 | 24.8476 | 24747.588 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 33.9413 | 246.7504 | 246650.3934 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 13.8103 | 13710.3497 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 12.5214 | 12421.447 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 11.1991 | 11099.1102 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 9.1705 | 9070.5129 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 8.9025 | 8802.4535 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.505 | 8.6507 | 8550.7145 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.6147 | 45.7967 | 45696.6539 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.6147 | 22.4462 | 22346.2085 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.2727 | 26.6795 | 26579.5005 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.2727 | 41.9239 | 41823.9457 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.2351 | 21.1166 | 21016.5666 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.2351 | 21.0476 | 20947.6436 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.2351 | 19.3571 | 19257.143 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.2351 | 18.8809 | 18780.8523 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 8.9506 | 20.3291 | 20229.0827 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 27.2057 | 0.2212 | 121.1531 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 18.295 | 18194.9752 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 18.295 | 18194.9752 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 18.295 | 18194.9752 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 18.0296 | 17929.5864 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 19.0602 | 18960.1549 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 19.0602 | 18960.1549 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 19.0602 | 18960.1549 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 21.7428 | 20.4493 | 20349.3154 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.3379 | 19.1095 | 19009.5095 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.3379 | 24.8478 | 24747.7757 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 33.9413 | 246.7533 | 246653.3024 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 13.8103 | 13710.2757 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 12.5214 | 12421.3859 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 11.1991 | 11099.0594 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 9.1704 | 9070.3937 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 8.9023 | 8802.34 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.5056 | 8.6506 | 8550.6059 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.6137 | 45.7996 | 45699.5978 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.6137 | 22.4458 | 22345.769 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.2779 | 26.6674 | 26567.351 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.2779 | 41.9818 | 41881.7714 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.2355 | 21.1049 | 21004.8578 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.2355 | 21.0323 | 20932.2664 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.2355 | 19.3478 | 19247.7687 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.2355 | 18.869 | 18768.9942 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 9.1427 | 20.1395 | 20039.4554 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 27.2057 | 0.2212 | 121.1819 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 18.0296 | 17929.6147 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 21.7433 | 20.4494 | 20349.3626 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4777 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.7009 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 33.9415 | 246.7522 | 246652.2126 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3397 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4404 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1039 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4875 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4306 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6938 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.6149 | 45.7962 | 45696.2161 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.6149 | 22.4463 | 22346.2669 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 21.1157 | 21015.6776 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 21.0468 | 20946.833 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 19.3566 | 19256.5732 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.2503 | 18.8805 | 18780.5316 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 9.168 | 20.1779 | 20077.9303 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 27.2092 | 0.2211 | 121.1202 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 18.0296 | 17929.6288 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2068 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2068 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2068 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 21.7429 | 20.4494 | 20349.3816 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4062 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.3378 | 24.8475 | 24747.5331 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 33.9414 | 246.7518 | 246651.7648 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 13.8104 | 13710.356 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 12.5215 | 12421.454 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1157 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.512 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 8.9025 | 8802.4544 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.7166 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.6147 | 45.7979 | 45697.876 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.6147 | 22.446 | 22346.0049 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4476 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.2973 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.2495 | 21.1156 | 21015.5551 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.2495 | 21.0466 | 20946.5594 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.2495 | 19.3564 | 19256.445 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.2495 | 18.8802 | 18780.2449 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 9.1667 | 20.1746 | 20074.6282 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 27.2065 | 0.2211 | 121.0859 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 18.295 | 18195.0135 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 18.295 | 18195.0135 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 18.295 | 18195.0135 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 18.0296 | 17929.624 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2001 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2001 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2001 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 21.7433 | 20.4494 | 20349.3748 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.338 | 19.1095 | 19009.4843 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.338 | 24.8477 | 24747.7153 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 33.9415 | 246.7521 | 246652.0627 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3432 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4433 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1064 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4926 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4356 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6986 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.615 | 45.7963 | 45696.339 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.615 | 22.4462 | 22346.2391 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4494 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.2782 | 41.9813 | 41881.2975 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.2491 | 21.1159 | 21015.9047 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.2491 | 21.0472 | 20947.1816 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.2491 | 19.3567 | 19256.7495 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.2491 | 18.8808 | 18780.8087 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 9.1552 | 20.179 | 20079.0417 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 27.2093 | 0.2211 | 121.1125 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 18.2951 | 18195.0602 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 18.2951 | 18195.0602 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 18.2951 | 18195.0602 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 18.0297 | 17929.6694 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 19.0603 | 18960.2519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 19.0603 | 18960.2519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 19.0603 | 18960.2519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 21.7427 | 20.4494 | 20349.4331 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4718 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6863 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 33.9415 | 246.752 | 246652.0046 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 13.8104 | 13710.3517 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 12.5215 | 12421.4503 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 11.1991 | 11099.1126 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 9.1705 | 9070.5058 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 8.9024 | 8802.4475 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.5058 | 8.6507 | 8550.7108 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.6151 | 45.7966 | 45696.6355 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.6151 | 22.4462 | 22346.1796 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4478 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.2782 | 41.9813 | 41881.2789 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.2496 | 21.1159 | 21015.8695 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.2496 | 21.047 | 20946.9768 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.2496 | 19.3567 | 19256.6914 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.2496 | 18.8806 | 18780.5606 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 9.144 | 20.1831 | 20083.0515 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 27.2042 | 0.221 | 121.013 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 18.295 | 18194.9981 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 18.295 | 18194.9981 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 18.295 | 18194.9981 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 18.0296 | 17929.6092 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 19.0602 | 18960.182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 19.0602 | 18960.182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 19.0602 | 18960.182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 21.7428 | 20.4494 | 20349.3516 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.338 | 19.1095 | 19009.5358 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.338 | 24.8478 | 24747.8377 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 33.9414 | 246.7531 | 246653.0609 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 13.8103 | 13710.2683 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 12.5214 | 12421.3797 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 11.1991 | 11099.0544 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 9.1704 | 9070.3829 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 8.9023 | 8802.3286 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.5057 | 8.6506 | 8550.595 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.6141 | 45.7979 | 45697.9047 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.6141 | 22.446 | 22346.0128 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.2781 | 26.6675 | 26567.4707 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.2781 | 41.9812 | 41881.1804 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.2472 | 21.1161 | 21016.1272 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.2472 | 21.0474 | 20947.4437 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.2472 | 19.3569 | 19256.8998 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.2472 | 18.881 | 18780.9625 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 9.1543 | 20.1792 | 20079.1805 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 27.2064 | 0.2211 | 121.1067 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6147 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3626 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.3379 | 19.1095 | 19009.4777 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.3379 | 24.8477 | 24747.7009 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 33.9415 | 246.7522 | 24665221% | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3397 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 12.5214 | 1242144% | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.1039 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.4875 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4306 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.6938 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.6149 | 45.7962 | 45696.2161 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.6149 | 22.4463 | 22346.2669 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.2503 | 21.1157 | 21015.6776 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.2503 | 21.0468 | 20946.833 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.2503 | 19.3566 | 19256.5732 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.2503 | 18.8805 | 18780.5316 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 9.168 | 20.1779 | 20077.9303 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 27.2092 | 0.2211 | 121.1202 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6147 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3626 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.3379 | 19.1095 | 19009.4777 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.3379 | 24.8477 | 24747.7009 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 33.9415 | 246.7522 | 246652.2126 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3397 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 12.5214 | 12421.4404 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.1039 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.4875 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4306 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.6938 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.6149 | 45.7962 | 45696.2161 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.6149 | 22.4463 | 22346.2669 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.2503 | 21.1157 | 21015.6776 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.2503 | 21.0468 | 20946.833 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.2503 | 19.3566 | 19256.5732 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.2503 | 18.8805 | 18780.5316 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 9.168 | 20.1779 | 20077.9303 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 27.2092 | 0.2211 | 121.1202 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 18.0296 | 17929.6098 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 21.7431 | 20.4494 | 20349.352 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.1344 | 19.2389 | 19138.8985 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.1344 | 24.9526 | 24852.5935 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 33.9407 | 246.7452 | 246645.1706 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 13.8103 | 13710.2983 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 12.5214 | 12421.4052 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 11.1991 | 11099.0754 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 9.1704 | 9070.4268 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 8.9024 | 8802.372 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.5058 | 8.6506 | 8550.6368 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.6149 | 45.7967 | 45696.7171 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1834 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4601 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.2782 | 41.9813 | 41881.2606 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.2503 | 21.1157 | 21015.7077 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.2503 | 21.0469 | 20946.8841 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.2503 | 19.3566 | 19256.5997 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.2503 | 18.8806 | 18780.5775 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 9.168 | 20.178 | 20077.9883 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 27.2089 | 0.2211 | 121.1181 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 18.295 | 18194.9986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 18.0296 | 17929.6098 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 19.0602 | 18960.1826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 21.7431 | 20.4494 | 20349.352 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.1344 | 19.2389 | 19138.8985 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.1344 | 24.9526 | 24852.5935 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 33.9407 | 246.7452 | 246645.1706 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 13.8103 | 13710.2983 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 12.5214 | 12421.4052 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 11.1991 | 11099.0754 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 9.1704 | 9070.4268 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 8.9024 | 8802.372 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.5058 | 8.6506 | 8550.6368 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.6149 | 45.7967 | 45696.7171 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.6149 | 22.4462 | 22346.1834 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.2782 | 26.6675 | 26567.4601 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.2782 | 41.9813 | 41881.2606 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.2503 | 21.1157 | 21015.7077 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.2503 | 21.0469 | 20946.8841 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.2503 | 19.3566 | 19256.5997 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.2503 | 18.8806 | 18780.5775 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 9.168 | 20.178 | 20077.9883 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 27.2089 | 0.2211 | 121.1181 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 18.295 | 18194.9922 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 18.295 | 18194.9922 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 18.295 | 18194.9922 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 18.0296 | 17929.6033 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1774 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1774 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1774 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 21.7432 | 20.4493 | 20349.347 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.2796 | 19.0638 | 18963.8337 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.2796 | 24.7892 | 24689.2407 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 33.9403 | 246.738 | 246637.955 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 13.8103 | 13710.3343 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 12.5214 | 12421.4359 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 11.1991 | 11099.1006 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 9.1705 | 9070.4804 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 8.9024 | 8802.423 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.5059 | 8.6507 | 8550.6864 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.6149 | 45.7967 | 45696.7182 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.6149 | 22.4462 | 22346.1855 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.2782 | 26.6675 | 26567.4501 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.2782 | 41.9813 | 41881.2939 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.2502 | 21.1157 | 21015.6509 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.2502 | 21.0468 | 20946.7824 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.2502 | 19.3565 | 19256.5472 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.2502 | 18.8805 | 18780.4816 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 9.168 | 20.178 | 20077.9515 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 27.2088 | 0.2211 | 121.1273 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 18.295 | 18194.9896 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 18.295 | 18194.9896 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 18.295 | 18194.9896 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 18.0296 | 17929.5997 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 19.0602 | 18960.1733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 19.0602 | 18960.1733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 19.0602 | 18960.1733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 21.7431 | 20.4493 | 20349.3422 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.2629 | 19.0514 | 18951.388 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.2629 | 24.7732 | 24673.1585 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 33.9399 | 246.7331 | 246633.1302 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 13.8103 | 13710.3333 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 12.5214 | 12421.4349 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 11.1991 | 11099.0995 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 9.1705 | 9070.4781 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 8.9024 | 8802.4215 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.5059 | 8.6507 | 8550.685 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.6149 | 45.7967 | 45696.7159 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.6149 | 22.4462 | 22346.1836 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.2782 | 26.6675 | 26567.4501 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.2782 | 41.9813 | 41881.294 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.2502 | 21.1156 | 21015.6443 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.2502 | 21.0468 | 20946.7696 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.2502 | 19.3565 | 19256.5406 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.2502 | 18.8805 | 18780.4686 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 9.168 | 20.1779 | 20077.9479 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 27.2087 | 0.2211 | 121.1293 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 18.295 | 18194.9795 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 18.295 | 18194.9795 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 18.295 | 18194.9795 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 18.0296 | 17929.5912 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 21.7432 | 20.4493 | 20349.3311 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.338 | 19.0994 | 18999.4216 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.338 | 24.836 | 24736.0243 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 33.9413 | 246.7539 | 246653.8759 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3018 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4081 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 11.1991 | 11099.0774 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 9.1704 | 9070.4314 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 8.9024 | 8802.3756 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.5059 | 8.6506 | 8550.6406 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.6148 | 45.7967 | 45696.743 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.6148 | 22.4462 | 22346.1815 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4536 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.2782 | 41.9813 | 41881.2758 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.2503 | 21.1157 | 21015.6662 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.2503 | 21.0468 | 20946.8113 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.2503 | 19.3566 | 19256.5624 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.2503 | 18.8805 | 18780.5094 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 9.168 | 20.1779 | 20077.9301 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 27.2089 | 0.2211 | 121.13 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 18.295 | 18195.0029 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 18.295 | 18195.0029 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 18.295 | 18195.0029 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 18.0296 | 17929.6136 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1894 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1894 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1894 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 21.7433 | 20.4494 | 20349.3613 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.3379 | 19.109 | 19008.9837 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.3379 | 24.847 | 24746.9984 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 33.9415 | 246.7527 | 246652.6661 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3392 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 12.5214 | 12421.44 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 11.1991 | 11099.1035 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4866 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4298 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.5059 | 8.6507 | 8550.693 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.6149 | 45.7967 | 45696.6951 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1885 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.2503 | 21.1157 | 21015.6746 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.2503 | 21.0468 | 20946.8276 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.2503 | 19.3566 | 19256.5706 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.2503 | 18.8805 | 18780.5257 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 9.168 | 20.178 | 20077.9734 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 27.2092 | 0.2211 | 121.1207 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 18.2949 | 18194.9427 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 18.2949 | 18194.9427 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 18.2949 | 18194.9427 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 18.0296 | 17929.5563 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 19.0601 | 18960.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 19.0601 | 18960.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 19.0601 | 18960.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 21.7421 | 20.4493 | 2034926% | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5313 | 19.4674 | 19367.3608 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5313 | 25.1849 | 2508486% | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 33.9242 | 246.2118 | 246111.7642 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 13.8105 | 13710.4948 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 12.5216 | 12421.571 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 11.1992 | 11099.212 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 9.1707 | 9070.7188 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 8.9027 | 8802.6533 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.5059 | 8.6509 | 8550.9099 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.615 | 45.7968 | 45696.8004 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.615 | 22.4462 | 22346.1651 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4928 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.2782 | 41.9811 | 41881.0892 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.2488 | 21.1152 | 21015.2181 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.2488 | 21.046 | 20945.9508 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.2488 | 19.3561 | 19256.1291 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.2488 | 18.8797 | 18779.6611 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 9.1678 | 20.1777 | 20077.7315 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 27.2047 | 0.2212 | 121.217 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 18.295 | 18194.9841 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 18.295 | 18194.9841 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 18.295 | 18194.9841 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 18.0296 | 17929.5953 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.169 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.169 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.169 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 21.7433 | 20.4493 | 20349.3373 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.3178 | 19.0377 | 18937.7265 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.3178 | 24.7248 | 24624.799 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 33.9371 | 246.7041 | 246604.1386 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3329 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4347 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 11.1991 | 11099.0992 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4783 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4212 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.5059 | 8.6507 | 8550.6847 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.6149 | 45.7967 | 45696.6918 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1867 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.2782 | 26.6674 | 26567.4472 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3257 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.2502 | 21.1156 | 21015.628 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.2502 | 21.0467 | 20946.7419 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.2502 | 19.3565 | 19256.5269 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.2502 | 18.8804 | 18780.443 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 9.168 | 20.178 | 20077.9541 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 27.209 | 0.2211 | 121.128 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 18.2954 | 18195.3893 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 18.2954 | 18195.3893 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 18.2954 | 18195.3893 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 18.03 | 17929.9892 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6153 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6153 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6153 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 21.7444 | 20.4499 | 20349.8622 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.3674 | 19.2025 | 19102.543 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.3674 | 24.9607 | 24860.6533 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 33.9517 | 246.1071 | 246007.1323 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 13.8108 | 13710.7746 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 12.5218 | 12421.809 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 11.1994 | 11099.4089 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 9.1711 | 9071.13 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 8.9031 | 8803.0515 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.5065 | 8.6513 | 8551.2954 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.6157 | 45.7955 | 45695.498 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.6157 | 22.4463 | 22346.3114 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.2783 | 26.6674 | 26567.3842 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.2783 | 41.9816 | 41881.6217 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.2514 | 21.1161 | 21016.0801 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.2514 | 21.0476 | 20947.5853 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.2514 | 19.357 | 19256.9555 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.2514 | 18.8813 | 18781.263 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 9.1685 | 20.1788 | 20078.794 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 27.2152 | 0.2209 | 120.9277 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0116 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0116 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0116 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 18.0296 | 17929.6227 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1962 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1962 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1962 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 21.7431 | 20.4494 | 20349.3669 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.584 | 20.3482 | 20248.2458 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.584 | 25.8215 | 25721.498 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 33.9193 | 243.7474 | 243647.3562 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 13.8105 | 13710.4591 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 12.5215 | 12421.5411 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 11.1992 | 11099.1875 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 9.1707 | 9070.6663 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 8.9026 | 8802.6026 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.506 | 8.6509 | 8550.8602 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.615 | 45.7967 | 45696.6828 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.615 | 22.4462 | 22346.1878 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4632 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.2782 | 41.9812 | 41881.247 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.2499 | 21.1155 | 21015.516 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.2499 | 21.0465 | 20946.5309 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.2499 | 19.3564 | 19256.4193 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.2499 | 18.8802 | 18780.237 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 9.1679 | 20.1779 | 20077.8781 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 27.2082 | 0.2211 | 121.1489 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 18.03 | 17929.9769 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 19.0606 | 18960.6026 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 19.0606 | 18960.6026 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 19.0606 | 18960.6026 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 21.7445 | 20.4498 | 20349.8495 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.3688 | 19.2396 | 19139.6439 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.3688 | 25.0057 | 24905.7104 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 33.9522 | 246.4173 | 246317.2541 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 13.8108 | 13710.7668 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 12.5218 | 12421.8019 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 11.1994 | 11099.4032 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 9.1711 | 9071.1165 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 8.903 | 8803.0395 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.5066 | 8.6513 | 8551.2838 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.6157 | 45.7955 | 45695.4904 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.6157 | 22.4463 | 22346.3136 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.2783 | 26.6674 | 26567.3729 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.2783 | 41.9817 | 41881.6856 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.2514 | 21.1161 | 21016.0689 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.2514 | 21.0476 | 20947.5673 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.2514 | 19.3569 | 19256.9463 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.2514 | 18.8812 | 18781.2475 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 9.1685 | 20.1788 | 20078.7828 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 27.2153 | 0.2209 | 120.9302 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0169 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0169 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0169 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6271 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3802 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.0729 | 19.0454 | 18945.4038 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.0729 | 24.7092 | 24609.2379 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 33.9465 | 246.8081 | 246708.1203 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3313 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 12.5214 | 12421.4333 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.0981 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.475 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4178 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.6815 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.615 | 45.7967 | 45696.6724 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.615 | 22.4462 | 22346.1911 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.2783 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.2783 | 41.9813 | 41881.3102 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.2505 | 21.1157 | 21015.7307 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.2505 | 21.0469 | 20946.9321 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.2505 | 19.3566 | 19256.6232 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.2505 | 18.8806 | 18780.6269 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 9.168 | 20.178 | 20078.0141 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 27.2095 | 0.2211 | 121.1084 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 18.4062 | 18306.2061 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 18.4062 | 18306.2061 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 18.4062 | 18306.2061 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 18.1395 | 18039.4545 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 19.1726 | 19072.6112 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 19.1726 | 19072.6112 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 19.1726 | 19072.6112 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.9861 | 20.5667 | 20466.654 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3549 | 19.1226 | 19022.6293 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3549 | 24.8765 | 24776.5017 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.953 | 246.2352 | 246135.1754 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 13.8371 | 13737.0672 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 12.5439 | 12443.9136 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 11.2177 | 11117.7239 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 9.2108 | 9110.8012 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 8.9413 | 8841.3099 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4674 | 8.6882 | 8588.2415 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6269 | 45.845 | 45744.9548 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6269 | 22.437 | 22336.967 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2702 | 26.6927 | 26592.6919 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2702 | 41.8616 | 41761.5587 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2609 | 21.1476 | 21047.5927 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2609 | 21.0982 | 20998.1861 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2609 | 19.3841 | 19284.0602 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2609 | 18.9255 | 18825.5214 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1738 | 20.1982 | 20098.1654 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 25.3002 | 0.2058 | 105.7842 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 18.3088 | 18208.8218 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 18.3088 | 18208.8218 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 18.3088 | 18208.8218 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 18.0437 | 17943.7014 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 19.0725 | 18972.4567 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 19.0725 | 18972.4567 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 19.0725 | 18972.4567 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.0215 | 20.4595 | 20359.4744 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.3368 | 19.1105 | 19010.4709 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.3368 | 24.8492 | 24749.2174 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 33.9273 | 244.5195 | 244419.463 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 13.8304 | 13730.3921 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 12.5377 | 12437.7491 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 11.2141 | 11114.1113 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 9.2015 | 9101.547 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 8.9317 | 8831.6721 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.418 | 8.6783 | 8578.279 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.6053 | 45.9645 | 45864.5228 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.6053 | 22.4191 | 22319.052 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.1947 | 26.8662 | 26766.1872 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.1947 | 41.084 | 40983.9721 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.2473 | 21.1158 | 21015.7773 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.2473 | 21.0468 | 20946.7654 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.2473 | 19.3566 | 19256.5749 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.2473 | 18.8803 | 18780.3109 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 9.1675 | 20.1779 | 20077.9466 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 27.1953 | 0.2212 | 121.1797 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 18.3083 | 18208.3434 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 18.3083 | 18208.3434 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 18.3083 | 18208.3434 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 18.0432 | 17943.1509 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 19.0717 | 1897168% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 19.0717 | 18971.6784 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 19.0717 | 1897168% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 21.387 | 20.4581 | 20358.1154 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.3374 | 19.1092 | 19009.1537 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.3374 | 24.847 | 24746.9637 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 33.9433 | 246.7245 | 246624.5368 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 13.8274 | 13727.4126 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 12.5338 | 12433.7995 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 11.2122 | 11112.2494 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 9.2026 | 9102.6442 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 8.9315 | 8831.4989 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 10.6527 | 8.677 | 8576.9815 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.6091 | 45.908 | 45807.9905 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.6091 | 22.4281 | 22328.128 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.2004 | 26.9059 | 26805.8538 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.2004 | 40.9036 | 40803.6269 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.2482 | 21.1163 | 21016.3315 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.2482 | 21.0477 | 20947.6832 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.2482 | 19.3571 | 19257.0708 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.2482 | 18.8811 | 18781.149 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.1678 | 20.1783 | 20078.2723 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 27.1945 | 0.2211 | 121.1166 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 18.2948 | 18194.7738 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 18.2948 | 18194.7738 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 18.2948 | 18194.7738 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 18.0294 | 17929.386 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 19.06 | 18959.9807 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 19.06 | 18959.9807 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 19.06 | 18959.9807 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.7385 | 20.4492 | 20349.1833 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.3253 | 19.1105 | 19010.4707 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.3253 | 24.8463 | 24746.3079 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 33.9105 | 243.9302 | 243830.2477 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 13.8103 | 13710.324 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 12.5214 | 12421.4251 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 11.1991 | 11099.0913 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 9.1705 | 9070.4747 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 8.9024 | 8802.4168 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.5056 | 8.6507 | 8550.6792 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.6149 | 45.7968 | 45696.8407 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1606 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.2782 | 26.6673 | 26567.3049 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.2782 | 41.982 | 41882.0136 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.2385 | 21.1196 | 21019.5708 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.2385 | 21.0521 | 20952.0982 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.2385 | 19.3596 | 19259.5503 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.2385 | 18.8844 | 18784.4491 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.1672 | 20.1788 | 20078.8055 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 27.1822 | 0.2211 | 121.1391 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 18.2859 | 18185.9377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 18.2859 | 18185.9377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 18.2859 | 18185.9377 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 18.0208 | 17920.8343 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 19.0503 | 18950.3448 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 19.0503 | 18950.3448 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 19.0503 | 18950.3448 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5832 | 20.438 | 20338.0239 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3337 | 19.1132 | 19013.2189 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3337 | 24.8529 | 24752.9256 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.9153 | 244.8767 | 244776.7272 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 13.8064 | 13706.3911 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 12.5181 | 12418.1024 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 11.1964 | 11096.3534 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 9.1646 | 9064.6002 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 8.8967 | 8796.7378 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4987 | 8.6452 | 8545.1831 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6121 | 45.8066 | 45706.5636 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6121 | 22.4448 | 22344.7981 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2778 | 26.6682 | 26568.1617 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2778 | 41.9779 | 41877.9462 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2399 | 21.1113 | 21011.3112 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2399 | 21.039 | 20938.9726 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2399 | 19.3525 | 19252.4935 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2399 | 18.873 | 18773.0025 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1665 | 20.1758 | 20075.7949 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.5821 | 0.2248 | 124.8186 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 18.3248 | 18224.8231 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 18.3248 | 18224.8231 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 18.3248 | 18224.8231 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 18.0606 | 17960.5744 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 19.0852 | 18985.2184 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 19.0852 | 18985.2184 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 19.0852 | 18985.2184 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.5747 | 20.4675 | 20367.5169 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3248 | 19.1022 | 19002.1686 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3248 | 24.8307 | 24730.6705 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.9255 | 246.3627 | 246262.6969 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 13.8003 | 13700.2596 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 12.5128 | 12412.7572 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 11.1921 | 11092.1003 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 9.1561 | 9056.0728 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 8.8884 | 8788.3552 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3529 | 8.6369 | 8536.9424 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.606 | 45.8275 | 45727.5447 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.606 | 22.4418 | 22341.8335 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2711 | 26.6903 | 26590.3481 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2711 | 41.8716 | 41771.5586 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.0164 | 21.2087 | 21108.7186 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.0164 | 21.1687 | 21068.6995 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.0164 | 19.4268 | 19326.7762 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.0164 | 18.9685 | 18868.4547 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.1556 | 20.1929 | 20092.8622 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 26.8884 | 0.2239 | 123.854 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 18.2982 | 18198.2227 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 18.2982 | 18198.2227 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 18.2982 | 18198.2227 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 18.0328 | 17932.7516 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 19.0638 | 18963.8094 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 19.0638 | 18963.8094 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 19.0638 | 18963.8094 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.6934 | 20.4537 | 20353.7407 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.3377 | 19.1095 | 19009.4784 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.3377 | 24.8477 | 24747.6579 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 33.9419 | 246.7452 | 246645.1999 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 13.8109 | 13710.9349 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 12.5219 | 12421.9434 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 11.1995 | 11099.5224 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 9.1714 | 9071.3688 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 8.9033 | 8803.2818 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.5041 | 8.6515 | 8551.5167 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.6155 | 45.7974 | 45697.385 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.6155 | 22.446 | 22346.0224 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.2758 | 26.6662 | 26566.2476 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.2758 | 41.9882 | 41888.1942 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 19.1419 | 21.3874 | 21287.4459 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 19.1419 | 21.3862 | 21286.1567 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 19.1419 | 19.5482 | 19448.2437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 19.1419 | 19.099 | 18998.992 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 9.1405 | 20.1885 | 20088.4818 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 27.103 | 0.2202 | 120.2443 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 18.2852 | 18185.1688 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 18.2852 | 18185.1688 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 18.2852 | 18185.1688 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 18.0201 | 17920.0874 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 19.0495 | 18949.4744 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 19.0495 | 18949.4744 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 19.0495 | 18949.4744 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.5897 | 20.437 | 20336.9602 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3334 | 19.1102 | 19010.1935 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.3334 | 24.8474 | 24747.3922 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.9212 | 245.6773 | 245577.2827 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 13.8061 | 13706.0749 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 12.5178 | 12417.8325 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 11.1961 | 11096.1315 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 9.1641 | 9064.1434 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 8.8963 | 8796.2946 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.4972 | 8.6448 | 8544.7519 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6118 | 45.8068 | 45706.7886 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.6118 | 22.4448 | 22344.7824 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2778 | 26.6684 | 26568.4022 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2778 | 41.9767 | 41876.7317 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2393 | 21.111 | 21010.9898 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2393 | 21.0384 | 20938.3675 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2393 | 19.3522 | 19252.1938 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.2393 | 18.8724 | 18772.4209 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.1666 | 20.1756 | 20075.619 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.6109 | 0.2252 | 125.2056 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 18.5049 | 18404.8912 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 18.5049 | 18404.8912 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 18.5049 | 18404.8912 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 18.2395 | 18139.5003 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 19.2599 | 19159.9231 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 19.2599 | 19159.9231 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 19.2599 | 19159.9231 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 18.5725 | 20.6379 | 20537.8741 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.3355 | 19.1095 | 19009.5184 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.3355 | 24.847 | 24747.0483 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 33.938 | 246.4645 | 246364.5183 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 13.8216 | 13721.5806 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 12.5306 | 12430.5899 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 11.2069 | 11106.8755 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 9.1887 | 9088.7308 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 8.9198 | 8819.7933 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.3136 | 8.6672 | 8567.2498 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.6129 | 45.855 | 45755.0041 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.6129 | 22.4366 | 22336.5775 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.2602 | 26.7232 | 26623.2472 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 13.2602 | 41.7176 | 41617.5561 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 20.2501 | 21.1162 | 21016.2058 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 20.2501 | 21.0476 | 20947.6126 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 20.2501 | 19.357 | 19257.0011 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 20.2501 | 18.8812 | 18781.1652 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 9.1677 | 20.1783 | 20078.2908 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 25.8002 | 0.2211 | 121.1348 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 18.2923 | 18192.3333 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 18.2923 | 18192.3333 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 18.2923 | 18192.3333 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 18.027 | 17926.9915 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 19.0575 | 18957.4506 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 19.0575 | 18957.4506 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 19.0575 | 18957.4506 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.728 | 20.4464 | 20346.4463 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.3372 | 19.1091 | 19009.1181 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.3372 | 24.8469 | 24746.8535 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 33.9405 | 246.7285 | 246628.5046 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 13.8096 | 13709.5861 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 12.5208 | 12420.8046 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 11.1986 | 11098.5796 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 9.1694 | 9069.3578 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 8.9013 | 8801.3386 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.5046 | 8.6496 | 8549.6376 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.6146 | 45.797 | 45697.0142 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.6146 | 22.4462 | 22346.1599 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.278 | 26.6717 | 26571.7484 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.278 | 41.9602 | 41860.1894 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 20.2462 | 21.1185 | 21018.5245 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 20.2462 | 21.0502 | 20950.2088 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 20.2462 | 19.3587 | 19258.6862 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 20.2462 | 18.8828 | 18782.7952 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 9.1678 | 20.1789 | 20078.8839 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 27.1481 | 0.2217 | 121.7077 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 18.2829 | 18182.9375 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 18.2829 | 1818294% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 18.2829 | 18182.9375 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 18.0176 | 1791759% | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 19.049 | 18948.9794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 19.049 | 18948.9794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 19.049 | 18948.9794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.7603 | 20.4393 | 20339.3037 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.339 | 19.11 | 19010.0176 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.339 | 24.849 | 24749.0149 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 33.9423 | 246.7703 | 246670.2873 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 13.8109 | 13710.8755 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 12.5219 | 12421.9194 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 11.1995 | 11099.5016 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 9.1711 | 9071.1485 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 8.9031 | 8803.0841 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.5082 | 8.6513 | 8551.3404 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.6159 | 45.793 | 45692.9907 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.6159 | 22.4467 | 22346.7273 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.2784 | 26.6654 | 26565.3688 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.2784 | 41.9917 | 41891.7269 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 20.2527 | 21.1157 | 21015.7029 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 20.2527 | 21.0473 | 20947.2644 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 20.2527 | 19.3567 | 19256.6956 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 20.2527 | 18.8811 | 18781.1272 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 9.1686 | 20.1787 | 20078.7224 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 27.2555 | 0.2207 | 120.6957 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 18.2952 | 18195.1851 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 18.2952 | 18195.1851 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 18.2952 | 18195.1851 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 18.0298 | 17929.7817 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 19.0605 | 18960.4668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 19.0605 | 18960.4668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 19.0605 | 18960.4668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.742 | 20.4498 | 20349.8046 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.3378 | 19.1095 | 19009.4685 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.3378 | 24.8477 | 24747.6605 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 33.9416 | 246.7489 | 246648.8567 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 13.8106 | 13710.6345 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 12.5217 | 12421.6866 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 11.1993 | 11099.3086 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 9.1709 | 9070.9392 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 8.9029 | 8802.8648 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.5044 | 8.6511 | 8551.1125 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.615 | 45.7972 | 45697.1706 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.615 | 22.4461 | 22346.1003 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.1979 | 26.6991 | 26599.0841 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.1979 | 41.8601 | 41760.0624 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 20.2271 | 21.1086 | 21008.6491 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 20.2271 | 21.0404 | 20940.4467 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 20.2271 | 19.3508 | 19250.8003 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 20.2271 | 18.8763 | 18776.2871 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.1598 | 20.1801 | 20080.1237 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 27.1791 | 0.221 | 120.9768 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 18.295 | 18194.9928 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 18.295 | 18194.9928 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 18.295 | 18194.9928 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 18.0296 | 17929.6032 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 21.7433 | 20.4493 | 20349.3434 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.3379 | 19.1095 | 19009.4728 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.3379 | 24.8477 | 24747.6886 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 33.9414 | 246.7504 | 246650.4448 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 13.8103 | 13710.3465 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 12.5214 | 12421.4454 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 11.1991 | 11099.1087 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 9.1705 | 9070.4966 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 8.9024 | 8802.4395 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 12.5059 | 8.6507 | 8550.7024 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.6149 | 45.7967 | 45696.6565 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.6149 | 22.4462 | 22346.1957 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.2781 | 26.6668 | 26566.7557 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 13.2781 | 41.9848 | 41884.7828 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 20.1757 | 21.1226 | 21022.6027 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 20.1757 | 21.057 | 20956.9778 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 20.1757 | 19.3612 | 19261.1733 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 20.1757 | 18.8874 | 18787.3981 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 9.1671 | 20.1783 | 20078.2745 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532958 [NEOSH4 1 13.200] CKT 1 | 27.2091 | 0.2211 | 121.1244 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 18.295 | 18194.9853 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 18.295 | 18194.9853 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 18.295 | 18194.9853 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 18.0296 | 17929.5972 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 19.0602 | 18960.168 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 19.0602 | 18960.168 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 19.0602 | 18960.168 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 21.7432 | 20.4493 | 20349.3319 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.3379 | 19.1095 | 19009.4713 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.3379 | 24.8477 | 24747.6826 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 33.9413 | 246.7498 | 246649.802 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 13.8104 | 13710.3511 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 12.5214 | 12421.4493 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 11.1991 | 11099.1119 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 9.1705 | 9070.5034 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 8.9024 | 8802.446 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 12.5059 | 8.6507 | 8550.7088 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.6149 | 45.7966 | 45696.5876 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.6149 | 22.4462 | 22346.2053 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.2779 | 26.6663 | 26566.2746 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 13.2779 | 41.9872 | 41887.1824 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 20.1239 | 21.128 | 21028.0294 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 20.1239 | 21.0649 | 20964.8564 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 20.1239 | 19.3649 | 19264.8535 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 20.1239 | 18.8928 | 18792.8047 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 9.1664 | 20.1785 | 20078.5008 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] TO BUS 532959 [NEOSH5 1 13.200] CKT 1 | 27.2091 | 0.2211 | 121.1265 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 18.295 | 18195.0411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 18.295 | 18195.0411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 18.295 | 18195.0411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 18.0297 | 17929.6547 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 19.0602 | 18960.2104 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 19.0602 | 18960.2104 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 19.0602 | 18960.2104 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.7417 | 20.4494 | 20349.3555 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.3379 | 19.1095 | 19009.4661 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.3379 | 24.8477 | 24747.6723 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 33.9413 | 246.7494 | 246649.416 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 13.8103 | 13710.3174 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 12.5214 | 12421.421 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 11.1991 | 11099.0882 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 9.1705 | 9070.4557 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 8.9024 | 8802.3996 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.5058 | 8.6507 | 8550.6635 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.6149 | 45.7968 | 45696.8383 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.6149 | 22.4462 | 22346.1632 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.2782 | 26.6671 | 26567.0538 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.2782 | 41.9832 | 41883.2443 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 20.1873 | 21.1278 | 21027.7786 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 20.1873 | 21.0643 | 20964.2734 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 20.1873 | 19.3655 | 19265.5149 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 20.1873 | 18.8934 | 18793.4442 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 9.1678 | 20.1785 | 20078.4767 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 27.2055 | 0.2211 | 121.1474 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0488 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0488 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0488 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 18.0297 | 17929.6587 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2337 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2337 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2337 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 21.7431 | 20.4494 | 20349.4043 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.3352 | 19.1093 | 19009.2604 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.3352 | 24.8469 | 24746.9405 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 26.4017 | 21.7295 | 21629.5131 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 13.8104 | 13710.3689 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 12.5215 | 12421.4647 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 11.1991 | 11099.1241 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 9.1705 | 9070.5354 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 8.9025 | 8802.4764 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 12.5058 | 8.6507 | 8550.7376 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.711 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1837 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.5074 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 13.2782 | 41.981 | 41881.0083 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.679 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8302 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5737 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5259 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9813 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539643 [ROLLHLS3 115.00] CKT 1 | 27.209 | 0.2211 | 121.118 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 18.295 | 18195.047 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 18.295 | 18195.047 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 18.295 | 18195.047 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 18.0297 | 17929.6578 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 19.0602 | 18960.2325 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 19.0602 | 18960.2325 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 19.0602 | 18960.2325 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 21.7434 | 20.4494 | 20349.4038 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.3322 | 19.1077 | 19007.6646 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.3322 | 24.8445 | 24744.4539 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 19.6049 | 13.5599 | 13459.8909 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 13.8104 | 13710.3689 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 12.5215 | 12421.4633 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.1233 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.537 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 8.9025 | 8802.4778 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.7385 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.615 | 45.7967 | 45696.6658 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.615 | 22.4462 | 22346.1863 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.5285 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 13.2782 | 41.9809 | 41880.9037 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 20.2504 | 21.1157 | 21015.7049 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 20.2504 | 21.0469 | 20946.8827 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 20.2504 | 19.3566 | 19256.5986 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 20.2504 | 18.8806 | 18780.579 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 9.168 | 20.178 | 20078.0073 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539678 [GRTBEND3 115.00] CKT 1 | 27.2095 | 0.2211 | 121.1127 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0005 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0005 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0005 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.6112 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 21.7433 | 20.4494 | 20349.3583 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.3373 | 19.1093 | 19009.33 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.3373 | 24.8474 | 24747.4064 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 25.7911 | 25.3734 | 25273.4479 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3316 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4334 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0986 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4758 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4193 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6828 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.6948 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1859 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.4565 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.2789 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 20.2504 | 21.1157 | 21015.6797 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 20.2504 | 21.0468 | 20946.8367 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 20.2504 | 19.3566 | 19256.575 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 20.2504 | 18.8805 | 18780.535 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 9.168 | 20.178 | 2007798% | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539698 [WALDO 3 115.00] CKT 1 | 27.2092 | 0.2211 | 121.1203 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 18.295 | 1819498% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 18.295 | 18194.9795 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 18.295 | 18194.9795 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 18.0296 | 17929.5908 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 21.7432 | 20.4493 | 20349.3314 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.3376 | 19.1092 | 19009.2262 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.3376 | 24.8472 | 24747.2291 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 33.9308 | 286.0983 | 285998.3465 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 13.8103 | 13710.315 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 12.5214 | 12421.4196 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 11.1991 | 11099.0873 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 9.1705 | 9070.4516 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 8.9024 | 8802.3953 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 12.5059 | 8.6507 | 8550.6597 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.6149 | 45.7967 | 45696.7485 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.6149 | 22.4462 | 22346.1825 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.2782 | 26.6674 | 26567.4498 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 13.2782 | 41.9813 | 41881.2948 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 20.2502 | 21.1156 | 21015.6474 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 20.2502 | 21.0468 | 20946.7765 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 20.2502 | 19.3565 | 19256.5452 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 20.2502 | 18.8805 | 18780.4764 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 9.1679 | 20.1779 | 20077.9268 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539734 [WALDO 1 34.500] TO BUS 539938 [WALDO-T 7.2000] CKT 1 | 27.2088 | 0.2211 | 121.1319 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 18.4062 | 18306.1711 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 18.4062 | 18306.1711 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 18.4062 | 18306.1711 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 18.1441 | 18044.0561 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 19.148 | 19047.9658 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 19.148 | 19047.9658 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 19.148 | 19047.9658 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.3072 | 20.5014 | 20401.4244 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3494 | 19.1162 | 19016.2259 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3494 | 24.8633 | 24763.283 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.9488 | 246.8286 | 246728.5643 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 13.8091 | 13709.0647 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 12.5198 | 12419.8199 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 11.198 | 11098.0399 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 9.171 | 9070.9798 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 8.9025 | 8802.5044 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2484 | 8.6504 | 8550.3972 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.6117 | 45.9321 | 45832.1469 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.6117 | 22.4238 | 22323.8421 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2526 | 26.7519 | 26651.8564 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2526 | 41.5838 | 41483.8379 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2455 | 21.1243 | 21024.3148 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2455 | 21.0601 | 20960.1122 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2455 | 19.3638 | 19263.8131 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2455 | 18.8918 | 18791.8074 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.1707 | 20.1856 | 20085.6227 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542955 [LAC G1 1 22.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 27.1081 | 0.2195 | 119.525 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 18.5969 | 18496.901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 18.5969 | 18496.901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 18.5969 | 18496.901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 18.3308 | 18230.7908 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 19.3505 | 19250.4968 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 19.3505 | 19250.4968 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 19.3505 | 19250.4968 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.1707 | 20.7285 | 20628.5002 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3486 | 19.1158 | 19015.8368 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3486 | 24.8623 | 24762.3464 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.9501 | 246.8244 | 246724.4457 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 13.8437 | 13743.7452 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 12.5491 | 12449.1007 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 11.2223 | 11122.2625 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 9.2228 | 9122.7514 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 8.9525 | 8852.5154 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2483 | 8.6988 | 8598.7687 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.619 | 45.9353 | 45835.251 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.619 | 22.4226 | 22322.6447 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2487 | 26.7649 | 26664.8807 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2487 | 41.5251 | 41425.116 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2564 | 21.1305 | 21030.5383 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2564 | 21.0711 | 20971.0503 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2564 | 19.3695 | 19269.4813 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2564 | 18.902 | 18801.9944 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.1713 | 20.1873 | 20087.2803 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542956 [LAC G2 1 24.000] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 27.0976 | 0.219 | 118.9865 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 18.2902 | 18190.1986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 18.2902 | 18190.1986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 18.2902 | 18190.1986 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 18.0251 | 17925.1008 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 19.054 | 18954.0111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 19.054 | 18954.0111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 19.054 | 18954.0111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 21.6828 | 20.4408 | 20340.7754 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.3362 | 19.1087 | 19008.6707 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.3362 | 24.8457 | 24745.7459 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 33.9346 | 246.4652 | 246365.1824 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 13.8424 | 13742.3951 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 12.5488 | 12448.8081 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 11.2238 | 11123.7697 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 9.214 | 9114.0156 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 8.9442 | 8844.1547 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 11.1145 | 8.6908 | 8590.7535 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.5936 | 46.2541 | 46154.0589 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.5936 | 22.3733 | 22273.2969 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.2645 | 26.6771 | 26577.063 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 13.2645 | 41.9377 | 41837.6953 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 20.2496 | 21.1158 | 21015.8162 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 20.2496 | 21.047 | 20946.9554 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 20.2496 | 19.3567 | 19256.6585 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 20.2496 | 18.8806 | 18780.57 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 9.1679 | 20.1782 | 20078.235 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542968 [STILWEL7 345.00] CKT 1 | 27.2046 | 0.2212 | 121.2388 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 18.3444 | 18244.3842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 18.3444 | 18244.3842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 18.3444 | 18244.3842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 18.0799 | 17979.8938 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 19.1073 | 19007.3457 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 19.1073 | 19007.3457 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 19.1073 | 19007.3457 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.8864 | 20.4946 | 20394.633 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3415 | 19.1115 | 19011.51 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3415 | 24.8524 | 24752.3864 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.9449 | 246.7916 | 246691.5552 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 13.8296 | 13729.6335 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 12.5361 | 12436.1282 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 11.2126 | 11112.6238 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 9.2057 | 9105.6752 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 8.9351 | 8835.0946 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.5453 | 8.6811 | 8581.0718 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.6106 | 45.8513 | 45751.2898 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.6106 | 22.4375 | 22337.4554 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2298 | 26.8414 | 26741.3791 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2298 | 41.1811 | 41081.1131 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2391 | 21.1164 | 21016.3609 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2391 | 21.047 | 20946.9974 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2391 | 19.3568 | 19256.8081 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2391 | 18.88 | 18780.0036 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.167 | 20.1773 | 20077.325 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 27.0812 | 0.2219 | 121.8549 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 18.3047 | 18204.6892 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 18.3047 | 18204.6892 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 18.3047 | 18204.6892 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 18.0394 | 17939.416 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 19.0686 | 18968.6113 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 19.0686 | 18968.6113 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 19.0686 | 18968.6113 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 21.7339 | 20.4559 | 20355.9231 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.3466 | 19.1144 | 19014.3947 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.3466 | 24.8591 | 24759.1101 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 33.9492 | 246.8704 | 246770.3988 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 13.8112 | 13711.1816 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 12.5214 | 12421.4428 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 11.1995 | 11099.4909 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 9.1748 | 9074.8365 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 8.9061 | 8806.1012 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 12.4884 | 8.6538 | 8553.7584 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.6176 | 45.8597 | 45759.681 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.6176 | 22.4356 | 22335.6088 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.2781 | 26.7473 | 26647.3343 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 13.2781 | 41.6046 | 41504.6063 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 20.26 | 21.1196 | 21019.6371 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 20.26 | 21.054 | 20953.995 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 20.26 | 19.3603 | 19260.2549 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 20.26 | 18.8874 | 18787.3514 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 9.1707 | 20.1823 | 20082.3399 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 762279 [GEN-2017-195345.00] CKT 1 | 27.2394 | 0.2202 | 120.1658 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 18.3053 | 18205.2765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 18.3053 | 18205.2765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 18.3053 | 18205.2765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 18.0398 | 17939.8166 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 19.0707 | 18970.7385 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 19.0707 | 18970.7385 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 19.0707 | 18970.7385 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 21.4069 | 20.4607 | 20360.6755 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 13.3379 | 19.1096 | 19009.5916 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 13.3379 | 24.8479 | 24747.8896 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 33.9405 | 246.6562 | 246556.1904 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 13.8345 | 13734.512 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 12.542 | 12441.9571 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 11.2167 | 11116.6519 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 9.2052 | 9105.2104 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 8.9359 | 8835.8953 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.0745 | 8.683 | 8582.9908 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 13.6152 | 45.7977 | 45697.6525 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 13.6152 | 22.446 | 22345.9772 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.6104 | 28.5804 | 28480.3699 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 12.6104 | 35.68 | 35579.9937 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 20.251 | 21.1163 | 21016.2562 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 20.251 | 21.0478 | 20947.8261 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 20.251 | 19.3571 | 19257.0936 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 20.251 | 18.8814 | 18781.4473 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 9.1682 | 20.1784 | 20078.3523 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542966 [WGARDNR5 161.00] TO BUS 543649 [WGAR T11 13.800] CKT 11 | 27.1905 | 0.2212 | 121.2214 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 18.2952 | 18195.2418 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 18.2952 | 18195.2418 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 18.2952 | 18195.2418 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 18.0299 | 17929.8545 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 19.0604 | 18960.4181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 19.0604 | 18960.4181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 19.0604 | 18960.4181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 21.74 | 20.4496 | 20349.5814 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 13.3382 | 19.1096 | 19009.6485 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 13.3382 | 24.8481 | 24748.094 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 33.9418 | 246.753 | 246653.0472 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 13.8117 | 13711.7292 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 12.5226 | 12422.5654 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 11.2001 | 11100.1103 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 9.1727 | 9072.7014 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 8.9045 | 8804.5208 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 12.4697 | 8.6527 | 8552.671 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 13.6146 | 45.7968 | 45696.7958 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 13.6146 | 22.4462 | 22346.1916 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 5.8303 | 19.0494 | 18949.4485 | 73.77 | 170.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 5.8303 | 13.9153 | 13815.2625 | 76.23 | 181.05 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 20.2424 | 21.1159 | 21015.8761 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 20.2424 | 21.0468 | 2094682% | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 20.2424 | 19.3566 | 19256.6123 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 20.2424 | 18.8803 | 1878027% | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 9.1665 | 20.178 | 20077.9793 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543077 [PLSTVAL5 161.00] CKT 1 | 27.2097 | 0.2211 | 121.0952 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 18.3552 | 18255.2274 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 18.3552 | 18255.2274 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 18.3552 | 18255.2274 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 18.0906 | 17990.6391 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 19.1205 | 19020.5452 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 19.1205 | 19020.5452 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 19.1205 | 19020.5452 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.027 | 20.5123 | 20412.2655 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3448 | 19.1135 | 19013.4608 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3448 | 24.8568 | 24756.7878 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.9445 | 246.871 | 246771.0144 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 13.7802 | 13680.1803 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 12.4951 | 12395.1206 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 11.1776 | 11077.6283 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 9.1294 | 9029.3974 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 8.8621 | 8762.1433 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.2846 | 8.6112 | 8511.1826 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.5861 | 46.3909 | 46290.8968 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.5861 | 22.3519 | 22251.9201 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2388 | 26.863 | 26762.9643 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.2388 | 41.0802 | 40980.1759 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2329 | 21.1145 | 21014.4662 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2329 | 21.0436 | 20943.5902 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2329 | 19.355 | 19255.0269 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.2329 | 18.8767 | 18776.7273 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.1663 | 20.1759 | 20075.8744 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 27.005 | 0.2231 | 123.0532 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 18.2931 | 18193.0635 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 18.2931 | 18193.0635 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 18.2931 | 18193.0635 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 18.0277 | 17927.7093 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 19.0582 | 18958.1825 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 19.0582 | 18958.1825 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 19.0582 | 18958.1825 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 21.7372 | 20.4472 | 20347.1959 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.3377 | 19.1094 | 19009.3563 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.3377 | 24.8474 | 24747.4128 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 33.9404 | 246.7225 | 246622.458 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 13.8094 | 13709.393 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 12.521 | 12421.0152 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 11.1989 | 11098.9471 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 9.1669 | 9066.8979 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 8.8991 | 8799.1424 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 12.3699 | 8.6477 | 8547.6775 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.6131 | 45.8215 | 45721.503 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.6131 | 22.4422 | 22342.2165 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.2746 | 26.6918 | 26591.8031 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 13.2746 | 41.8643 | 41764.2737 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 20.2504 | 21.1157 | 21015.6797 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 20.2504 | 21.0468 | 20946.8396 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 20.2504 | 19.3566 | 19256.5754 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 20.2504 | 18.8805 | 18780.5388 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 9.168 | 20.178 | 20078.0098 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543641 [CRAI T11 13.800] CKT 11 | 27.2081 | 0.2212 | 121.1505 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 18.2931 | 18193.1155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 18.2931 | 18193.1155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 18.2931 | 18193.1155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 18.0278 | 17927.7594 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 19.0582 | 18958.2368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 19.0582 | 18958.2368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 19.0582 | 18958.2368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 21.7373 | 20.4473 | 20347.2571 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.3377 | 19.1094 | 19009.357 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.3377 | 24.8474 | 24747.4141 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 33.9404 | 246.7235 | 246623.5332 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 13.8096 | 13709.6373 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 12.5212 | 12421.2154 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 11.1991 | 11099.1101 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 9.1673 | 9067.2995 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 8.8995 | 8799.5266 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 12.3716 | 8.648 | 8548.0458 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.6131 | 45.8212 | 45721.2217 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.6131 | 22.4423 | 22342.2606 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.2747 | 26.6916 | 26591.5743 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 13.2747 | 41.8654 | 41765.3675 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 20.2504 | 21.1157 | 21015.6804 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 20.2504 | 21.0468 | 20946.8391 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 20.2504 | 19.3566 | 19256.576 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 20.2504 | 18.8805 | 18780.5396 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 9.168 | 20.178 | 20078.0096 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543642 [CRAI T22 13.800] CKT 22 | 27.2081 | 0.2212 | 121.1501 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 18.2943 | 18194.2676 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 18.2943 | 18194.2676 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 18.2943 | 18194.2676 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 18.0289 | 17928.8862 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 19.0595 | 18959.469 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 19.0595 | 18959.469 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 19.0595 | 18959.469 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 21.739 | 20.4486 | 20348.6492 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.3378 | 19.1094 | 19009.3871 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.3378 | 24.8475 | 24747.4845 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 33.9411 | 246.7363 | 246636.3221 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 13.8205 | 13720.489 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 12.5303 | 12430.2972 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 11.2066 | 11106.5806 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 9.184 | 9083.9548 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 8.9156 | 8815.5779 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 12.4038 | 8.6635 | 8563.5367 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.6127 | 45.8143 | 45714.3184 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.6127 | 22.4434 | 22343.4487 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.2764 | 26.6819 | 26581.889 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 13.2764 | 41.9114 | 41811.3648 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 20.2504 | 21.1157 | 21015.6962 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 20.2504 | 21.0469 | 20946.8685 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 20.2504 | 19.3566 | 19256.5913 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 20.2504 | 18.8806 | 18780.5668 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 9.168 | 20.178 | 20077.99 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542978 [CRAIG 5 161.00] TO BUS 543643 [CRAI T33 13.800] CKT 33 | 27.2084 | 0.2211 | 121.1415 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 18.2851 | 18185.1041 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 18.2851 | 18185.1041 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 18.2851 | 18185.1041 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 18.0196 | 17919.6281 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 19.0518 | 18951.7981 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 19.0518 | 18951.7981 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 19.0518 | 18951.7981 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.7251 | 20.4433 | 20343.2704 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.3369 | 19.109 | 19009.0474 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.3369 | 24.8467 | 24746.7018 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 33.9401 | 246.7359 | 246635.9429 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 13.8104 | 13710.4308 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 12.5215 | 12421.5461 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 11.1992 | 11099.1941 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 9.1705 | 9070.4734 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 8.9024 | 8802.4334 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.5039 | 8.6507 | 8550.712 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.6141 | 45.7959 | 45695.9135 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.6141 | 22.4464 | 22346.3614 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.278 | 26.6655 | 26565.4785 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.278 | 41.9911 | 41891.1447 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 20.2488 | 21.1152 | 21015.2462 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 20.2488 | 21.0461 | 20946.0869 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 20.2488 | 19.3562 | 19256.1789 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 20.2488 | 18.8798 | 18779.8328 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 9.1674 | 20.1775 | 20077.4743 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 27.2032 | 0.2212 | 121.2475 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 18.2949 | 18194.9051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 18.2949 | 18194.9051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 18.2949 | 18194.9051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 18.0295 | 17929.5171 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 19.0601 | 18960.0881 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 19.0601 | 18960.0881 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 19.0601 | 18960.0881 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.7434 | 20.4493 | 20349.2511 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.3379 | 19.1095 | 19009.4761 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.3379 | 24.8477 | 24747.6976 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 33.9415 | 246.7523 | 246652.2704 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3239 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4272 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 11.1991 | 11099.093 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4644 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4075 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.5059 | 8.6507 | 8550.6716 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.6149 | 45.7967 | 45696.6928 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1892 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.2782 | 26.6674 | 26567.4403 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3427 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 20.2503 | 21.1157 | 21015.6711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 20.2503 | 21.0468 | 20946.8217 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 20.2503 | 19.3566 | 19256.5677 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 20.2503 | 18.8805 | 18780.5204 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 9.168 | 20.178 | 20077.973 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 27.2092 | 0.2211 | 121.1209 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18194.996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18194.996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18194.996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 18.0296 | 17929.6061 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.7433 | 20.4494 | 20349.3599 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.3379 | 19.1095 | 19009.4762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.3379 | 24.8477 | 24747.6977 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 33.9415 | 246.7522 | 246652.2474 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 13.8103 | 13710.3418 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 12.5214 | 12421.4415 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 11.1991 | 11099.1053 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 9.1705 | 9070.4897 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 8.9024 | 8802.4328 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.5059 | 8.6507 | 8550.696 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.6149 | 45.7967 | 45696.6961 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.6149 | 22.4462 | 22346.1882 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.2782 | 26.6674 | 26567.4435 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.2782 | 41.9813 | 41881.3274 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 20.2503 | 21.1157 | 21015.6747 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 20.2503 | 21.0468 | 20946.8279 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 20.2503 | 19.3566 | 19256.5708 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 20.2503 | 18.8805 | 18780.5259 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 9.168 | 20.178 | 20077.9741 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 27.2092 | 0.2211 | 121.1205 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 18.0296 | 17929.6219 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.199 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.199 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 19.0602 | 18960.199 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.7433 | 20.4494 | 20349.3726 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.3379 | 19.1095 | 19009.4767 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.3379 | 24.8477 | 24747.6989 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 33.9415 | 246.7522 | 246652.2293 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 13.8103 | 13710.3419 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 12.5214 | 12421.4423 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 11.1991 | 11099.1055 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 9.1705 | 9070.4907 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 8.9024 | 8802.4337 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.5059 | 8.6507 | 8550.6968 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.6149 | 45.7967 | 45696.6966 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.6149 | 22.4462 | 22346.188 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.2782 | 26.6675 | 2656745% | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.2782 | 41.9813 | 41881.3104 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 20.2503 | 21.1157 | 2101568% | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 20.2503 | 21.0468 | 20946.8289 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 20.2503 | 19.3566 | 19256.5713 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 20.2503 | 18.8805 | 18780.528 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 18.2906 | 18190.5567 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 18.2906 | 18190.5567 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 18.2906 | 18190.5567 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 18.0252 | 17925.153 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 19.0563 | 18956.2502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 19.0563 | 18956.2502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 19.0563 | 18956.2502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.7377 | 20.4462 | 20346.1683 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.3376 | 19.1093 | 19009.318 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.3376 | 24.8473 | 24747.3297 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 33.9409 | 246.7455 | 246645.4732 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 13.8102 | 13710.2266 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 12.5214 | 12421.3551 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 11.199 | 11099.0349 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 9.1703 | 9070.2631 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 8.9022 | 8802.2195 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.5051 | 8.6505 | 8550.4955 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.6145 | 45.7964 | 45696.3529 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.6145 | 22.4463 | 22346.2595 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.2781 | 26.6667 | 26566.6604 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.2781 | 41.9852 | 41885.2068 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 20.2497 | 21.1155 | 21015.4887 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 20.2497 | 21.0465 | 20946.506 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 20.2497 | 19.3564 | 19256.4002 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 20.2497 | 18.8802 | 18780.2253 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 9.1678 | 20.1778 | 20077.7811 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 27.2069 | 0.2212 | 121.1703 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 18.2948 | 18194.7634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 18.2948 | 18194.7634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 18.2948 | 18194.7634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 18.0294 | 17929.374 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 19.06 | 18959.9647 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 19.06 | 18959.9647 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 19.06 | 18959.9647 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 21.7428 | 20.4492 | 20349.1577 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.3376 | 19.1093 | 19009.3399 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.3376 | 24.8474 | 24747.3815 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 33.9411 | 246.7465 | 246646.5474 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 13.8103 | 13710.2555 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 12.5214 | 12421.3838 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 11.1991 | 11099.0588 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 9.1703 | 9070.2845 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 8.9022 | 8802.2427 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 12.5053 | 8.6505 | 8550.5202 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.6148 | 45.7963 | 45696.263 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.6148 | 22.4463 | 22346.2748 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.2767 | 26.4799 | 26379.8802 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 13.2767 | 42.957 | 42856.9776 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 20.2499 | 21.1155 | 21015.5289 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 20.2499 | 21.0466 | 20946.564 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 20.2499 | 19.3564 | 19256.4355 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 20.2499 | 18.8803 | 18780.2734 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 9.1679 | 20.1778 | 20077.8183 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543030 [PLSTVAL1 34.500] TO BUS 543077 [PLSTVAL5 161.00] TO BUS 543115 [PLSTVL2_TER17.6210] CKT 2 | 27.2081 | 0.2211 | 121.1473 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 18.2942 | 18194.2361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 18.2942 | 18194.2361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 18.2942 | 18194.2361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 18.0289 | 17928.8636 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 19.0594 | 18959.3716 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 19.0594 | 18959.3716 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 19.0594 | 18959.3716 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 21.7371 | 20.4484 | 20348.4417 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 13.3372 | 19.1091 | 19009.0641 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 13.3372 | 24.8467 | 24746.7411 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 33.9404 | 246.7263 | 246626.3395 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 13.8105 | 13710.4515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 12.5216 | 12421.5568 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 11.1992 | 11099.2278 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 9.1705 | 9070.5033 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 8.9025 | 8802.4527 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 12.4676 | 8.6507 | 8550.7214 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 13.615 | 45.8071 | 45707.1008 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 13.615 | 22.4445 | 22344.4596 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 7.6386 | 35.1975 | 35097.482 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 7.6386 | 29.1954 | 29095.4373 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 20.2476 | 21.1187 | 21018.7424 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 20.2476 | 21.0516 | 20951.5913 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 20.2476 | 19.3591 | 19259.1358 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 20.2476 | 18.8846 | 18784.5759 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 9.1677 | 20.1804 | 20080.4434 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543066 [S.OTTWA5 161.00] CKT 1 | 27.2067 | 0.2212 | 121.1877 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 18.295 | 18194.9979 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 18.295 | 18194.9979 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 18.295 | 18194.9979 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 18.0296 | 17929.6086 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1846 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1846 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1846 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 21.7433 | 20.4494 | 20349.3578 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.699 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 33.9415 | 246.7522 | 246652.2315 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3351 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4362 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1007 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4795 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4223 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6859 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.6149 | 45.7966 | 45696.6354 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.6149 | 22.4462 | 22346.1984 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.2792 | 26.6577 | 26557.7249 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 13.2792 | 42.0264 | 41926.4026 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 20.2503 | 21.1157 | 21015.6745 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 20.2503 | 21.0468 | 20946.8278 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 20.2503 | 19.3566 | 19256.5697 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 20.2503 | 18.8805 | 18780.5259 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 9.168 | 20.178 | 20077.9735 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 543166 [NEASTOTTW5 161.00] CKT 1 | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 18.2948 | 18194.842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 18.2948 | 18194.842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 18.2948 | 18194.842 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 18.0295 | 17929.452 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 19.06 | 18960.0427 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 19.06 | 18960.0427 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 19.06 | 18960.0427 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 21.7451 | 20.4492 | 20349.2344 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.3388 | 19.11 | 19009.9697 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.3388 | 24.8488 | 24748.8471 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 33.9423 | 246.7736 | 246673.5732 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 13.8098 | 13709.8385 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 12.521 | 12421.0256 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 11.1988 | 11098.7586 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 9.1697 | 9069.6985 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 8.9017 | 8801.674 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 12.508 | 8.65 | 8549.9672 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.6155 | 45.7947 | 45694.726 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.6155 | 22.4465 | 22346.4703 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.2901 | 26.574 | 26474.0381 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 13.2901 | 42.4196 | 42319.5847 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 20.2517 | 21.1161 | 21016.1354 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 20.2517 | 21.0477 | 20947.6948 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 20.2517 | 19.357 | 19257.0111 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 20.2517 | 18.8814 | 18781.3742 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 9.1684 | 20.1785 | 20078.5164 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 762405 [ASG-2018-010161.00] CKT 1 | 27.2123 | 0.221 | 121.0237 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 18.2951 | 18195.0693 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 18.2951 | 18195.0693 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 18.2951 | 18195.0693 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 18.0297 | 17929.678 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 19.0603 | 18960.2641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 19.0603 | 18960.2641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 19.0603 | 18960.2641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 21.7432 | 20.4495 | 20349.4509 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5386 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.338 | 24.8478 | 24747.8437 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 33.9416 | 246.7545 | 246654.525 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 13.8103 | 13710.2681 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3797 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 11.1991 | 11099.0539 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.3818 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.3284 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.5947 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.6145 | 45.7988 | 45698.7506 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.6145 | 22.4459 | 22345.8643 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.2776 | 26.6691 | 26569.146 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 13.2776 | 41.9731 | 41873.0696 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 19.3581 | 21.1593 | 21059.3237 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 19.3581 | 21.1111 | 21011.1365 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 19.3581 | 19.3774 | 19277.3966 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 19.3581 | 18.9131 | 18813.0868 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 9.0132 | 20.2973 | 20197.258 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547469 [RIV4525 161.00] CKT 1 | 27.2086 | 0.2211 | 121.1259 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9621 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9621 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9621 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 18.0296 | 17929.5748 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1405 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1405 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1405 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.743 | 20.4493 | 20349.2986 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.3382 | 19.1096 | 19009.645 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.3382 | 24.8481 | 24748.0817 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 33.9416 | 246.7557 | 246655.6562 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 13.8101 | 13710.0907 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 12.5212 | 12421.2289 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 11.1989 | 11098.9297 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 9.1701 | 9070.1218 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 8.9021 | 8802.0767 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5055 | 8.6504 | 8550.3508 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.6125 | 45.8292 | 45729.2251 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.6125 | 22.441 | 22340.9524 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.2781 | 26.6675 | 26567.5236 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.2781 | 41.9809 | 41880.9432 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.1287 | 21.1398 | 21039.79 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.1287 | 21.0773 | 20977.3404 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.1287 | 19.3737 | 19273.7004 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.1287 | 18.9007 | 18800.7265 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 8.5856 | 20.3811 | 20281.0723 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 27.2016 | 0.2213 | 121.2611 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 18.2957 | 18195.6603 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 18.2957 | 18195.6603 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 18.2957 | 18195.6603 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 18.0303 | 17930.2653 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 19.0608 | 18960.8372 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 19.0608 | 18960.8372 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 19.0608 | 18960.8372 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 21.7375 | 20.45 | 20350.0115 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.5 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.7386 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 33.9415 | 246.7487 | 246648.7096 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 13.8104 | 13710.395 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 12.5215 | 12421.4858 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 11.1991 | 11099.1421 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 9.1706 | 9070.5761 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 8.9025 | 8802.5145 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 12.5054 | 8.6508 | 855077% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.6149 | 45.7968 | 45696.8147 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.6149 | 22.4462 | 2234617% | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.2779 | 26.6677 | 26567.6502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 13.2779 | 41.9804 | 41880.4086 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 17.945 | 21.5942 | 21494.2265 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 17.945 | 21.6992 | 21599.1629 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 17.945 | 19.696 | 19596.0012 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 17.945 | 19.3274 | 19227.4403 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 9.1478 | 20.1953 | 20095.3433 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547498 [STL439 5 161.00] CKT 1 | 27.1995 | 0.2211 | 121.0758 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 18.0306 | 17930.6094 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0492 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0492 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0492 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 21.7308 | 20.45 | 20350.0309 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.3381 | 19.1096 | 19009.5915 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.3381 | 24.848 | 24747.9632 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 33.9414 | 246.7411 | 246641.115 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 13.8112 | 13711.1647 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 12.5221 | 12422.1345 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 11.1997 | 11099.6781 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 9.1717 | 9071.732 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 8.9036 | 8803.6314 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 12.5056 | 8.6519 | 8551.854 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.6161 | 45.805 | 45704.9755 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.6161 | 22.4447 | 22344.6965 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.2768 | 26.672 | 26571.9657 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 13.2768 | 41.9596 | 41859.5763 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 18.317 | 21.9195 | 21819.528 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 18.317 | 22.1134 | 22013.3776 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 18.317 | 19.9523 | 19852.3296 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 18.317 | 19.6307 | 19530.7041 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 9.0445 | 20.2953 | 20195.3399 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547503 [RIV452T 5 161.00] CKT 1 | 27.175 | 0.2213 | 121.3269 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 18.2954 | 18195.4339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 18.2954 | 18195.4339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 18.2954 | 18195.4339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 18.03 | 17930.034 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 19.0607 | 18960.6526 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 19.0607 | 18960.6526 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 19.0607 | 18960.6526 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 21.7412 | 20.4499 | 20349.8904 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.3362 | 19.1085 | 19008.4832 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.3362 | 24.8454 | 24745.3992 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 33.9407 | 246.7302 | 246630.191 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 13.8105 | 13710.496 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 12.5216 | 12421.5726 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 11.1992 | 11099.2131 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 9.1707 | 9070.7211 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 8.9027 | 8802.6554 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 12.5057 | 8.6509 | 8550.9119 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.6144 | 45.7982 | 45698.2018 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.6144 | 22.446 | 22345.9782 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.2777 | 26.6679 | 26567.9018 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 13.2777 | 41.9793 | 41879.2702 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 19.1487 | 21.1955 | 21095.4676 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 19.1487 | 21.1609 | 21060.8951 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 19.1487 | 19.4046 | 19304.5924 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 19.1487 | 18.9497 | 18849.6849 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 9.1228 | 20.1882 | 20088.1706 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547729 [BAX488 5 161.00] CKT 1 | 27.2055 | 0.2211 | 121.1103 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 18.295 | 18194.952 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 18.295 | 18194.952 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 18.295 | 18194.952 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 18.0296 | 17929.5629 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 19.0601 | 18960.1378 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 19.0601 | 18960.1378 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 19.0601 | 18960.1378 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 21.7431 | 20.4493 | 20349.3085 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.3379 | 19.1095 | 19009.45 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.3379 | 24.8476 | 24747.6348 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 33.9415 | 246.7513 | 246651.3284 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 13.8103 | 13710.3033 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 12.5214 | 12421.4096 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 11.1991 | 11099.0785 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 9.1704 | 9070.4341 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 8.9024 | 8802.3782 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 12.5059 | 8.6506 | 8550.6431 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.615 | 45.7968 | 45696.8127 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.615 | 22.4462 | 22346.1619 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.2782 | 26.6674 | 26567.3953 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 13.2782 | 41.9815 | 41881.5495 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 20.1115 | 21.0459 | 20945.9276 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 20.1115 | 20.9538 | 20853.7835 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 20.1115 | 19.2989 | 19198.9147 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 20.1115 | 18.8058 | 18705.7963 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 9.1638 | 20.1863 | 20086.3265 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 547541 [RIV167 2 69.000] TO BUS 547725 [RIV452 1 12.500] CKT 1 | 27.2086 | 0.2211 | 121.1387 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 18.295 | 18194.9883 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 18.295 | 18194.9883 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 18.295 | 18194.9883 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 18.0296 | 17929.5982 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1725 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1725 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1725 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 21.7431 | 20.4493 | 20349.3431 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5365 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.8361 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 33.9415 | 246.7527 | 246652.7243 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 13.8103 | 13710.2674 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3791 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 11.1991 | 11099.054 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.3813 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.3271 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.5936 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.6139 | 45.8066 | 45706.5862 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.6139 | 22.4446 | 22344.5951 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.2781 | 26.6675 | 26567.4595 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 13.2781 | 41.9812 | 41881.237 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.0892 | 21.1535 | 21053.4882 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.0892 | 21.0965 | 20996.4864 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.0892 | 19.3839 | 19283.8703 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 20.0892 | 18.9148 | 18814.7617 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 8.8489 | 20.3703 | 20270.3072 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547480 [MON383 5 161.00] CKT 1 | 27.2073 | 0.2212 | 121.1588 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 18.2951 | 18195.0817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 18.2951 | 18195.0817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 18.2951 | 18195.0817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 18.0297 | 17929.6902 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 19.0603 | 18960.2715 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 19.0603 | 18960.2715 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 19.0603 | 18960.2715 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 21.7433 | 20.4495 | 20349.4509 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.338 | 19.1095 | 19009.4856 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.338 | 24.8477 | 24747.7203 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 33.9415 | 246.7517 | 246651.6898 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 13.8104 | 13710.3639 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 12.5215 | 12421.4606 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 11.1991 | 11099.1212 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 9.1705 | 9070.5245 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 8.9025 | 8802.4656 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 12.5059 | 8.6507 | 8550.7284 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.6152 | 45.799 | 45699.039 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.6152 | 22.4458 | 22345.7668 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.2782 | 26.6675 | 26567.4616 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 13.2782 | 41.9812 | 41881.2378 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 20.2499 | 21.1203 | 21020.3344 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 20.2499 | 21.0546 | 20954.6063 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 20.2499 | 19.3606 | 19260.6319 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 20.2499 | 18.8875 | 18787.4859 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 9.0702 | 20.1586 | 20058.6452 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547591 [MON383 2 69.000] TO BUS 547712 [MON383 1 12.500] CKT 1 | 27.2089 | 0.2211 | 121.1119 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 18.0296 | 17929.555 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 21.743 | 20.4493 | 20349.2546 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.3383 | 19.1097 | 19009.6762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.3383 | 24.8482 | 24748.1816 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 33.9416 | 246.755 | 246655.0104 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 13.8108 | 13710.8435 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 12.5219 | 12421.8672 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 11.1995 | 11099.4568 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 9.1712 | 9071.232 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 8.9032 | 8803.1502 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 12.5066 | 8.6514 | 8551.3915 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.6162 | 45.798 | 45698.025 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.6162 | 22.4459 | 22345.8676 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.2783 | 26.6678 | 26567.7526 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 13.2783 | 41.9798 | 41879.8227 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 20.2535 | 21.1284 | 21028.3644 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 20.2535 | 21.0639 | 20963.8511 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 20.2535 | 19.3664 | 19266.3819 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 20.2535 | 18.8933 | 18793.2884 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 9.1893 | 20.4454 | 20345.3766 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 588981 [G17-060XFMR134.500] CKT 1 | 27.203 | 0.2213 | 121.3247 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 18.2951 | 18195.0767 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 18.2951 | 18195.0767 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 18.2951 | 18195.0767 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 18.0297 | 17929.6898 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 19.0602 | 18960.2392 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 19.0602 | 18960.2392 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 19.0602 | 18960.2392 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 21.7411 | 20.4494 | 20349.373 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.3377 | 19.1094 | 19009.364 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.3377 | 24.8474 | 24747.4371 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 33.9413 | 246.748 | 246648.0019 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 13.8104 | 13710.4216 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 12.5215 | 12421.5101 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 11.1992 | 11099.1618 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 9.1706 | 9070.6082 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 8.9025 | 8802.5468 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 12.506 | 8.6508 | 8550.8066 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.0213 | 55.2562 | 55156.1574 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.0213 | 21.3737 | 21273.7029 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.2779 | 26.6682 | 26568.1512 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 13.2779 | 41.9779 | 41877.9074 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 20.249 | 21.1158 | 21015.7968 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 20.249 | 21.0469 | 20946.912 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 20.249 | 19.3566 | 19256.6369 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 20.249 | 18.8805 | 18780.5237 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 9.1668 | 20.1782 | 20078.1815 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300124 [5HOLDENB2 161.00] CKT 1 | 27.204 | 0.2212 | 121.1771 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9873 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9873 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9873 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.598 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7432 | 20.4493 | 20349.3447 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4594 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.6592 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 33.9414 | 246.7514 | 246651.3742 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 13.8103 | 13710.3279 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 12.5214 | 12421.4308 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 11.1991 | 1109910% | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 9.1705 | 9070.467 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 8.9024 | 880241% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5058 | 8.6507 | 8550.6752 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.5888 | 44.9344 | 44834.378 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.5888 | 22.5984 | 22498.3747 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.2781 | 26.6673 | 26567.3359 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.2781 | 41.9819 | 41881.8801 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.2504 | 21.1157 | 21015.6783 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.2504 | 21.0468 | 20946.8467 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.2504 | 19.3566 | 19256.5773 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.2504 | 18.8805 | 18780.5497 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 9.1681 | 20.1781 | 20078.0526 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 27.209 | 0.2211 | 121.1228 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 18.295 | 18194.9872 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 18.295 | 18194.9872 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 18.295 | 18194.9872 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 18.0296 | 17929.598 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 19.0602 | 18960.1736 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 21.7432 | 20.4493 | 20349.3447 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.3379 | 19.1095 | 19009.4594 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.3379 | 24.8477 | 24747.6591 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 33.9414 | 246.7514 | 246651.3777 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 13.8103 | 13710.3279 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 12.5214 | 12421.4308 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 11.1991 | 11099.0964 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 9.1705 | 9070.467 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 8.9024 | 8802.4111 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 12.5058 | 8.6507 | 8550.6752 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.5887 | 44.9344 | 44834.3645 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.5887 | 22.5984 | 22498.3862 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.2781 | 26.6673 | 26567.3359 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 13.2781 | 41.9819 | 41881.8801 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 20.2504 | 21.1157 | 21015.6781 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 20.2504 | 21.0468 | 20946.8464 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 20.2504 | 19.3566 | 19256.5772 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 20.2504 | 18.8805 | 18780.5494 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 9.1681 | 20.1781 | 20078.0529 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 3 | 27.209 | 0.2211 | 121.1228 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 18.2953 | 18195.2617 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 18.2953 | 18195.2617 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 18.2953 | 18195.2617 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 18.0299 | 17929.867 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 19.0605 | 18960.4575 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 19.0605 | 18960.4575 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 19.0605 | 18960.4575 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 21.7418 | 20.4497 | 20349.6539 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.337 | 19.109 | 19008.99 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.337 | 24.8466 | 24746.5727 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 33.9404 | 246.7354 | 246635.4413 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 13.8113 | 13711.3386 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 12.5223 | 12422.2739 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 11.1998 | 11099.7968 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 9.172 | 9072.0236 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 8.9039 | 8803.9072 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 12.5026 | 8.6521 | 8552.1161 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.1774 | 50.4267 | 50326.7285 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.1774 | 21.8412 | 21741.1632 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.2781 | 26.6701 | 26570.0746 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 13.2781 | 41.9688 | 41868.8107 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 20.242 | 21.117 | 21017.0472 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 20.242 | 21.0482 | 20948.2301 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 20.242 | 19.3575 | 19257.4686 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 20.242 | 18.8812 | 18781.2113 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 9.1579 | 20.1824 | 20082.3599 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 301477 [5OSCEOKCTP 161.00] CKT 1 | 27.1816 | 0.2214 | 121.4461 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 18.2961 | 18196.13 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 18.2961 | 18196.13 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 18.2961 | 18196.13 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 18.0307 | 17930.7424 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 19.0612 | 18961.2241 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 19.0612 | 18961.2241 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 19.0612 | 18961.2241 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 21.7303 | 20.4503 | 20350.2704 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.3377 | 19.1094 | 19009.3719 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.3377 | 24.8474 | 24747.4497 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 33.9409 | 246.7428 | 246642.8088 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 13.8109 | 13710.8757 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 12.5219 | 12421.8549 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 11.1995 | 11099.4551 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 9.1715 | 9071.4674 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 8.9034 | 8803.3523 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 12.4962 | 8.6516 | 8551.5624 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.0961 | 55.2132 | 55113.2064 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.0961 | 21.37 | 21269.9679 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.2756 | 26.676 | 26576.0113 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 13.2756 | 41.9401 | 41840.0873 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 20.249 | 21.1155 | 21015.4552 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 20.249 | 21.0464 | 20946.4033 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 20.249 | 19.3564 | 19256.3572 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 20.249 | 18.8801 | 18780.1044 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 9.1673 | 20.1774 | 20077.3782 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 505502 [TRUMAN 5 161.00] CKT 1 | 27.2054 | 0.2212 | 121.1856 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 18.2948 | 18194.7829 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 18.2948 | 18194.7829 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 18.2948 | 18194.7829 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 18.0294 | 17929.3979 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 19.06 | 18959.9546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 19.06 | 18959.9546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 19.06 | 18959.9546 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 21.7429 | 20.4491 | 20349.097 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.338 | 19.1095 | 19009.5287 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.338 | 24.8478 | 24747.8193 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 33.9414 | 246.7536 | 246653.5952 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 13.81 | 13709.9652 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 12.5211 | 12421.1238 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 11.1988 | 11098.8428 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 9.1699 | 9069.9282 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 8.9019 | 8801.8898 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 12.5055 | 8.6502 | 8550.171 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.5384 | 44.1589 | 44058.8817 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.5384 | 22.7478 | 22647.8232 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.2778 | 26.6669 | 26566.9312 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 13.2778 | 41.9838 | 41883.7912 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 20.2499 | 21.1156 | 21015.6051 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 20.2499 | 21.0467 | 20946.6788 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 20.2499 | 19.3565 | 19256.5002 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 20.2499 | 18.8804 | 18780.3733 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 9.1677 | 20.1777 | 20077.7029 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541242 [CLINTON5 161.00] CKT Z1 | 27.2076 | 0.2212 | 121.164 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 18.297 | 18197.0058 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 18.297 | 18197.0058 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 18.297 | 18197.0058 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 18.0316 | 17931.6199 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 19.0621 | 18962.0724 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 19.0621 | 18962.0724 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 19.0621 | 18962.0724 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 21.6873 | 20.4511 | 20351.0975 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 13.3368 | 19.1088 | 19008.8249 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 13.3368 | 24.8462 | 24746.1699 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 33.9396 | 246.7013 | 246601.2541 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 13.8118 | 13711.782 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 12.5226 | 12422.6026 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 11.2001 | 11100.1021 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 9.1729 | 9072.873 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 8.9047 | 8804.6917 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.4635 | 8.6528 | 8552.8409 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.2174 | 55.5515 | 55451.4587 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 12.2174 | 18.2559 | 18155.9447 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 13.266 | 26.6868 | 26586.8265 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 13.266 | 41.8911 | 41791.1004 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 20.2479 | 21.1148 | 21014.8143 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 20.2479 | 21.0452 | 20945.2169 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 20.2479 | 19.3557 | 19255.7479 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 20.2479 | 18.879 | 18778.951 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 9.1667 | 20.178 | 20077.9737 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 761278 [G17-108-TAP 161.00] CKT 1 | 27.1971 | 0.2215 | 121.5089 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 18.2946 | 18194.6324 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 18.2946 | 18194.6324 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 18.2946 | 18194.6324 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 18.0293 | 17929.251 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 19.0598 | 18959.7999 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 19.0598 | 18959.7999 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 19.0598 | 18959.7999 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7374 | 20.4489 | 20348.9313 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.3384 | 19.1098 | 19009.7513 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.3384 | 24.8483 | 24748.3198 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 33.9411 | 246.7472 | 246647.153 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 13.8093 | 13709.3039 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 12.5206 | 12420.5647 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 11.1984 | 11098.3815 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 9.1689 | 9068.9439 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 8.9009 | 8800.9377 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5022 | 8.6492 | 8549.2488 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 8.1685 | 34.9628 | 34862.7669 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 8.1685 | 17.1701 | 17070.0544 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.2773 | 26.6671 | 26567.1424 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.2773 | 41.9829 | 41882.9338 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2487 | 21.1155 | 21015.4927 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2487 | 21.0464 | 20946.432 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2487 | 19.3564 | 19256.3759 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2487 | 18.8801 | 18780.1066 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 9.1667 | 20.1772 | 20077.249 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 27.2061 | 0.2211 | 121.1081 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.1313 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.1313 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.1313 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 18.0297 | 17929.7435 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2933 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2933 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2933 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 21.7429 | 20.4494 | 20349.4262 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.3385 | 19.1097 | 19009.7471 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.3385 | 24.8483 | 24748.33 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 33.9419 | 246.7586 | 246658.6327 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 13.8102 | 13710.1775 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 12.5213 | 12421.2962 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 11.199 | 11098.9864 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 9.1703 | 9070.2821 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 8.9022 | 8802.2271 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 12.5054 | 8.6505 | 8550.493 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.613 | 49.6094 | 49509.4126 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.613 | 21.9067 | 21806.6882 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.2778 | 26.6687 | 26568.6504 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 13.2778 | 41.9754 | 41875.4126 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 20.2509 | 21.1159 | 21015.8665 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 20.2509 | 21.0472 | 20947.1674 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 20.2509 | 19.3567 | 19256.748 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 20.2509 | 18.8808 | 18780.8461 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 9.1682 | 20.1782 | 20078.2366 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 99911 [GI91POI 69.000] CKT 1 | 27.2101 | 0.2211 | 121.0953 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9962 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9962 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9962 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.607 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1828 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1828 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1828 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 21.7432 | 20.4494 | 20349.3543 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.338 | 19.1095 | 19009.4838 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.338 | 24.8477 | 24747.7144 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 33.9415 | 246.7522 | 24665225% | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3266 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 12.5214 | 1242143% | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.0949 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4687 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4119 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6755 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.6025 | 45.7947 | 45694.6706 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.6025 | 22.4471 | 22347.0531 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.2782 | 26.6674 | 26567.4301 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 13.2782 | 41.9814 | 41881.3767 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 20.2503 | 21.1157 | 21015.6698 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 20.2503 | 21.0468 | 20946.8193 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 20.2503 | 19.3566 | 19256.5657 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 20.2503 | 18.8805 | 18780.5181 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 9.168 | 20.178 | 20077.9532 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300530 [2GEOGT2 69.000] CKT 1 | 27.2091 | 0.2211 | 121.12 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9788 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9788 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9788 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.5899 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1637 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1637 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1637 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 21.7432 | 20.4493 | 20349.3323 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4698 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.6857 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 33.9415 | 246.7523 | 246652.308 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3411 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4419 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1058 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4885 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4319 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6953 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.5811 | 46.1851 | 46085.1399 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.5811 | 22.385 | 22284.9691 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.2783 | 26.6674 | 26567.4197 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 13.2783 | 41.9814 | 41881.4446 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 20.2502 | 21.1157 | 21015.6525 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 20.2502 | 21.0468 | 20946.779 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 20.2502 | 19.3565 | 19256.546 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 20.2502 | 18.8805 | 18780.4753 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 9.1679 | 20.1779 | 20077.8909 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300534 [2LINCLN 69.000] CKT 1 | 27.2087 | 0.2211 | 121.1314 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.0753 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.0753 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 18.2951 | 18195.0753 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 18.0297 | 17929.6833 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2669 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2669 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 19.0603 | 18960.2669 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 21.7429 | 20.4494 | 20349.4496 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.3379 | 19.1094 | 19009.4435 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.3379 | 24.8476 | 24747.6211 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 33.9413 | 246.7496 | 246649.5897 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 13.8105 | 13710.4973 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 12.5216 | 12421.5733 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 11.1992 | 11099.2147 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 9.1707 | 9070.7234 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 8.9027 | 8802.6583 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 12.5056 | 8.6509 | 8550.9138 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.5154 | 45.8517 | 45751.6981 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.5154 | 22.446 | 22345.9651 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.2784 | 26.6676 | 26567.5768 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 13.2784 | 41.9807 | 41880.7144 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 20.25 | 21.1156 | 21015.6208 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 20.25 | 21.0467 | 20946.7278 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 20.25 | 19.3565 | 19256.5196 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 20.25 | 18.8804 | 18780.4299 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 9.1678 | 20.1779 | 20077.8708 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300541 [2SEDALI 69.000] TO BUS 300545 [2SYLVAN 69.000] CKT 1 | 27.2084 | 0.2211 | 121.1362 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0129 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0129 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0129 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6234 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1996 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1996 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1996 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 21.7432 | 20.4494 | 20349.3746 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4569 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.652 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 33.9415 | 246.751 | 246650.9867 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3463 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4458 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1084 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4973 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4394 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.7023 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.6149 | 45.7967 | 45696.704 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.6149 | 22.4462 | 22346.1828 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.446 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3146 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 20.2503 | 21.1156 | 21015.6107 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 20.2503 | 21.0467 | 20946.73 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 20.2503 | 19.3565 | 19256.5166 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 20.2503 | 18.8804 | 18780.4422 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 9.1671 | 20.1766 | 20076.6419 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 300089 [5JAMESV 161.00] CKT 1 | 27.2086 | 0.2211 | 121.1025 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 18.2742 | 18174.223 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 18.2742 | 18174.223 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 18.2742 | 18174.223 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 18.0095 | 17909.4704 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 19.0371 | 18937.1417 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 19.0371 | 18937.1417 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 19.0371 | 18937.1417 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.5702 | 20.422 | 20322.0293 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.3259 | 19.1032 | 19003.2392 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.3259 | 24.8329 | 24732.8822 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 33.9282 | 246.3448 | 246244.8316 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 13.8003 | 13700.265 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 12.5129 | 12412.8968 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 11.1921 | 11092.0552 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 9.1556 | 9055.6164 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 8.888 | 8788.037 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4864 | 8.6367 | 8536.7476 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.608 | 45.8423 | 45742.2606 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.608 | 22.4392 | 22339.2254 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.2778 | 26.6687 | 26568.7468 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.2778 | 41.9744 | 41874.4315 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1794 | 21.1353 | 21035.3231 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1794 | 21.0693 | 20969.3166 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1794 | 19.3703 | 19270.326 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1794 | 18.8941 | 18794.1226 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.1549 | 20.1878 | 20087.7569 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.3591 | 0.239 | 138.961 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 18.0297 | 17929.7143 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2797 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2797 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2797 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7414 | 20.4494 | 20349.4377 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.3381 | 19.1096 | 19009.5561 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.8708 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 33.9415 | 246.7514 | 246651.3808 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 13.8104 | 13710.3501 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 12.5214 | 12421.4484 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 11.1991 | 11099.1113 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 9.1705 | 9070.5058 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 8.9024 | 8802.4471 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5057 | 8.6507 | 8550.7101 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.6148 | 45.7983 | 45698.3165 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.6148 | 22.4459 | 22345.925 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.2782 | 26.6676 | 26567.575 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.2782 | 41.9807 | 41880.7033 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2487 | 21.1165 | 21016.4658 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2487 | 21.0478 | 20947.8496 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2487 | 19.3572 | 19257.1732 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2487 | 18.8813 | 18781.2658 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 9.1674 | 20.1784 | 20078.4001 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 27.1894 | 0.2212 | 121.1968 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 18.2951 | 18195.1036 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 18.2951 | 18195.1036 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 18.2951 | 18195.1036 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 18.0297 | 17929.7144 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 19.0603 | 18960.2798 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 19.0603 | 18960.2798 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 19.0603 | 18960.2798 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.7414 | 20.4494 | 20349.4368 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.3381 | 19.1096 | 19009.5561 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.3381 | 24.8479 | 24747.8708 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 33.9415 | 246.7514 | 246651.3816 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 13.8104 | 13710.3501 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 12.5214 | 12421.4484 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 11.1991 | 11099.1113 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 9.1705 | 9070.5058 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 8.9024 | 8802.4471 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.5057 | 8.6507 | 8550.7102 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.6148 | 45.7983 | 45698.3165 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.6148 | 22.4459 | 22345.925 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.2782 | 26.6676 | 26567.575 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.2782 | 41.9807 | 41880.7033 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 20.2487 | 21.1165 | 21016.4663 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 20.2487 | 21.0479 | 20947.8503 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 20.2487 | 19.3572 | 19257.1736 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 20.2487 | 18.8813 | 18781.2663 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 9.1674 | 20.1784 | 20078.4001 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 27.1894 | 0.2212 | 121.1968 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 18.2953 | 18195.3024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 18.2953 | 18195.3024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 18.2953 | 18195.3024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 18.0299 | 17929.9143 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 19.0605 | 18960.4863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 19.0605 | 18960.4863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 19.0605 | 18960.4863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.7232 | 20.4497 | 20349.665 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.3344 | 19.1075 | 19007.4598 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.3344 | 24.843 | 24743.0213 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 33.9398 | 246.6988 | 246598.8079 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 13.8101 | 13710.0772 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 12.5212 | 12421.2162 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 11.1989 | 11098.9205 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 9.1701 | 9070.1058 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 8.9021 | 8802.0592 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.5037 | 8.6503 | 8550.3328 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.6143 | 45.8016 | 45701.5615 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.6143 | 22.4454 | 22345.4251 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.2779 | 26.6679 | 26567.9282 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.2779 | 41.9791 | 41879.059 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 20.2435 | 21.1143 | 21014.3343 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 20.2435 | 21.0444 | 20944.3642 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 20.2435 | 19.3553 | 19255.2707 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 20.2435 | 18.8781 | 18778.0977 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 9.1663 | 20.1753 | 20075.2957 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 26.9454 | 0.2199 | 119.9221 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 18.2938 | 18193.7666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 18.2938 | 18193.7666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 18.2938 | 18193.7666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 18.0284 | 17928.394 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 19.059 | 18958.9554 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 19.059 | 18958.9554 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 19.059 | 18958.9554 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.7378 | 20.4481 | 2034810% | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.3385 | 19.1098 | 19009.8316 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.3385 | 24.8485 | 2474849% | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 33.9419 | 246.7609 | 246660.8851 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 13.8094 | 13709.4475 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 12.5207 | 12420.6739 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 11.1985 | 11098.4721 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 9.1692 | 9069.2227 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 8.9012 | 8801.1997 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.5042 | 8.6495 | 8549.4956 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.5787 | 46.5231 | 46423.0602 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.5787 | 22.3318 | 22231.7923 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.278 | 26.6701 | 26570.0782 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.278 | 41.9684 | 41868.4328 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 20.2512 | 21.1162 | 21016.1582 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 20.2512 | 21.0476 | 20947.6029 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 20.2512 | 19.357 | 19256.9939 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 20.2512 | 18.8812 | 18781.2174 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 9.161 | 20.1835 | 20083.4971 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 26.95 | 0.221 | 121.0103 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 18.2977 | 18197.713 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 18.2977 | 18197.713 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 18.2977 | 18197.713 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 18.0324 | 17932.4014 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 19.0624 | 18962.4151 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 19.0624 | 18962.4151 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 19.0624 | 18962.4151 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.6032 | 20.4509 | 20350.8592 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.3376 | 19.1098 | 19009.7979 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.3376 | 24.8481 | 24748.104 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 33.9401 | 246.6497 | 246549.7329 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 13.8064 | 13706.4168 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 12.5181 | 12418.1002 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 11.1964 | 11096.3564 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 9.1648 | 9064.7532 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 8.8969 | 8796.8704 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.4904 | 8.6453 | 8545.2968 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.6036 | 45.8647 | 45764.6836 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.6036 | 22.4358 | 22335.8422 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.2761 | 26.6713 | 26571.3117 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.2761 | 41.9629 | 41862.9276 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 20.2129 | 21.1216 | 21021.571 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 20.2129 | 21.0534 | 20953.3853 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 20.2129 | 19.3604 | 19260.4163 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 20.2129 | 18.884 | 18784.0234 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 9.139 | 20.1801 | 20080.0654 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 25.5061 | 0.2203 | 120.302 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 18.295 | 18195.0339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 18.295 | 18195.0339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 18.295 | 18195.0339 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 18.0296 | 17929.6456 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 19.0602 | 18960.2167 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 19.0602 | 18960.2167 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 19.0602 | 18960.2167 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 21.7424 | 20.4494 | 20349.3819 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.3377 | 19.1093 | 19009.3327 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.3377 | 24.8474 | 24747.3605 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 33.9413 | 246.7474 | 246647.3611 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 13.8102 | 13710.2181 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 12.5213 | 12421.3368 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 11.199 | 11099.0188 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 9.1703 | 9070.3103 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 8.9023 | 8802.2583 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 12.5056 | 8.6505 | 8550.5265 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.6141 | 45.7984 | 45698.3671 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.6141 | 22.446 | 22345.9789 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.278 | 26.668 | 26567.9571 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 13.278 | 41.9789 | 41878.8963 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 20.083 | 21.1516 | 21051.5627 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 20.083 | 21.092 | 20991.9516 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 20.083 | 19.3821 | 19282.0819 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 20.083 | 18.9103 | 18810.2916 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 9.1052 | 20.2025 | 20102.5331 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505485 [WASHBURN5 161.00] CKT 1 | 27.206 | 0.2212 | 121.1846 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 18.2952 | 18195.1801 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 18.2952 | 18195.1801 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 18.2952 | 18195.1801 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 18.0298 | 17929.7859 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 19.0604 | 18960.3833 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 19.0604 | 18960.3833 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 19.0604 | 18960.3833 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 21.7431 | 20.4496 | 20349.5889 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.337 | 19.1089 | 19008.9452 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.337 | 24.8465 | 24746.4697 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 33.9411 | 246.7397 | 246639.7229 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 13.8105 | 13710.4833 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 12.5216 | 12421.5618 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 11.1992 | 11099.2047 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 9.1707 | 9070.7004 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 8.9026 | 8802.6357 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 12.506 | 8.6509 | 8550.8932 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.6148 | 45.7969 | 45696.9465 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.6148 | 22.4462 | 22346.1502 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.2779 | 26.6677 | 26567.7078 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 13.2779 | 41.9801 | 41880.1065 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 20.1122 | 21.1339 | 21033.893 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 20.1122 | 21.073 | 20972.9763 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 20.1122 | 19.3696 | 19269.5975 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 20.1122 | 18.8993 | 18799.2581 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 9.062 | 20.2365 | 20136.5249 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547471 [NEO184 5 161.00] CKT 1 | 27.2087 | 0.2211 | 121.1135 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 18.2952 | 18195.2245 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 18.2952 | 18195.2245 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 18.2952 | 18195.2245 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 18.0298 | 17929.8385 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 19.0604 | 18960.368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 19.0604 | 18960.368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 19.0604 | 18960.368 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7402 | 20.4495 | 20349.4744 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3377 | 19.1094 | 19009.3715 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3377 | 24.8475 | 24747.4539 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9413 | 246.7458 | 246645.8163 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 13.8106 | 13710.5527 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 12.5216 | 12421.6188 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 11.1993 | 11099.2517 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 9.1708 | 9070.8117 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 8.9027 | 8802.7421 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5058 | 8.651 | 8550.9949 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6153 | 45.7961 | 45696.0697 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6153 | 22.4463 | 22346.2585 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2768 | 26.6726 | 26572.5961 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2768 | 41.9565 | 41856.4894 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 19.8233 | 21.2795 | 21179.5297 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 19.8233 | 21.2569 | 21156.8562 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 19.8233 | 19.478 | 19378.035 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 19.8233 | 19.0272 | 18927.1852 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 6.0628 | 21.9488 | 21848.8145 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2087 | 0.2211 | 121.0771 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 18.295 | 18195.0467 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 18.295 | 18195.0467 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 18.295 | 18195.0467 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 18.0297 | 17929.6578 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 19.0602 | 18960.2217 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 19.0602 | 18960.2217 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 19.0602 | 18960.2217 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 21.7419 | 20.4494 | 20349.3756 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.338 | 19.1095 | 19009.4874 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.338 | 24.8477 | 24747.7251 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 33.9415 | 246.7522 | 246652.196 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 13.8103 | 13710.3134 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 12.5214 | 12421.417 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 11.1991 | 11099.085 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 9.1705 | 9070.4534 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 8.9024 | 8802.3967 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 12.5055 | 8.6507 | 8550.6602 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.6117 | 45.817 | 45717.0376 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.6117 | 22.4431 | 22343.0775 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.2781 | 26.6675 | 26567.4667 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 13.2781 | 41.9812 | 41881.2102 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 20.2246 | 21.1235 | 21023.5257 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 20.2246 | 21.0575 | 20957.4544 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 20.2246 | 19.3625 | 19262.5125 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 20.2246 | 18.8884 | 18788.3505 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 9.1168 | 20.2141 | 20114.0538 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300649 [2JASPER 69.000] CKT 1 | 27.1953 | 0.2212 | 121.1904 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 18.295 | 18194.9913 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 18.295 | 18194.9913 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 18.295 | 18194.9913 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 18.0296 | 17929.6016 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 19.0602 | 18960.1794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 19.0602 | 18960.1794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 19.0602 | 18960.1794 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 21.7431 | 20.4494 | 20349.3543 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.3378 | 19.1094 | 19009.4222 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.3378 | 24.8476 | 24747.5718 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 33.9413 | 246.7503 | 246650.2592 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 13.8104 | 13710.3587 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 12.5215 | 12421.4566 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1174 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.5151 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 8.9025 | 8802.4569 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.7193 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.6146 | 45.7936 | 45693.6331 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.6146 | 22.4467 | 22346.7097 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.2782 | 26.6674 | 26567.3984 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 13.2782 | 41.9816 | 41881.5696 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 20.2478 | 21.115 | 21014.9702 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 20.2478 | 21.0456 | 20945.5613 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 20.2478 | 19.3559 | 19255.9191 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 20.2478 | 18.8793 | 18779.3255 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 9.1473 | 20.1779 | 20077.948 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300745 [2DMNDTP 69.000] CKT 1 | 27.2084 | 0.2211 | 121.1171 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9894 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9894 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9894 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.6007 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1742 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1742 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1742 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 21.7432 | 20.4493 | 20349.3427 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.338 | 19.1095 | 19009.5158 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.338 | 24.8478 | 24747.7883 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 33.9415 | 246.7531 | 246653.0691 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 13.8103 | 13710.2885 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 12.5214 | 12421.3968 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 11.1991 | 11099.0685 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 9.1704 | 9070.4129 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 8.9024 | 8802.3576 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 12.5058 | 8.6506 | 8550.6231 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.6139 | 45.8009 | 45700.9304 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.6139 | 22.4456 | 22345.5692 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.2782 | 26.6675 | 26567.4501 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 13.2782 | 41.9813 | 41881.3102 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 20.2199 | 21.1148 | 21014.8356 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 20.2199 | 21.0458 | 20945.8034 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 20.2199 | 19.3555 | 19255.5146 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 20.2199 | 18.8792 | 18779.2398 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 9.1422 | 20.183 | 20083.0225 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505490 [CARTHG 2 69.000] TO BUS 300751 [2REEDS 69.000] CKT 1 | 27.2078 | 0.2212 | 121.1513 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8787 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8787 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8787 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.0295 | 17929.4935 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.06 | 1896005% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.06 | 18960.0494 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.06 | 1896005% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 20.4492 | 20349.1939 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3383 | 19.1097 | 19009.6643 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3383 | 24.8481 | 24748.127 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9415 | 246.7553 | 246655.3174 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 13.81 | 13710.0102 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 12.5212 | 12421.1607 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 11.1989 | 11098.8734 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 9.17 | 9070.0031 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 8.902 | 8801.961 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5054 | 8.6502 | 8550.2394 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6124 | 45.812 | 45712.035 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6124 | 22.4438 | 22343.8317 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.278 | 26.6677 | 26567.6835 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.278 | 41.9802 | 41880.194 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1302 | 21.125 | 21024.9699 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1302 | 21.0561 | 20956.1236 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1302 | 19.3618 | 19261.8233 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1302 | 18.8838 | 18783.7947 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 7.7479 | 20.4742 | 20374.1783 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.1997 | 0.2214 | 121.3638 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 18.295 | 18194.9802 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 18.295 | 18194.9802 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 18.295 | 18194.9802 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 18.0296 | 17929.5926 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 19.0602 | 18960.1596 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 19.0602 | 18960.1596 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 19.0602 | 18960.1596 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 21.7429 | 20.4493 | 20349.3203 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.338 | 19.1095 | 19009.5176 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.338 | 24.8478 | 24747.7947 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 33.9414 | 246.7531 | 246653.119 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 13.8103 | 13710.2823 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 12.5214 | 12421.3914 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 11.1991 | 11099.0641 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 9.1704 | 9070.4039 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 8.9023 | 8802.3497 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 12.5057 | 8.6506 | 8550.6151 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.6126 | 45.806 | 45705.9623 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.6126 | 22.4448 | 22344.8062 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.278 | 26.6675 | 26567.514 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 13.278 | 41.981 | 41880.9563 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 20.2497 | 21.1156 | 21015.6108 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 20.2497 | 21.0467 | 20946.6572 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 20.2497 | 19.3565 | 19256.4971 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 20.2497 | 18.8803 | 18780.3373 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 9.1673 | 20.176 | 20075.9622 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505494 [SPRGFLD2 69.000] TO BUS 300669 [2ELWOOD 69.000] CKT 1 | 27.2079 | 0.2212 | 121.1548 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0332 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0332 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0332 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 18.0296 | 17929.6447 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2166 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 21.7429 | 20.4494 | 20349.384 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4736 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6912 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 33.9415 | 246.7523 | 246652.3406 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3403 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4405 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1045 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4898 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4328 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6958 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.6145 | 45.8042 | 45704.1648 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.6145 | 22.445 | 22344.9806 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4853 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 13.2782 | 41.9811 | 41881.109 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 20.2501 | 21.1157 | 21015.677 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 20.2501 | 21.0468 | 20946.7799 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 20.2501 | 19.3566 | 19256.5569 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 20.2501 | 18.8805 | 18780.4528 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 9.1673 | 20.176 | 20076.0454 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505472 [TABLE R5 161.00] CKT 1 | 27.2047 | 0.2211 | 121.1316 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0012 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0012 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0012 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6108 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3594 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.338 | 19.1095 | 19009.4823 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.338 | 24.8477 | 24747.711 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 33.9415 | 246.7537 | 246653.6954 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3375 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 12.5214 | 12421.4385 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.1024 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.4841 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4273 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.6906 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.6148 | 45.7968 | 45696.7723 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.6148 | 22.4462 | 22346.1734 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.2782 | 26.6674 | 26567.4473 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 13.2782 | 41.9813 | 41881.3084 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 20.2502 | 21.1156 | 21015.6402 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 20.2502 | 21.0468 | 20946.7813 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 20.2502 | 19.3565 | 19256.5437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 20.2502 | 18.8805 | 18780.492 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 9.1678 | 20.1776 | 20077.6445 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505497 [NXA X1 1 13.800] CKT 1 | 27.209 | 0.2211 | 121.123 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6112 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1871 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1871 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1871 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3599 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.3379 | 19.1095 | 19009.4808 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.3379 | 24.8477 | 24747.7108 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 33.9415 | 246.7522 | 246652.1693 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3377 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 12.5214 | 12421.4388 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.1026 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.4845 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4277 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.691 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.6149 | 45.7968 | 45696.7742 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.6149 | 22.4462 | 22346.1728 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.2782 | 26.6674 | 26567.4473 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 13.2782 | 41.9813 | 41881.3084 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 20.2502 | 21.1156 | 21015.6438 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 20.2502 | 21.0468 | 20946.7875 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 20.2502 | 19.3565 | 19256.5456 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 20.2502 | 18.8805 | 18780.4955 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 9.1678 | 20.1777 | 20077.68 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505496 [NIXA 5 161.00] TO BUS 505501 [NIXA 2 69.000] TO BUS 505499 [NXA X2 1 13.800] CKT 1 | 27.209 | 0.2211 | 121.1228 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.4296 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.4296 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 18.2954 | 18195.4296 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 18.03 | 17930.0274 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 19.0607 | 18960.6577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 19.0607 | 18960.6577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 19.0607 | 18960.6577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 21.7445 | 20.4499 | 20349.9112 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.3087 | 19.1595 | 19059.4745 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.3087 | 24.8677 | 24767.6591 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 33.9405 | 246.5947 | 246494.651 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 13.8111 | 13711.061 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 12.5221 | 12422.0512 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 11.1996 | 11099.6089 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 9.1716 | 9071.5515 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 8.9035 | 8803.4595 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 12.5069 | 8.6517 | 8551.6913 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.616 | 45.7953 | 45695.2678 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.616 | 22.4463 | 22346.3339 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.2783 | 26.6673 | 26567.3412 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 13.2783 | 41.9818 | 41881.8416 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 20.2506 | 21.1158 | 21015.7845 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 20.2506 | 21.047 | 20947.0286 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 20.2506 | 19.3567 | 19256.6729 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 20.2506 | 18.8807 | 18780.7207 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 9.1685 | 20.1787 | 20078.7377 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515590 [PALDR2W7 345.00] CKT 1 | 27.2144 | 0.221 | 120.9558 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 18.2954 | 18195.4094 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 18.2954 | 18195.4094 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 18.2954 | 18195.4094 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 18.03 | 17930.0093 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 19.0606 | 18960.6349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 21.7444 | 20.4499 | 20349.8837 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.2999 | 19.1869 | 19086.8844 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.2999 | 24.904 | 24804.0213 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 33.9409 | 246.5854 | 246485.3652 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 13.811 | 13711.016 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 12.522 | 12422.0137 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 11.1996 | 11099.5774 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 9.1715 | 9071.4858 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 8.9034 | 8803.3967 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 12.5068 | 8.6516 | 8551.6297 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.6159 | 45.7954 | 45695.3503 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.6159 | 22.4463 | 22346.3231 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.2783 | 26.6674 | 26567.3581 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 13.2783 | 41.9818 | 41881.7902 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 20.2506 | 21.1158 | 21015.7895 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 20.2506 | 21.047 | 20947.0356 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 20.2506 | 19.3567 | 19256.6778 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 20.2506 | 18.8807 | 18780.7264 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 9.1684 | 20.1787 | 20078.6934 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515618 [BALKOW 7 345.00] CKT 1 | 27.214 | 0.221 | 120.9653 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0286 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0286 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 18.295 | 18195.0286 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 18.0296 | 17929.6391 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.2149 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.2149 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 19.0602 | 18960.2149 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7431 | 20.4494 | 20349.3888 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.1995 | 19.2146 | 19114.6325 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.1995 | 24.9716 | 24871.6061 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 33.9437 | 246.7712 | 246671.1707 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3365 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4375 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 11.1991 | 11099.1021 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4834 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4266 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5059 | 8.6507 | 8550.6898 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.6149 | 45.7967 | 45696.694 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1859 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.2782 | 26.6675 | 26567.4668 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.2782 | 41.9812 | 41881.2277 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2504 | 21.1157 | 21015.734 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2504 | 21.0469 | 20946.9285 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2504 | 19.3566 | 19256.6235 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2504 | 18.8806 | 18780.6189 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 9.168 | 20.178 | 20077.9968 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 27.209 | 0.2211 | 121.1141 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 18.295 | 18195.0287 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 18.295 | 1819503% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 18.295 | 18195.0287 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 18.0296 | 1792964% | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 19.0602 | 18960.215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 19.0602 | 18960.215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 19.0602 | 18960.215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 21.7431 | 20.4494 | 20349.389 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.1993 | 19.2147 | 19114.7423 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.1993 | 24.9717 | 24871.7135 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 33.9437 | 246.7711 | 246671.1309 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 13.8103 | 13710.3365 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 12.5214 | 12421.4375 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 11.1991 | 11099.102 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 9.1705 | 9070.4834 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 8.9024 | 8802.4258 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 12.5059 | 8.6507 | 8550.6898 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.6149 | 45.7967 | 45696.694 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.6149 | 22.4462 | 22346.1859 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.2782 | 26.6675 | 26567.4668 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 13.2782 | 41.9812 | 41881.2277 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 20.2504 | 21.1157 | 21015.7341 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 20.2504 | 21.0469 | 20946.9286 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 20.2504 | 19.3566 | 19256.6235 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 20.2504 | 18.8806 | 18780.619 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 9.168 | 20.178 | 20077.9968 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 2 | 27.209 | 0.2211 | 121.1141 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 18.295 | 18195.0114 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 18.0296 | 17929.6208 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 19.0602 | 18960.1977 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 19.0602 | 18960.1977 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 19.0602 | 18960.1977 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 21.7433 | 20.4494 | 20349.3712 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.3107 | 19.0704 | 18970.3925 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.3107 | 24.7974 | 24697.3704 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 33.9404 | 246.7468 | 246646.7962 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 13.8104 | 13710.3629 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 12.5215 | 12421.4601 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 11.1991 | 11099.1201 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 9.1705 | 9070.5219 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 8.9025 | 8802.4639 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 12.5059 | 8.6507 | 8550.7261 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.615 | 45.7966 | 45696.6248 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.615 | 22.4462 | 22346.1945 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.2783 | 26.6674 | 26567.4437 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 13.2783 | 41.9813 | 41881.3267 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 20.2503 | 21.1157 | 21015.6636 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 20.2503 | 21.0468 | 20946.8067 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 20.2503 | 19.3566 | 19256.5602 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 20.2503 | 18.8805 | 18780.5052 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 9.168 | 20.178 | 20077.9901 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523155 [OCHILTREE 6230.00] CKT 1 | 27.2091 | 0.2211 | 121.1184 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0023 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0023 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0023 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 18.0296 | 17929.6124 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.186 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.186 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.186 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 21.743 | 20.4494 | 20349.3554 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.1338 | 19.1634 | 19063.4444 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.1338 | 24.9015 | 24801.5133 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 33.9377 | 246.641 | 246541.0256 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 13.8104 | 13710.4052 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 12.5215 | 12421.4957 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 11.1991 | 11099.1495 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 9.1706 | 9070.5841 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 8.9025 | 8802.524 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 12.5059 | 8.6508 | 8550.7843 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.615 | 45.7967 | 45696.6665 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.615 | 22.4462 | 22346.1861 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 13.2782 | 41.9813 | 41881.2945 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 20.25 | 21.1156 | 21015.5676 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 20.25 | 21.0466 | 20946.6223 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 20.25 | 19.3565 | 19256.468 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 20.25 | 18.8803 | 18780.3228 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 9.168 | 20.1779 | 20077.9368 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523309 [MOORE_CNTY 6230.00] CKT 1 | 27.2081 | 0.2211 | 121.1392 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 18.295 | 18194.9968 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 18.295 | 18194.9968 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 18.295 | 18194.9968 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 18.0296 | 17929.6078 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 21.7432 | 20.4494 | 20349.3532 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.3087 | 19.0758 | 18975.8115 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.3087 | 24.8055 | 24705.4628 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 33.9411 | 246.7503 | 246650.3342 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 13.8103 | 13710.3317 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 12.5214 | 12421.4329 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 11.1991 | 11099.0983 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 9.1705 | 9070.4749 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 8.9024 | 8802.4185 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 12.5059 | 8.6507 | 8550.682 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.6149 | 45.7967 | 45696.719 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.6149 | 22.4462 | 22346.1854 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.2782 | 26.6674 | 26567.4467 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 13.2782 | 41.9813 | 41881.2938 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 20.2503 | 21.1157 | 21015.669 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 20.2503 | 21.0468 | 20946.8163 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 20.2503 | 19.3566 | 19256.5648 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 20.2503 | 18.8805 | 18780.5139 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 9.168 | 20.178 | 20077.9641 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523098 [HITCHLD_TR4113.200] CKT 2 | 27.209 | 0.2211 | 121.1235 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 18.0296 | 17929.6074 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1811 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1811 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1811 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 21.7432 | 20.4494 | 20349.3526 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.3064 | 19.074 | 18973.9587 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.3064 | 24.8031 | 24703.1037 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 33.941 | 246.7506 | 246650.578 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 13.8103 | 13710.3313 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 12.5214 | 12421.4326 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 11.1991 | 11099.098 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 9.1705 | 9070.4744 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 8.9024 | 8802.4179 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 12.5059 | 8.6507 | 8550.6816 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.6149 | 45.7967 | 45696.7187 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.6149 | 22.4462 | 22346.1855 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.2782 | 26.6674 | 26567.4467 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 13.2782 | 41.9813 | 41881.2938 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 20.2503 | 21.1157 | 21015.669 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 20.2503 | 21.0468 | 20946.8146 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 20.2503 | 19.3566 | 19256.5648 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 20.2503 | 18.8805 | 18780.5136 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 9.168 | 20.178 | 20077.9635 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523095 [HITCHLAND 6230.00] TO BUS 523093 [HITCHLAND 3115.00] TO BUS 523092 [HITCHLD_TR1113.200] CKT 1 | 27.209 | 0.2211 | 121.1236 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 18.2948 | 18194.7918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 18.2948 | 18194.7918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 18.2948 | 18194.7918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 18.0294 | 17929.4085 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 19.06 | 18959.952 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 19.06 | 18959.952 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 19.06 | 18959.952 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.7429 | 20.4491 | 20349.0756 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 6.6715 | 32.378 | 32278.02 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 6.6715 | 35.5149 | 35414.8564 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 33.8187 | 244.4325 | 244332.5273 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 13.8116 | 13711.6289 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 12.5225 | 12422.5333 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 11.2 | 11100.0065 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 9.1724 | 9072.3917 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 8.9043 | 8804.2724 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5077 | 8.6525 | 8552.4782 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.6153 | 45.7966 | 45696.5898 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.6153 | 22.4462 | 22346.1727 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.2782 | 26.6673 | 26567.324 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.2782 | 41.982 | 41881.9518 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.244 | 21.1134 | 21013.3723 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.244 | 21.0425 | 20942.5365 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.244 | 19.3544 | 19254.3812 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.244 | 18.8763 | 18776.3479 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 9.1672 | 20.1767 | 20076.7411 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 27.1978 | 0.2215 | 121.5042 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 18.295 | 18194.9796 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 18.295 | 18194.9796 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 18.295 | 18194.9796 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 18.0296 | 17929.5912 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 19.0602 | 18960.1638 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 21.7432 | 20.4493 | 20349.3312 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.3381 | 19.0995 | 18999.5086 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.3381 | 24.8362 | 24736.1738 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 33.9413 | 246.7553 | 246655.2924 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 13.8103 | 13710.3018 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 12.5214 | 12421.4081 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 11.1991 | 11099.0774 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 9.1704 | 9070.4315 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 8.9024 | 8802.3756 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 12.5059 | 8.6506 | 8550.6406 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.6148 | 45.7967 | 45696.7431 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.6148 | 22.4462 | 22346.1815 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.2782 | 26.6675 | 26567.4536 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 13.2782 | 41.9813 | 41881.2928 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 20.2503 | 21.1157 | 21015.6663 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 20.2503 | 21.0468 | 20946.8114 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 20.2503 | 19.3566 | 19256.5624 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 20.2503 | 18.8805 | 18780.5095 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 9.168 | 20.1779 | 20077.9301 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523101 [NOBLE_WND 7345.00] TO BUS 523103 [NOBLE_WND 3115.00] TO BUS 523102 [NOBLE_TR 113.800] CKT 1 | 27.2089 | 0.2211 | 121.13 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 18.295 | 18195.0032 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 18.295 | 18195.0032 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 18.295 | 18195.0032 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 18.0296 | 17929.6139 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 21.7433 | 20.4494 | 20349.3618 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.338 | 19.1094 | 19009.4399 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.338 | 24.8477 | 24747.6931 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 33.9415 | 246.7522 | 246652.1905 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 13.8103 | 13710.3398 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 12.5214 | 12421.4405 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 11.1991 | 11099.104 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 9.1705 | 9070.4876 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 8.9024 | 8802.4307 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 12.5059 | 8.6507 | 8550.6939 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.6149 | 45.7967 | 45696.6959 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.6149 | 22.4462 | 22346.1882 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 20.2503 | 21.0468 | 20946.8283 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 20.2503 | 19.3566 | 19256.571 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 20.2503 | 18.8805 | 18780.5275 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 9.168 | 20.178 | 2007797% | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 560577 [G06-44 115.00] TO BUS 560578 [NOVUS1_TR2 213.800] CKT 2 | 27.2092 | 0.2211 | 121.1205 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 18.295 | 1819500% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 18.295 | 18195.0032 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 18.295 | 18195.0032 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 18.0296 | 17929.614 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 19.0602 | 18960.1898 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 21.7433 | 20.4494 | 20349.3618 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.338 | 19.1094 | 19009.4116 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.338 | 24.8477 | 24747.6795 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 33.9415 | 246.7537 | 246653.7061 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 13.8103 | 13710.3396 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 12.5214 | 12421.4403 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 11.1991 | 11099.1038 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 9.1705 | 9070.4872 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 8.9024 | 8802.4304 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 12.5059 | 8.6507 | 8550.6936 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.6149 | 45.7967 | 45696.6956 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.6149 | 22.4462 | 22346.1883 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 20.2503 | 21.1157 | 21015.6749 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 20.2503 | 21.0468 | 20946.8282 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 20.2503 | 19.3566 | 19256.571 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 20.2503 | 18.8805 | 18780.5274 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 9.168 | 20.178 | 20077.974 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523112 [NOVUS1 7345.00] TO BUS 523111 [NOVUS1 3115.00] TO BUS 523110 [NOVUS1_TR1 113.800] CKT 1 | 27.2092 | 0.2211 | 121.1205 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 18.0296 | 17929.6171 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 21.7433 | 20.4494 | 20349.3652 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.3404 | 19.1214 | 19021.3856 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.3404 | 24.862 | 24762.0246 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 33.9421 | 246.6682 | 246568.1975 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 13.8103 | 13710.3415 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 12.5214 | 12421.4419 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 11.1991 | 11099.1056 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 9.1705 | 9070.4911 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 8.9024 | 8802.4334 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 12.5059 | 8.6507 | 8550.6965 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.6149 | 45.7967 | 45696.6967 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.6149 | 22.4462 | 22346.1879 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 13.2782 | 41.9813 | 41881.2934 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 20.2503 | 21.1157 | 21015.6779 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 20.2503 | 21.0468 | 20946.833 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 20.2503 | 19.3566 | 19256.5734 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 20.2503 | 18.8805 | 18780.5303 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 9.168 | 20.178 | 20077.9756 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523116 [BUFF_DUNES1134.500] TO BUS 523114 [BUFF_DN_TR1113.200] CKT 1 | 27.2091 | 0.2211 | 121.12 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 18.295 | 18195.0064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 18.0296 | 17929.6171 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 19.0602 | 18960.1919 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 21.7433 | 20.4494 | 20349.3652 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.3404 | 19.1214 | 19021.4256 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.3404 | 24.8621 | 24762.0759 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 33.9421 | 246.6696 | 246569.6345 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 13.8103 | 13710.3415 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 12.5214 | 12421.4419 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 11.1991 | 11099.1056 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 9.1705 | 9070.4911 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 8.9024 | 8802.4333 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 12.5059 | 8.6507 | 8550.6964 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.6149 | 45.7967 | 45696.6967 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.6149 | 22.4462 | 22346.1879 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 13.2782 | 41.9813 | 41881.2934 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 20.2503 | 21.1157 | 21015.6779 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 20.2503 | 21.0468 | 20946.833 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 20.2503 | 19.3566 | 19256.5734 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 20.2503 | 18.8805 | 18780.5303 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 9.168 | 20.178 | 20077.9756 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523117 [BUFF_DUNES2134.500] TO BUS 523115 [BUFF_DN_TR2113.200] CKT 2 | 27.2091 | 0.2211 | 121.12 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 18.295 | 18194.9568 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 18.295 | 18194.9568 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 18.295 | 18194.9568 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 18.0296 | 17929.5692 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 19.0601 | 18960.1365 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 19.0601 | 18960.1365 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 19.0601 | 18960.1365 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 21.743 | 20.4493 | 20349.2975 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 8.6234 | 26.0806 | 25980.6085 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 8.6234 | 31.3037 | 31203.7128 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 33.8928 | 244.9737 | 244873.7427 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 13.8109 | 13710.9391 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 12.5219 | 12421.9484 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 11.1995 | 11099.5235 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 9.1714 | 9071.3728 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 8.9033 | 8803.2865 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 12.5066 | 8.6515 | 8551.5237 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.6151 | 45.7966 | 45696.5637 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.6151 | 22.4462 | 22346.1925 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.2783 | 26.6674 | 26567.3931 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 13.2783 | 41.9816 | 41881.5939 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.2478 | 21.1147 | 21014.7464 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.2478 | 21.0451 | 20945.0941 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.2478 | 19.3557 | 19255.6884 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 20.2478 | 18.8788 | 18778.8393 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 9.1677 | 20.1775 | 20077.4597 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 523823 [CARPENTER 7345.00] CKT 1 | 27.2043 | 0.2213 | 121.2774 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 18.0296 | 17929.6143 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.7432 | 20.4494 | 20349.3616 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2945 | 19.1171 | 19017.1227 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2945 | 24.8571 | 24757.0602 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 33.9412 | 246.7401 | 246640.0862 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 13.8103 | 13710.3421 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 12.5214 | 12421.4417 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 11.1991 | 11099.1055 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 9.1705 | 9070.4904 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 8.9024 | 8802.4334 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 8.6507 | 8550.6965 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.6149 | 45.7967 | 45696.6954 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.6149 | 22.4462 | 22346.191 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2782 | 26.6674 | 26567.4434 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2503 | 21.1157 | 21015.671 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2503 | 21.0468 | 20946.8202 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2503 | 19.3566 | 19256.5675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2503 | 18.8805 | 18780.5186 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 9.168 | 20.178 | 20077.9695 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 27.2091 | 0.2211 | 121.1218 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 18.295 | 18195.0035 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 18.0296 | 17929.6143 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 19.0602 | 18960.1899 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 21.7432 | 20.4494 | 20349.3616 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.2945 | 19.1171 | 19017.1227 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.2945 | 24.8571 | 24757.0602 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 33.9412 | 246.7401 | 246640.0862 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 13.8103 | 13710.3421 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 12.5214 | 12421.4417 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 11.1991 | 11099.1055 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 9.1705 | 9070.4904 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 8.9024 | 8802.4334 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 12.5059 | 8.6507 | 8550.6965 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.6149 | 45.7967 | 45696.6954 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.6149 | 22.4462 | 22346.191 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.2782 | 26.6674 | 26567.4434 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 20.2503 | 21.1157 | 21015.671 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 20.2503 | 21.0468 | 20946.8202 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 20.2503 | 19.3566 | 19256.5675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 20.2503 | 18.8805 | 18780.5186 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 9.168 | 20.178 | 20077.9695 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 2 | 27.2091 | 0.2211 | 121.1218 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 18.2952 | 18195.1918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 18.2952 | 18195.1918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 18.2952 | 18195.1918 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 18.0298 | 17929.7971 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 19.0604 | 18960.3978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 19.0604 | 18960.3978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 19.0604 | 18960.3978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 21.7438 | 20.4496 | 20349.6069 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.318 | 19.1153 | 19015.2925 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.318 | 24.836 | 24736.0369 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 33.9408 | 246.7028 | 246602.7649 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 13.8107 | 13710.6829 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 12.5217 | 12421.7314 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 11.1993 | 11099.3442 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 9.171 | 9070.9943 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 8.9029 | 8802.9203 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 12.5064 | 8.6512 | 8551.1683 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.6154 | 45.796 | 45695.9822 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.6154 | 22.4463 | 22346.2636 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.2783 | 26.6674 | 26567.3913 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 13.2783 | 41.9816 | 41881.5715 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 20.2504 | 21.1157 | 21015.6988 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 20.2504 | 21.0469 | 20946.8738 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 20.2504 | 19.3566 | 19256.5936 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 20.2504 | 18.8806 | 18780.5709 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 9.1682 | 20.1783 | 20078.3202 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 524296 [SPNSPUR_WND7345.00] CKT 1 | 27.2114 | 0.221 | 121.0486 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 18.0296 | 17929.5955 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 19.0602 | 18960.1673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 21.7431 | 20.4493 | 20349.3338 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.2244 | 19.1698 | 19069.8033 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.2244 | 24.913 | 24812.955 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 33.9376 | 246.6613 | 246561.3465 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 13.8104 | 13710.4376 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 12.5215 | 12421.5232 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 11.1992 | 11099.1728 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 9.1706 | 9070.6324 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 8.9026 | 8802.5708 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 12.506 | 8.6508 | 8550.8296 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.615 | 45.7966 | 45696.6212 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.615 | 22.4462 | 22346.19 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.2782 | 26.6674 | 26567.4435 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3281 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 20.2498 | 21.1155 | 21015.4797 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 20.2498 | 21.0465 | 2094646% | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 20.2498 | 19.3564 | 19256.3847 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 20.2498 | 18.8802 | 1878017% | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 9.168 | 20.1779 | 20077.9036 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 525549 [TOLK 7345.00] CKT 1 | 27.2079 | 0.2212 | 121.1541 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 18.2946 | 18194.6155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 18.2946 | 18194.6155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 18.2946 | 18194.6155 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 18.0292 | 17929.2372 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 19.0598 | 18959.7577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 19.0598 | 18959.7577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 19.0598 | 18959.7577 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.7417 | 20.4488 | 20348.8462 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.7796 | 19.1479 | 19047.8577 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.7796 | 24.8291 | 24729.1241 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 33.9022 | 245.1637 | 245063.6785 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 13.8091 | 13709.1307 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 12.5204 | 12420.4148 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 11.1983 | 11098.2573 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 9.1687 | 9068.7057 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 8.9007 | 8800.7055 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.5042 | 8.649 | 8549.022 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 13.6143 | 45.7978 | 45697.7947 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 13.6143 | 22.4461 | 22346.0545 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 13.2782 | 26.6676 | 26567.6355 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 13.2782 | 41.9804 | 41880.3585 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 20.2514 | 21.1161 | 21016.09 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 20.2514 | 21.0476 | 20947.5985 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 20.2514 | 19.357 | 19256.9633 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 20.2514 | 18.8813 | 18781.2731 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 9.1681 | 20.1781 | 20078.134 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 27.2086 | 0.2211 | 121.1085 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 18.2948 | 18194.8496 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 18.2948 | 18194.8496 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 18.2948 | 18194.8496 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 18.0295 | 17929.4693 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 19.06 | 18959.9932 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 19.06 | 18959.9932 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 19.06 | 18959.9932 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 21.7378 | 20.4491 | 20349.0911 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.3614 | 19.6148 | 19514.803 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.3614 | 25.3391 | 25239.101 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 33.8312 | 242.6428 | 242542.7904 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 13.8098 | 13709.8429 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 12.521 | 12421.0172 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 11.1988 | 11098.7551 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 9.1698 | 9069.7665 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 8.9017 | 8801.7304 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 12.5034 | 8.65 | 8550.0145 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 13.6146 | 45.7977 | 45697.6863 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 13.6146 | 22.4461 | 22346.0547 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 13.2781 | 26.6677 | 26567.7478 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 13.2781 | 41.9798 | 41879.8437 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 20.2494 | 21.1156 | 21015.5557 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 20.2494 | 21.0466 | 20946.5646 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 20.2494 | 19.3564 | 19256.4444 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 20.2494 | 18.8802 | 18780.25 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 9.1678 | 20.1778 | 20077.7906 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531501 [BUCKNER7 345.00] CKT 1 | 27.2001 | 0.2212 | 121.2028 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 18.2951 | 18195.0874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 18.2951 | 18195.0874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 18.2951 | 18195.0874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 18.0297 | 17929.6975 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 19.0603 | 18960.2758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 19.0603 | 18960.2758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 19.0603 | 18960.2758 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 21.742 | 20.4495 | 20349.453 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.9154 | 19.2127 | 19112.6553 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.9154 | 24.9753 | 24875.3056 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 33.9079 | 244.653 | 244553.0176 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 13.8104 | 13710.3879 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 12.5215 | 12421.481 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 11.1991 | 11099.1377 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 9.1706 | 9070.5621 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 8.9025 | 8802.5025 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 12.5054 | 8.6508 | 8550.763 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 13.615 | 45.7967 | 45696.6982 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 13.615 | 22.4462 | 22346.1815 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 13.2782 | 26.6675 | 26567.506 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 13.2782 | 41.981 | 41881.0242 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 20.2504 | 21.1158 | 21015.7658 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 20.2504 | 21.047 | 20946.9849 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 20.2504 | 19.3567 | 19256.6542 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 20.2504 | 18.8807 | 18780.6729 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 9.168 | 20.178 | 20078.0432 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531449 [HOLCOMB7 345.00] TO BUS 531448 [HOLCOMB3 115.00] TO BUS 531450 [HOLCTER1 13.800] CKT 1 | 27.2079 | 0.2211 | 121.1011 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.6274 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.2054 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.2054 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.2054 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 21.7433 | 20.4494 | 20349.3806 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.073 | 19.0462 | 18946.2495 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.073 | 24.7101 | 24610.0844 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 33.9465 | 246.8069 | 246706.856 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3318 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4337 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0985 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4757 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4185 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6821 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 13.615 | 45.7967 | 45696.6729 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 13.615 | 22.4462 | 22346.1909 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 13.2783 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 13.2783 | 41.9813 | 41881.3102 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 20.2505 | 21.1157 | 21015.7309 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 20.2505 | 21.0469 | 20946.9324 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 20.2505 | 19.3566 | 19256.6234 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 20.2505 | 18.8806 | 18780.6272 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 9.168 | 20.178 | 20078.0148 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531405 [WALKMYR3 115.00] CKT 1 | 27.2095 | 0.2211 | 121.1083 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 18.295 | 18195.0172 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 18.0296 | 17929.6274 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 19.0602 | 18960.2055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 19.0602 | 18960.2055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 19.0602 | 18960.2055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 21.7433 | 20.4494 | 20349.3807 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.0729 | 19.0454 | 18945.4104 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.0729 | 24.7092 | 24609.2403 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 33.9465 | 246.8066 | 246706.5596 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 13.8103 | 13710.3317 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 12.5214 | 12421.4337 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 11.1991 | 11099.0984 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 9.1705 | 9070.4757 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 8.9024 | 8802.4184 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 12.5059 | 8.6507 | 8550.6821 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 13.615 | 45.7967 | 45696.6729 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 13.615 | 22.4462 | 22346.1909 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 13.2783 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 13.2783 | 41.9813 | 41881.3102 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 20.2505 | 21.1157 | 21015.7311 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 20.2505 | 21.0469 | 20946.9328 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 20.2505 | 19.3566 | 19256.6235 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 20.2505 | 18.8806 | 18780.6275 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 9.168 | 20.178 | 20078.0149 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531512 [HARBNGR7 345.00] TO BUS 523823 [CARPENTER 7345.00] CKT Z1 | 27.2095 | 0.2211 | 121.1083 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 18.3014 | 18201.3513 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 18.3014 | 18201.3513 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 18.3014 | 18201.3513 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 18.0361 | 17936.0558 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 19.0657 | 18965.7477 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 19.0657 | 18965.7477 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 19.0657 | 18965.7477 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.5578 | 20.4538 | 20353.7753 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.3349 | 19.1097 | 19009.7402 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.3349 | 24.8475 | 24747.5134 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 33.9286 | 245.9477 | 245847.7331 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 13.8176 | 13717.6042 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 12.527 | 12427.0439 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 11.2042 | 11104.2203 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 9.1834 | 9083.3834 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 8.9144 | 8814.4428 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.1504 | 8.6619 | 8561.9041 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.6118 | 45.8689 | 45768.8582 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.6118 | 22.4344 | 22334.4097 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.2534 | 26.7483 | 26648.2836 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.2534 | 41.6028 | 41502.8404 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.2509 | 21.1159 | 21015.9301 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.2509 | 21.0473 | 20947.2797 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.2509 | 19.3568 | 19256.8061 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.2509 | 18.881 | 18780.9523 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.1681 | 20.1782 | 20078.1747 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.2099 | 0.2211 | 121.1117 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 18.2943 | 18194.3139 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 18.2943 | 18194.3139 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 18.2943 | 18194.3139 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 18.0289 | 17928.9345 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 19.0596 | 18959.5563 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 19.0596 | 18959.5563 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 19.0596 | 18959.5563 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.7072 | 20.4488 | 20348.8116 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.3382 | 19.1096 | 19009.5705 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.3382 | 24.8479 | 24747.9172 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 33.9415 | 246.6768 | 246576.8453 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 13.8105 | 13710.4531 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 12.5216 | 12421.607 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 11.1993 | 11099.302 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 9.1702 | 9070.2141 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 8.9022 | 8802.1936 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.4593 | 8.6505 | 8550.4911 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.6145 | 45.8 | 45700.0445 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.6145 | 22.4457 | 22345.6566 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.2748 | 26.6699 | 26569.9364 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.2748 | 41.9707 | 41870.7217 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 20.25 | 21.1157 | 21015.6624 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 20.25 | 21.0468 | 20946.7887 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 20.25 | 19.3566 | 19256.5523 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 20.25 | 18.8805 | 18780.4784 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 9.1679 | 20.178 | 20077.9506 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 27.2068 | 0.2211 | 121.1315 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 18.2944 | 18194.3649 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 18.2944 | 18194.3649 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 18.2944 | 18194.3649 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 18.029 | 17928.9858 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 19.0596 | 18959.602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 19.0596 | 18959.602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 19.0596 | 18959.602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.7079 | 20.4488 | 20348.8485 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.3382 | 19.1096 | 19009.57 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.3382 | 24.8479 | 24747.9151 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 33.9414 | 246.6775 | 246577.5005 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 13.8104 | 13710.4458 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 12.5216 | 12421.596 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 11.1993 | 11099.2921 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 9.1702 | 9070.2251 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 8.9022 | 8802.2026 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.4603 | 8.6505 | 8550.4965 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.6145 | 45.8 | 45700.0112 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.6145 | 22.4457 | 22345.6599 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.2749 | 26.67 | 2657002% | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.2749 | 41.9703 | 41870.2988 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 20.25 | 21.1157 | 2101566% | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 20.25 | 21.0468 | 20946.79 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 20.25 | 19.3566 | 19256.5528 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 20.25 | 18.8805 | 18780.4796 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 9.1679 | 20.178 | 20077.9513 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 27.2069 | 0.2211 | 121.1312 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 18.3121 | 18212.0591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 18.3121 | 18212.0591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 18.3121 | 18212.0591 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 18.0469 | 17946.8518 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 19.0751 | 18975.0841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 19.0751 | 18975.0841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 19.0751 | 18975.0841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.4398 | 20.4611 | 20361.0833 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.3362 | 19.1085 | 19008.4928 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.3362 | 24.8454 | 24745.4491 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 33.9407 | 246.702 | 246602.0212 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 13.8248 | 13724.7815 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 12.5312 | 12431.1928 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 11.2093 | 11109.2761 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 9.2018 | 9101.7836 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 8.9306 | 8830.6354 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.1107 | 8.6761 | 8576.1176 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.6082 | 45.9357 | 45835.73 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.6082 | 22.4236 | 22323.6353 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.2115 | 26.9192 | 26819.1765 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.2115 | 40.8403 | 40740.2892 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 20.2496 | 21.1168 | 21016.8404 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 20.2496 | 21.0486 | 20948.5793 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 20.2496 | 19.3575 | 19257.5414 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 20.2496 | 18.882 | 18781.9957 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 9.1681 | 20.1787 | 20078.6985 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 27.1994 | 0.221 | 121.0268 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 18.2932 | 18193.1785 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 18.2932 | 18193.1785 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 18.2932 | 18193.1785 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 18.0278 | 17927.8136 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 19.0584 | 18958.3683 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 19.0584 | 18958.3683 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 19.0584 | 18958.3683 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 21.7326 | 20.4475 | 20347.5038 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.3382 | 19.1096 | 19009.6045 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.3382 | 24.848 | 24747.997 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 33.9419 | 246.7503 | 246650.3423 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 13.809 | 13708.9819 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 12.5206 | 12420.5986 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 11.1986 | 11098.6233 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 9.1666 | 9066.6086 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 8.8988 | 8798.8149 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 12.3529 | 8.6473 | 8547.3174 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.6142 | 45.7985 | 45698.5379 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.6142 | 22.4459 | 22345.9359 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.2763 | 26.6633 | 26563.291 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 13.2763 | 42.0024 | 41902.436 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 20.2502 | 21.1156 | 21015.6015 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 20.2502 | 21.0467 | 20946.6987 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 20.2502 | 19.3565 | 19256.5038 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 20.2502 | 18.8804 | 18780.4046 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 9.168 | 20.178 | 20077.9503 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 533283 [87TH 3 115.00] TO BUS 532818 [87TH 1X1 13.800] CKT 1 | 27.2086 | 0.2211 | 121.1339 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 18.3013 | 18201.3391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 18.3013 | 18201.3391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 18.3013 | 18201.3391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 18.0359 | 17935.9403 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 19.0662 | 18966.2376 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 19.0662 | 18966.2376 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 19.0662 | 18966.2376 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.6658 | 20.4551 | 20355.0944 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.3036 | 19.1109 | 19010.948 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.3036 | 24.8447 | 24744.6937 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 33.8744 | 241.6719 | 241571.8844 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 13.8108 | 13710.8171 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 12.5218 | 12421.8434 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 11.1994 | 11099.4371 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 9.1712 | 9071.2014 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 8.9031 | 8803.1196 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.5067 | 8.6514 | 8551.3607 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.6151 | 45.8016 | 45701.6002 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.6151 | 22.4453 | 22345.3498 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.278 | 26.6685 | 26568.4526 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.278 | 41.9765 | 41876.5206 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.2341 | 21.1236 | 21023.5904 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.2341 | 21.0572 | 20957.2461 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.2341 | 19.3626 | 19262.6283 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.2341 | 18.8882 | 18788.1851 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.1669 | 20.18 | 20079.9717 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.8877 | 0.2209 | 120.9256 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 18.2943 | 18194.2936 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 18.2943 | 18194.2936 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 18.2943 | 18194.2936 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 18.0289 | 17928.9129 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 19.0595 | 18959.4787 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 19.0595 | 18959.4787 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 19.0595 | 18959.4787 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.7421 | 20.4486 | 20348.6327 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.3376 | 19.1091 | 19009.1024 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.3376 | 24.8469 | 24746.9376 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 33.9372 | 246.6964 | 246596.4375 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 13.8102 | 13710.1869 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 12.5213 | 12421.3117 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 11.199 | 11098.9978 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 9.1703 | 9070.2549 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 8.9022 | 8802.2057 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.5058 | 8.6505 | 8550.4767 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.6148 | 45.7967 | 45696.6916 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.6148 | 22.4462 | 22346.1929 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.2782 | 26.6674 | 26567.3598 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.2782 | 41.9817 | 41881.7318 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 20.2497 | 21.1154 | 21015.4297 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 20.2497 | 21.0464 | 20946.3671 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 20.2497 | 19.3563 | 19256.3368 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 20.2497 | 18.8801 | 18780.0768 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.1679 | 20.1779 | 20077.8909 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 27.2036 | 0.2212 | 121.2302 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 18.2943 | 18194.3481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 18.2943 | 18194.3481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 18.2943 | 18194.3481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 18.029 | 17928.9674 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 19.0595 | 18959.5329 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 19.0595 | 18959.5329 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 19.0595 | 18959.5329 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.7422 | 20.4487 | 20348.6879 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.3376 | 19.1091 | 19009.1264 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.3376 | 24.847 | 24746.987 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 33.9374 | 246.6998 | 246599.8376 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 13.8102 | 13710.1988 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 12.5213 | 12421.3217 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 11.199 | 11099.0065 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 9.1703 | 9070.2728 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 8.9022 | 8802.2237 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.5058 | 8.6505 | 8550.4941 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.6148 | 45.7967 | 45696.6975 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.6148 | 22.4462 | 22346.1912 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.2782 | 26.6674 | 26567.3668 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.2782 | 41.9817 | 41881.6974 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 20.2498 | 21.1154 | 21015.4405 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 20.2498 | 21.0464 | 20946.388 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 20.2498 | 19.3563 | 19256.3473 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 20.2498 | 18.8801 | 18780.0974 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.1679 | 20.1779 | 20077.8977 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 27.2041 | 0.2212 | 121.222 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 18.3051 | 18205.1391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 18.3051 | 18205.1391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 18.3051 | 18205.1391 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 18.0398 | 17939.7925 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 19.0697 | 18969.6676 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 19.0697 | 18969.6676 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 19.0697 | 18969.6676 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 21.4709 | 20.458 | 20358.0222 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.3288 | 19.1044 | 19004.3968 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.3288 | 24.8359 | 24735.906 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 33.9363 | 246.5429 | 246442.873 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 13.81 | 13709.9667 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 12.5211 | 12421.0853 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 11.1988 | 11098.8321 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 9.1701 | 9070.1067 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 8.902 | 8802.0322 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 12.4814 | 8.6503 | 8550.2812 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.6108 | 45.8384 | 45738.4079 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.6108 | 22.4395 | 22339.5429 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.2722 | 26.6786 | 26578.6083 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 13.2722 | 41.9286 | 41828.6418 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 20.0303 | 21.1737 | 21073.7008 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 20.0303 | 21.1199 | 21019.939 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 20.0303 | 19.3989 | 19298.8876 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 20.0303 | 18.9302 | 18830.2473 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 9.1526 | 20.1807 | 20080.7273 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 510380 [DELWARE7 345.00] CKT 1 | 26.6757 | 0.2218 | 121.7817 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 18.2936 | 18193.5516 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 18.2936 | 18193.5516 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 18.2936 | 18193.5516 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 18.0283 | 17928.2963 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 19.0581 | 18958.1383 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 19.0581 | 18958.1383 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 19.0581 | 18958.1383 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 21.6963 | 20.4463 | 20346.2842 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.3335 | 19.1112 | 19011.2213 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.3335 | 24.85 | 24749.9906 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 33.9394 | 246.0966 | 245996.575 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 13.8095 | 13709.4524 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 12.5207 | 12420.6861 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 11.1985 | 11098.486 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 9.1692 | 9069.1817 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 8.9012 | 8801.1648 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 12.5042 | 8.6495 | 8549.465 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.6132 | 45.8187 | 45718.7193 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.6132 | 22.4427 | 22342.687 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.2771 | 26.671 | 26570.9806 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 13.2771 | 41.9649 | 41864.8864 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 20.0911 | 21.1735 | 21073.4628 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 20.0911 | 21.1178 | 21017.8273 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 20.0911 | 19.3983 | 19298.3371 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 20.0911 | 18.9275 | 18827.5357 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 9.1581 | 20.1847 | 20084.728 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532777 [G17-009-TAP 345.00] CKT 1 | 27.1142 | 0.2224 | 122.402 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 18.2962 | 18196.2272 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 18.2962 | 18196.2272 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 18.2962 | 18196.2272 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 18.0308 | 17930.7948 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 19.0616 | 18961.5858 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 19.0616 | 18961.5858 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 19.0616 | 18961.5858 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.7508 | 20.4511 | 20351.0764 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.3388 | 19.1099 | 19009.9332 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.3388 | 24.8488 | 24748.7963 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 33.9422 | 246.7698 | 246669.7988 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 13.8117 | 13711.7391 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 12.5226 | 12422.6279 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 11.2001 | 11100.0845 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 9.1725 | 9072.5469 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 8.9044 | 8804.4245 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.5081 | 8.6526 | 855263% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.6169 | 45.7928 | 45692.7837 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.6169 | 22.4467 | 2234667% | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.2784 | 26.667 | 26566.9503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.2784 | 41.9838 | 41883.7727 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 20.2643 | 21.1185 | 21018.5046 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 20.2643 | 21.0528 | 20952.7882 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 20.2643 | 19.3595 | 19259.4866 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 20.2643 | 18.8867 | 18786.6929 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 9.1701 | 20.1808 | 20080.804 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 27.2313 | 0.2206 | 120.6277 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 18.2915 | 18191.5255 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 18.2915 | 18191.5255 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 18.2915 | 18191.5255 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 18.0262 | 17926.2059 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 19.0566 | 18956.5916 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 19.0566 | 18956.5916 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 19.0566 | 18956.5916 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.7186 | 20.4455 | 20345.4824 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.3377 | 19.1094 | 19009.3537 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.3377 | 24.8474 | 24747.4121 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 33.9413 | 246.7475 | 246647.5408 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 13.8096 | 13709.6361 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 12.5208 | 12420.8459 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 11.1986 | 11098.6141 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 9.1694 | 9069.4362 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 8.9014 | 8801.4135 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.5043 | 8.6497 | 8549.7101 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.6144 | 45.7977 | 45697.6598 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.6144 | 22.4461 | 22346.0712 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.2769 | 26.6683 | 26568.2668 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.2769 | 41.9777 | 41877.7476 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 19.9606 | 21.2683 | 21168.2574 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 19.9606 | 21.2597 | 21159.6774 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 19.9606 | 19.4752 | 19375.183 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 19.9606 | 19.0431 | 18943.1406 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 9.1621 | 20.1947 | 20094.7412 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 27.1466 | 0.2218 | 121.7723 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 18.2971 | 18197.1473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 18.2971 | 18197.1473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 18.2971 | 18197.1473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 18.0317 | 17931.6923 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 19.0626 | 18962.6488 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 19.0626 | 18962.6488 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 19.0626 | 18962.6488 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.7027 | 20.4524 | 20352.406 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.3337 | 19.112 | 19012.0463 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.3337 | 24.8504 | 24750.3997 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 33.9222 | 245.1635 | 245063.5202 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 13.8109 | 13710.9137 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 12.5219 | 12421.9303 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 11.1995 | 11099.5096 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 9.1713 | 9071.316 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 8.9032 | 8803.2342 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.5058 | 8.6515 | 8551.4742 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.6146 | 45.8021 | 45702.1229 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.6146 | 22.4453 | 22345.2771 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.2767 | 26.6674 | 26567.352 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.2767 | 41.9822 | 41882.2255 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 20.1086 | 21.1568 | 21056.8374 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 20.1086 | 21.103 | 21003.0015 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 20.1086 | 19.3882 | 19288.1913 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 20.1086 | 18.9227 | 18822.6596 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 9.1593 | 20.184 | 20084.0478 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 27.1525 | 0.2203 | 120.3322 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 18.3012 | 18201.1695 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 18.3012 | 18201.1695 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 18.3012 | 18201.1695 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 18.0358 | 17935.8257 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 19.0657 | 18965.6664 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 19.0657 | 18965.6664 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 19.0657 | 18965.6664 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 21.6537 | 20.4538 | 20353.8406 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.3289 | 19.1071 | 19007.063 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.3289 | 24.84 | 24740.0441 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 33.9247 | 244.607 | 244506.999 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 13.8101 | 13710.1317 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 12.5212 | 12421.2202 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 11.1989 | 11098.9325 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 9.1704 | 9070.3914 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 8.9023 | 8802.3075 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 12.4935 | 8.6505 | 8550.5477 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.6137 | 45.8089 | 45708.9377 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.6137 | 22.4442 | 22344.2397 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.2767 | 26.6734 | 26573.3751 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 13.2767 | 41.9526 | 41852.5982 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 20.234 | 21.1177 | 21017.6853 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 20.234 | 21.048 | 20948.0292 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 20.234 | 19.3576 | 19257.6379 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 20.234 | 18.8803 | 18780.2641 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 9.1664 | 20.1771 | 20077.1355 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15-052T 345.00] CKT 1 | 26.9979 | 0.2219 | 121.8929 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 18.2946 | 18194.5641 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 18.2946 | 18194.5641 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 18.2946 | 18194.5641 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 18.0292 | 17929.1789 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 19.0598 | 18959.7643 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 19.0598 | 18959.7643 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 19.0598 | 18959.7643 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.7416 | 20.4489 | 20348.9496 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.3381 | 19.1096 | 19009.619 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.3381 | 24.8479 | 24747.9054 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 33.9389 | 246.6645 | 246564.5358 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 13.8103 | 13710.2682 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 12.5214 | 12421.3802 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 11.1991 | 11099.055 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 9.1704 | 9070.3761 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 8.9023 | 8802.3236 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.5058 | 8.6506 | 8550.5905 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.6148 | 45.7967 | 45696.6597 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.6148 | 22.4462 | 22346.1987 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.2781 | 26.6673 | 26567.3488 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.2781 | 41.9818 | 41881.7724 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 20.2496 | 21.1155 | 21015.5148 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 20.2496 | 21.0466 | 20946.5772 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 20.2496 | 19.3564 | 19256.429 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 20.2496 | 18.8803 | 18780.3023 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 9.1679 | 20.1779 | 20077.9096 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 27.2029 | 0.2212 | 121.1621 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 18.2946 | 18194.6001 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 18.2946 | 18194.6001 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 18.2946 | 18194.6001 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 18.0292 | 17929.214 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 19.0598 | 18959.7989 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 19.0598 | 18959.7989 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 19.0598 | 18959.7989 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.7418 | 20.449 | 20348.9836 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.3381 | 19.1096 | 19009.6065 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.3381 | 24.8479 | 24747.8896 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 33.9392 | 246.6709 | 246570.9198 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 13.8103 | 13710.2738 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 12.5214 | 12421.3855 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 11.1991 | 11099.0588 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 9.1704 | 9070.3853 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 8.9023 | 8802.3324 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.5058 | 8.6506 | 8550.5991 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.6148 | 45.7967 | 45696.6624 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.6148 | 22.4462 | 22346.1979 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.2781 | 26.6674 | 26567.3561 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.2781 | 41.9817 | 41881.7361 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 20.2497 | 21.1155 | 21015.5287 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 20.2497 | 21.0466 | 20946.5985 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 20.2497 | 19.3564 | 19256.4411 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 20.2497 | 18.8803 | 18780.3204 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 9.1679 | 20.1779 | 20077.9146 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 27.2034 | 0.2212 | 121.1587 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 18.2948 | 18194.7805 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 18.2948 | 18194.7805 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 18.2948 | 18194.7805 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 18.0294 | 17929.3913 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 19.06 | 18959.9907 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 19.06 | 18959.9907 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 19.06 | 18959.9907 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.7412 | 20.4492 | 20349.1981 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.3384 | 19.1099 | 19009.8959 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.3384 | 24.8485 | 24748.4964 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 33.9425 | 246.6964 | 246596.373 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 13.8103 | 13710.3296 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 12.5214 | 12421.4322 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 11.1991 | 11099.0977 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 9.1705 | 9070.4704 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 8.9024 | 8802.4143 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.5058 | 8.6507 | 8550.6782 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.6149 | 45.7967 | 45696.6825 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.6149 | 22.4462 | 22346.1918 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.2782 | 26.6674 | 26567.4022 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.2782 | 41.9815 | 41881.5242 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 20.2506 | 21.1159 | 21015.9333 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 20.2506 | 21.0473 | 20947.3103 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 20.2506 | 19.3568 | 19256.8101 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 20.2506 | 18.881 | 18780.9867 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 9.168 | 20.178 | 20078.0373 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 27.2026 | 0.2211 | 121.1208 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 18.2849 | 18184.8955 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 18.2849 | 18184.8955 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 18.2849 | 18184.8955 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 18.0199 | 17919.8721 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 19.0487 | 18948.7439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 19.0487 | 18948.7439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 19.0487 | 18948.7439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.6113 | 20.4354 | 20335.4497 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.33 | 19.1055 | 19005.5399 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.33 | 24.8382 | 24738.2124 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 33.9334 | 246.4285 | 246328.4796 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 13.8044 | 13704.396 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 12.5164 | 12416.397 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 11.1949 | 11094.9468 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 9.1617 | 9061.7255 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 8.8939 | 8793.9472 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.4927 | 8.6425 | 8542.471 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.6117 | 45.8257 | 45725.7047 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.6117 | 22.4416 | 22341.6217 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.278 | 26.6683 | 26568.3078 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 13.278 | 41.9768 | 41876.8032 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1903 | 21.1371 | 21037.0615 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1903 | 21.0744 | 20974.3951 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1903 | 19.3726 | 19272.6254 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.1903 | 18.9002 | 18800.166 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.1561 | 20.1891 | 20089.1304 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 14.6975 | 0.2266 | 126.6355 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 18.3742 | 18274.2433 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 18.3742 | 18274.2433 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 18.3742 | 18274.2433 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 18.1099 | 18009.9291 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 19.1336 | 19033.6397 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 19.1336 | 19033.6397 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 19.1336 | 19033.6397 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 18.6704 | 20.5157 | 20415.6975 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.336 | 19.1099 | 19009.9268 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.336 | 24.8479 | 24747.895 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 33.9386 | 246.4881 | 246388.1258 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 13.8146 | 13714.6424 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 12.5249 | 12424.8875 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 11.2022 | 1110218% | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 9.1775 | 9077.5496 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 8.9091 | 880908% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.32 | 8.657 | 8556.9736 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.6121 | 45.8495 | 45749.4671 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.6121 | 22.4376 | 22337.6085 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.2612 | 26.7109 | 26610.9069 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.2612 | 41.7774 | 41677.3739 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2485 | 21.1159 | 21015.8706 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2485 | 21.0469 | 20946.8701 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2485 | 19.3567 | 19256.6568 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2485 | 18.8804 | 18780.3964 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.1676 | 20.1782 | 20078.2091 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 25.7242 | 0.2217 | 121.6768 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 18.283 | 18182.9763 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 18.283 | 18182.9763 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 18.283 | 18182.9763 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 18.0176 | 17917.6244 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 19.049 | 18949.0196 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 19.049 | 18949.0196 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 19.049 | 18949.0196 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 21.7602 | 20.4393 | 20339.3487 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.339 | 19.11 | 19010.0167 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.339 | 24.849 | 24749.016 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 33.9423 | 246.7703 | 246670.2789 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 13.8109 | 13710.8813 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 12.5219 | 12421.9244 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 11.1995 | 11099.5062 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 9.1712 | 9071.1573 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 8.9031 | 8803.0936 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 12.5082 | 8.6513 | 8551.3493 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.6159 | 45.793 | 45692.9919 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.6159 | 22.4467 | 22346.7296 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.2784 | 26.6654 | 26565.3752 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 13.2784 | 41.9917 | 41891.6779 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 20.2527 | 21.1157 | 21015.7068 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 20.2527 | 21.0473 | 20947.27 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 20.2527 | 19.3567 | 19256.6987 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 20.2527 | 18.8811 | 18781.1317 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 9.1686 | 20.1787 | 20078.7247 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532802 [WAVERTX7 345.00] TO BUS 532954 [WAVERTX1 34.500] TO BUS 532961 [WAVETV 1 13.800] CKT 1 | 27.2551 | 0.2207 | 120.6958 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 18.2957 | 18195.6737 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 18.2957 | 18195.6737 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 18.2957 | 18195.6737 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 18.0303 | 17930.2657 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 19.0609 | 18960.934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 19.0609 | 18960.934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 19.0609 | 18960.934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 21.7446 | 20.4502 | 20350.2476 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.3374 | 19.1092 | 19009.2107 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.3374 | 24.8471 | 24747.057 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 33.941 | 246.7306 | 246630.5838 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 13.8112 | 13711.198 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 12.5222 | 12422.1621 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 11.1997 | 11099.7025 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 9.1718 | 9071.7798 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 8.9037 | 8803.6766 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 12.5022 | 8.6519 | 8551.8975 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.6145 | 45.799 | 45699.0198 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.6145 | 22.4458 | 22345.8135 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.1494 | 26.7118 | 26611.8076 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 13.1494 | 41.8172 | 41717.2286 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 20.2502 | 21.1184 | 21018.3969 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 20.2502 | 21.0529 | 20952.8616 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 20.2502 | 19.3589 | 19258.859 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 20.2502 | 18.8861 | 18786.0855 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 9.1541 | 20.1763 | 20076.2884 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532934 [MARMTNE5 161.00] CKT Z1 | 27.1833 | 0.221 | 120.9945 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 18.2949 | 18194.8733 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 18.2949 | 18194.8733 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 18.2949 | 18194.8733 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 18.0295 | 17929.4832 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 19.0601 | 18960.0777 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 19.0601 | 18960.0777 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 19.0601 | 18960.0777 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.7418 | 20.4493 | 20349.2754 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.3378 | 19.1094 | 19009.3879 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.3378 | 24.8475 | 24747.4925 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 33.941 | 246.7418 | 246641.7783 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 13.8107 | 13710.6531 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 12.5217 | 12421.706 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 11.1993 | 11099.3249 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 9.171 | 9070.9501 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 8.9029 | 8802.8783 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.5046 | 8.6511 | 8551.1267 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.6146 | 45.7978 | 45697.7613 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.6146 | 22.446 | 22346.0249 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.2579 | 26.6863 | 26586.2575 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.2579 | 41.898 | 41797.9537 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 20.2316 | 21.108 | 21007.9754 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 20.2316 | 21.0353 | 20935.256 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 20.2316 | 19.35 | 19249.9758 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 20.2316 | 18.8706 | 18770.5569 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 9.1649 | 20.1745 | 20074.5311 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 27.21 | 0.2211 | 121.1172 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 18.3047 | 18204.6686 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 18.3047 | 18204.6686 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 18.3047 | 18204.6686 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 18.0392 | 17939.2262 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 19.0696 | 18969.5688 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 19.0696 | 18969.5688 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 19.0696 | 18969.5688 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6493 | 20.4585 | 20358.5082 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.3377 | 19.1097 | 19009.6737 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.3377 | 24.848 | 24747.9707 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 33.9417 | 246.6909 | 246590.9441 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 13.8113 | 13711.2728 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 12.5222 | 12422.2074 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 11.1997 | 11099.7467 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 9.172 | 9071.9741 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 8.9039 | 8803.8515 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.4975 | 8.6521 | 8552.0553 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.6149 | 45.8047 | 45704.7143 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.6149 | 22.4448 | 22344.8394 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.2744 | 26.67 | 26570.0287 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.2744 | 41.9704 | 41870.3771 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 14.3641 | 22.8265 | 22726.4961 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 14.3641 | 23.3744 | 23274.3692 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 14.3641 | 20.5348 | 20434.7653 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 14.3641 | 20.3762 | 20276.2348 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.0767 | 20.229 | 20129.0469 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532937 [NEOSHO 5 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 27.0505 | 0.2206 | 120.6341 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 18.2952 | 18195.1585 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 18.2952 | 18195.1585 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 18.2952 | 18195.1585 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 18.0298 | 17929.7662 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 19.0604 | 18960.3733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 19.0604 | 18960.3733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 19.0604 | 18960.3733 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 21.7313 | 20.4496 | 20349.5977 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.337 | 19.1089 | 19008.9487 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.337 | 24.8465 | 24746.4803 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 33.9407 | 246.7327 | 246632.7416 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 13.8103 | 13710.3401 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 12.5214 | 12421.4407 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 11.1991 | 11099.1056 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 9.1705 | 9070.4867 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 8.9024 | 8802.4293 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 12.5048 | 8.6507 | 8550.692 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.6146 | 45.7984 | 45698.3898 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.6146 | 22.4459 | 22345.9262 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.2775 | 26.6669 | 26566.8842 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 13.2775 | 41.9844 | 41884.364 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 20.174 | 21.1199 | 21019.9299 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 20.174 | 21.0521 | 20952.1276 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 20.174 | 19.3588 | 19258.8311 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 20.174 | 18.883 | 18782.9677 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 9.164 | 20.1777 | 20077.7249 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533008 [TV1MNDV4 138.00] CKT 1 | 27.1859 | 0.2211 | 121.1078 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 18.2932 | 18193.1729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 18.2932 | 18193.1729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 18.2932 | 18193.1729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 18.0278 | 17927.8076 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 19.0584 | 18958.3641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 19.0584 | 18958.3641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 19.0584 | 18958.3641 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.736 | 20.4475 | 20347.5014 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.338 | 19.1095 | 19009.5232 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.338 | 24.8478 | 24747.8015 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 33.9418 | 246.7543 | 246654.2866 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 13.8101 | 13710.119 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 12.5213 | 12421.2546 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 11.199 | 11098.9513 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 9.1702 | 9070.1505 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 8.9021 | 8802.1057 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.5055 | 8.6504 | 8550.3801 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.6146 | 45.7965 | 45696.5311 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.6146 | 22.4462 | 22346.2423 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.2783 | 26.6668 | 26566.8225 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.2783 | 41.9844 | 41884.3676 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 20.2035 | 21.0867 | 20986.6977 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 20.2035 | 21.0059 | 20905.9271 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 20.2035 | 19.3323 | 19232.3218 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 20.2035 | 18.8466 | 18746.6445 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 9.1673 | 20.1763 | 20076.255 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 27.191 | 0.2213 | 121.3301 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 18.2948 | 18194.7944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 18.2948 | 18194.7944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 18.2948 | 18194.7944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 18.0294 | 17929.407 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 19.06 | 18959.9888 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 19.06 | 18959.9888 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 19.06 | 18959.9888 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 21.7425 | 20.4492 | 20349.1695 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.3379 | 19.1095 | 19009.4749 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.3379 | 24.8477 | 24747.693 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 33.9414 | 246.7524 | 246652.4236 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 13.8103 | 13710.3026 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 12.5214 | 12421.4093 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 11.1991 | 11099.0784 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 9.1704 | 9070.4304 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 8.9024 | 8802.3756 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 12.5059 | 8.6506 | 8550.6407 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.6149 | 45.7967 | 45696.6589 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.6149 | 22.4462 | 22346.1924 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.278 | 26.6683 | 26568.3191 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 13.278 | 41.9771 | 41877.0683 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 20.2501 | 21.1157 | 21015.7481 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 20.2501 | 21.0468 | 20946.8243 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 20.2501 | 19.3566 | 19256.6056 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 20.2501 | 18.8805 | 18780.4603 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 9.1648 | 20.1809 | 20080.9421 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] TO BUS 532710 [NSES 2X1 13.200] CKT 1 | 27.207 | 0.2211 | 121.1351 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 18.293 | 18192.9773 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 18.293 | 18192.9773 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 18.293 | 18192.9773 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 18.0276 | 17927.6302 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 19.0581 | 18958.0826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 19.0581 | 18958.0826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 19.0581 | 18958.0826 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.7271 | 20.4471 | 20347.0726 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.3373 | 19.1092 | 19009.1624 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.3373 | 24.847 | 24746.9536 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 33.9406 | 246.7285 | 24662847% | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 13.8097 | 13709.6801 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 12.5209 | 1242088% | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 11.1986 | 11098.6448 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 9.1695 | 9069.5019 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 8.9015 | 8801.4772 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.5046 | 8.6498 | 8549.7712 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.6147 | 45.7972 | 45697.1628 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.6147 | 22.4461 | 22346.129 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.2778 | 26.6718 | 26571.8475 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.2778 | 41.9598 | 41859.7509 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 20.2462 | 21.1189 | 21018.8983 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 20.2462 | 21.0509 | 20950.9074 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 20.2462 | 19.359 | 19259.03 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 20.2462 | 18.8835 | 18783.4607 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 9.1678 | 20.1792 | 20079.1804 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 27.1464 | 0.2216 | 121.6401 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9964 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 18.0296 | 17929.6071 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.183 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.183 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.183 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.7433 | 20.4494 | 20349.3548 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4755 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.6962 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 33.9415 | 246.7523 | 246652.2597 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3386 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4388 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1031 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4852 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4284 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6917 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.6149 | 45.7967 | 45696.6946 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.6149 | 22.4462 | 22346.1886 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.2782 | 26.6674 | 26567.4434 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.2782 | 41.9813 | 41881.3275 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 20.2503 | 21.1157 | 21015.672 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 20.2503 | 21.0468 | 20946.8237 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 20.2503 | 19.3566 | 19256.5695 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 20.2503 | 18.8805 | 18780.5223 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 9.168 | 20.178 | 20077.9724 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 27.2091 | 0.2211 | 121.1213 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0006 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0006 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0006 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 18.0296 | 17929.6113 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1863 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7432 | 20.4494 | 20349.3596 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.3368 | 19.1088 | 19008.8216 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.3368 | 24.8467 | 24746.6656 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 9.2485 | 3.186 | 3086.0177 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.332 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.433 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0984 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4758 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4193 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6828 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.6149 | 45.7966 | 45696.6402 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1942 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.2782 | 26.6674 | 26567.444 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.3081 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 21.1157 | 21015.7066 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 21.0469 | 20946.887 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 19.3566 | 19256.602 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 18.8806 | 18780.5836 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9926 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539642 [ELLSWTP3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 27.209 | 0.2211 | 121.1173 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0446 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0446 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 18.295 | 18195.0446 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 18.0297 | 17929.6546 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2282 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2282 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 19.0602 | 18960.2282 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 21.7431 | 20.4494 | 20349.3982 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.3353 | 19.1093 | 19009.3246 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.3353 | 24.847 | 24747.044 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 26.4068 | 21.5176 | 21417.6417 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 13.8104 | 13710.3617 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 12.5215 | 12421.458 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 11.1991 | 11099.1186 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 9.1705 | 9070.524 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 8.9025 | 8802.4646 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 12.5058 | 8.6507 | 8550.7269 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.7081 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1819 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.5039 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 13.2782 | 41.981 | 41881.0256 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.6765 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8257 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5716 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5219 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9794 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539643 [ROLLHLS3 115.00] TO BUS 539660 [EHALLTP3 115.00] CKT 1 | 27.2089 | 0.2211 | 121.1187 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.6061 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1815 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 21.7433 | 20.4494 | 20349.3535 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.3372 | 19.1093 | 19009.2571 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.3372 | 24.8472 | 24747.2293 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 25.7897 | 25.0224 | 24922.4302 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3207 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4241 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0906 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4589 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4029 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6669 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.6922 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1894 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.453 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.2792 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.6773 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8321 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5729 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5296 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9743 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539644 [COVERT 3 115.00] TO BUS 539693 [SMITH-C3 115.00] CKT 1 | 27.2091 | 0.2211 | 121.1207 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0017 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0017 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 18.295 | 18195.0017 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 18.0296 | 17929.6125 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1878 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1878 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1878 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.7432 | 20.4494 | 20349.3591 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.3364 | 19.1089 | 19008.9337 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.3364 | 24.8468 | 24746.7662 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 33.0639 | 200.9901 | 200890.0559 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3327 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4344 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0996 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4773 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4209 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6843 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.6928 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1865 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.4535 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.2768 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.6749 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8258 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5708 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5251 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 9.168 | 20.178 | 20077.974 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 27.2091 | 0.2211 | 121.121 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.615 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.191 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.191 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.191 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.7433 | 20.4494 | 20349.3633 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.3377 | 19.1092 | 19009.2204 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.3377 | 24.8473 | 24747.3126 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 33.9135 | 250.6697 | 250569.7109 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3419 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4423 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.106 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4914 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4336 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6975 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.6971 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1879 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.3104 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8278 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5709 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5256 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9743 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 27.2092 | 0.2211 | 121.1203 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 33.9415 | 246.7522 | 246652.2293 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0008 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0008 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 18.295 | 18195.0008 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.6116 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.7433 | 20.4494 | 2034936% | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.3377 | 19.1093 | 19009.2889 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.3377 | 24.8473 | 2474729% | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 33.9073 | 247.1654 | 247065.3638 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3328 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4338 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.099 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4768 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4202 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6838 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.663 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1914 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.4502 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.2937 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 20.2503 | 21.1157 | 21015.6732 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 20.2503 | 21.0468 | 20946.8249 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 20.2503 | 19.3566 | 19256.5695 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 20.2503 | 18.8805 | 18780.5232 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9737 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 27.2091 | 0.2211 | 121.1208 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 18.295 | 18194.9839 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 18.0296 | 17929.5952 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1675 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1675 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 19.0602 | 18960.1675 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.7432 | 20.4493 | 20349.3369 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.3374 | 19.1091 | 19009.0835 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.3374 | 24.847 | 24746.9647 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 33.9368 | 248.9998 | 248899.79 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3157 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4201 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0872 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4526 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.3961 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6604 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.7246 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.1828 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.2924 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 20.2502 | 21.1157 | 21015.6538 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 20.2502 | 21.0468 | 20946.7887 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 20.2502 | 19.3566 | 19256.5517 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 20.2502 | 18.8805 | 18780.4877 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 9.168 | 20.1779 | 20077.9384 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 27.2088 | 0.2211 | 121.1291 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 18.295 | 18194.9661 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 18.295 | 18194.9661 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 18.295 | 18194.9661 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 18.0296 | 17929.5778 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 19.0601 | 18960.1478 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 19.0601 | 18960.1478 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 19.0601 | 18960.1478 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.7431 | 20.4493 | 20349.3137 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.3369 | 19.1089 | 19008.9338 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.3369 | 24.8467 | 24746.718 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 33.9506 | 250.1846 | 250084.6214 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 13.8103 | 13710.2975 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 12.5214 | 12421.4047 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 11.1991 | 11099.0745 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 9.1704 | 9070.4251 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 8.9024 | 8802.3695 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.5058 | 8.6506 | 8550.6347 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.6148 | 45.7968 | 45696.7918 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.6148 | 22.4462 | 22346.1778 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.2782 | 26.6675 | 26567.4568 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.2782 | 41.9813 | 41881.2764 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 20.2502 | 21.1156 | 21015.6345 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 20.2502 | 21.0468 | 20946.7521 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 20.2502 | 19.3565 | 19256.5321 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 20.2502 | 18.8805 | 18780.4516 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 9.1679 | 20.1779 | 20077.9001 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 27.2085 | 0.2211 | 121.1385 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 18.295 | 18195.0051 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 18.0296 | 17929.6159 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1922 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1922 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 19.0602 | 18960.1922 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.7433 | 20.4494 | 20349.3649 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.3379 | 19.1091 | 19009.0562 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.3379 | 24.847 | 24746.9941 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 33.278 | 186.9861 | 186886.1129 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 13.8104 | 13710.3503 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 12.5214 | 12421.4495 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 11.1991 | 11099.1114 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 9.1705 | 9070.503 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 8.9024 | 8802.4457 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.506 | 8.6507 | 8550.7084 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.6149 | 45.7967 | 45696.6682 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.6149 | 22.4462 | 22346.1925 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.2783 | 26.6674 | 26567.4401 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.2783 | 41.9813 | 41881.3271 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 20.2503 | 21.1157 | 21015.6711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 20.2503 | 21.0468 | 20946.8209 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 20.2503 | 19.3566 | 19256.5676 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 20.2503 | 18.8805 | 18780.5194 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 9.168 | 20.178 | 20077.9728 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 27.2092 | 0.2211 | 121.1207 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9974 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9974 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 18.295 | 18194.9974 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 18.0296 | 17929.6083 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1835 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1835 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 19.0602 | 18960.1835 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 21.7433 | 20.4494 | 20349.3545 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.337 | 19.1092 | 19009.2058 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.337 | 24.8471 | 24747.1169 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 25.7581 | 26.5096 | 26409.6234 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 13.8103 | 13710.3237 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 12.5214 | 12421.4265 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 11.1991 | 11099.0925 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 9.1705 | 9070.4638 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 8.9024 | 8802.4076 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 12.5059 | 8.6507 | 8550.6714 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.6149 | 45.7967 | 45696.6947 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.6149 | 22.4462 | 22346.186 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.2782 | 26.6675 | 26567.4565 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 13.2782 | 41.9813 | 41881.262 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 21.1157 | 21015.6858 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 21.0468 | 20946.8483 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 19.3566 | 19256.5813 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 20.2504 | 18.8805 | 18780.5456 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 9.168 | 20.178 | 20077.9806 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539698 [WALDO 3 115.00] TO BUS 539701 [RUSSELL3 115.00] CKT 1 | 27.2091 | 0.2211 | 121.1199 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 18.2948 | 18194.8379 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 18.2948 | 18194.8379 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 18.2948 | 18194.8379 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 18.0295 | 17929.4529 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 19.06 | 18960.009 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 19.06 | 18960.009 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 19.06 | 18960.009 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 21.7425 | 20.4492 | 20349.1507 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.3346 | 19.1075 | 19007.4633 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.3346 | 24.8438 | 24743.8081 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 33.7996 | 479.3197 | 479219.6766 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 13.8101 | 13710.1434 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 12.5213 | 12421.2742 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 11.199 | 11098.9668 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 9.1702 | 9070.1954 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 8.9021 | 8802.1482 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 12.5055 | 8.6504 | 8550.4203 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.6146 | 45.7972 | 45697.1798 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.6146 | 22.4461 | 22346.132 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.2782 | 26.6675 | 26567.4678 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 13.2782 | 41.9812 | 41881.2156 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 20.2498 | 21.1155 | 21015.4939 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 20.2498 | 21.0465 | 20946.4902 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 20.2498 | 19.3564 | 19256.3984 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 20.2498 | 18.8802 | 18780.1976 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 9.1678 | 20.1777 | 20077.6733 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 539703 [RUSSELL1 34.500] TO BUS 539701 [RUSSELL3 115.00] TO BUS 539943 [RUSSEL-T 7.2000] CKT 1 | 27.2066 | 0.2212 | 121.1935 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 18.2953 | 18195.2666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 18.2953 | 18195.2666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 18.2953 | 18195.2666 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 18.0299 | 17929.8769 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 19.0604 | 18960.4342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 19.0604 | 18960.4342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 19.0604 | 18960.4342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.7411 | 20.4496 | 20349.5816 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6992 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 33.9415 | 246.7533 | 246653.3469 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 13.8105 | 13710.455 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 12.5215 | 12421.53 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 11.1992 | 11099.1795 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 9.1707 | 9070.6956 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 8.9026 | 8802.6266 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.5044 | 8.6509 | 8550.8789 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.155 | 52.1232 | 52023.1727 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.155 | 21.6607 | 21560.6803 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.2779 | 26.669 | 26569.0179 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.2779 | 41.9737 | 41873.7151 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 20.2502 | 21.1157 | 21015.7243 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 20.2502 | 21.0469 | 20946.8971 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 20.2502 | 19.3566 | 19256.6096 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 20.2502 | 18.8806 | 18780.5822 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 9.1679 | 20.178 | 20078.0416 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 27.2087 | 0.2211 | 121.119 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 18.2944 | 18194.4473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 18.2944 | 18194.4473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 18.2944 | 18194.4473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 18.0291 | 17929.0719 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 19.0596 | 18959.5885 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 19.0596 | 18959.5885 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 19.0596 | 18959.5885 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.7428 | 20.4487 | 20348.6707 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.3379 | 19.1095 | 19009.4697 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.3379 | 24.8477 | 24747.6834 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 33.9413 | 246.75 | 246650.0335 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 13.8094 | 13709.3882 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 12.5206 | 12420.6359 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 11.1984 | 11098.4394 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 9.1691 | 9069.0754 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 8.9011 | 8801.0651 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.5054 | 8.6494 | 8549.3726 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.5759 | 44.1769 | 44076.9214 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.5759 | 22.7385 | 22638.4922 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.2781 | 26.6672 | 26567.1663 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.2781 | 41.9826 | 41882.5806 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 20.2499 | 21.1155 | 21015.5427 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 20.2499 | 21.0466 | 20946.5756 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 20.2499 | 19.3564 | 19256.4437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 20.2499 | 18.8803 | 18780.2789 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 9.1677 | 20.1776 | 20077.5808 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 27.208 | 0.2212 | 121.1566 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 18.2954 | 18195.4436 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 18.2954 | 18195.4436 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 18.2954 | 18195.4436 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 18.0301 | 17930.0571 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 19.0606 | 1896058% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 19.0606 | 18960.5779 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 19.0606 | 1896058% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.7391 | 20.4497 | 20349.6746 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4694 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6799 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 33.9414 | 246.7505 | 246650.4724 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 13.8104 | 13710.3627 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 12.5214 | 12421.4411 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 11.1991 | 11099.1073 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 9.1706 | 9070.613 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 8.9025 | 8802.5394 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.5027 | 8.6508 | 8550.7882 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.6202 | 80.9164 | 80816.4319 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.6202 | 20.2231 | 20123.0878 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 13.2776 | 26.6711 | 26571.0987 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 13.2776 | 41.9636 | 41863.5603 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 20.25 | 21.1157 | 21015.6818 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 20.25 | 21.0468 | 20946.8001 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 20.25 | 19.3566 | 19256.5637 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 20.25 | 18.8805 | 18780.4771 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 9.1678 | 20.1779 | 20077.8657 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 27.2079 | 0.2211 | 121.1352 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9656 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9656 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9656 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 18.0296 | 17929.5785 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 19.0601 | 18960.1449 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 19.0601 | 18960.1449 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 19.0601 | 18960.1449 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.7433 | 20.4493 | 20349.3021 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.338 | 19.1095 | 19009.4837 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.338 | 24.8477 | 24747.7152 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 33.9415 | 246.7533 | 246653.3002 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 13.8102 | 13710.2288 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 12.5213 | 12421.3458 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 11.199 | 11099.0257 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 9.1703 | 9070.3282 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 8.9023 | 8802.2753 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.5059 | 8.6505 | 8550.5431 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.5944 | 45.5062 | 45406.1714 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.5944 | 22.4977 | 22397.7079 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.2782 | 26.6676 | 26567.5615 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.2782 | 41.9807 | 41880.7176 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 20.2504 | 21.1157 | 21015.6872 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 20.2504 | 21.0469 | 20946.8503 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 20.2504 | 19.3566 | 19256.5824 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 20.2504 | 18.8805 | 18780.5473 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 9.168 | 20.178 | 20077.9967 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 27.2092 | 0.2211 | 121.119 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 18.295 | 18194.9895 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 18.295 | 18194.9895 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 18.295 | 18194.9895 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 18.0296 | 17929.6009 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 19.0602 | 18960.1726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 19.0602 | 18960.1726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 19.0602 | 18960.1726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.743 | 20.4493 | 20349.34 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.3379 | 19.1095 | 19009.4742 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.3379 | 24.8477 | 24747.6947 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 33.9413 | 246.7521 | 246652.1427 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 13.8103 | 13710.3061 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 12.5214 | 12421.412 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 11.1991 | 11099.0809 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 9.1704 | 9070.4382 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 8.9024 | 8802.3829 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.5057 | 8.6506 | 8550.6476 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.5985 | 45.3649 | 45264.9109 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.5985 | 22.5213 | 22421.279 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.278 | 26.6675 | 26567.4761 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.278 | 41.9811 | 41881.1467 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 20.2502 | 21.1157 | 21015.6795 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 20.2502 | 21.0468 | 20946.8341 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 20.2502 | 19.3566 | 19256.5747 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 20.2502 | 18.8805 | 18780.5326 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 9.1679 | 20.178 | 20077.9832 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 27.2088 | 0.2211 | 121.1213 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 18.2957 | 18195.6623 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 18.2957 | 18195.6623 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 18.2957 | 18195.6623 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 18.0303 | 17930.2779 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 19.0608 | 18960.7679 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 19.0608 | 18960.7679 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 19.0608 | 18960.7679 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.74 | 20.4498 | 20349.8211 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.3381 | 19.1096 | 19009.5839 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.9461 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 33.9417 | 246.7539 | 246653.8616 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 13.8103 | 13710.3312 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 12.5214 | 12421.3934 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 11.1991 | 11099.0709 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 9.1707 | 9070.6719 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 8.9026 | 8802.5829 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.5016 | 8.6508 | 8550.8174 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.0128 | 55.9931 | 55893.0549 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.0128 | 21.315 | 21215.046 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.2776 | 26.6731 | 26573.1072 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.2776 | 41.9537 | 41853.7381 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 20.2506 | 21.1158 | 21015.763 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 20.2506 | 21.047 | 20946.994 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 20.2506 | 19.3567 | 19256.656 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 20.2506 | 18.8807 | 18780.6877 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 9.168 | 20.1781 | 20078.1088 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 27.2103 | 0.2211 | 121.0848 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.503 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.503 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 18.2955 | 18195.503 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 18.0301 | 17930.1118 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 19.0607 | 18960.6668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 19.0607 | 18960.6668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 19.0607 | 18960.6668 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 21.7379 | 20.4498 | 20349.8146 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4744 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6909 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 33.9415 | 246.7502 | 246650.1653 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 13.8106 | 13710.593 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 12.5216 | 12421.6473 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 11.1993 | 11099.2796 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 9.1709 | 9070.8922 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 8.9028 | 8802.8162 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 12.5032 | 8.6511 | 8551.0626 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 6.0607 | 17.136 | 17036.0444 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 6.0607 | 12.7933 | 12693.3101 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.2773 | 26.6703 | 26570.299 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 13.2773 | 41.9678 | 41867.839 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2496 | 21.116 | 21015.9871 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2496 | 21.0473 | 20947.2708 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2496 | 19.3568 | 19256.8162 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 20.2496 | 18.8809 | 18780.8707 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 9.1673 | 20.1786 | 20078.5908 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 541217 [WINDSR 5 161.00] TO BUS 764355 [G20-072-TAP 161.00] CKT 1 | 27.206 | 0.2211 | 121.1115 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 18.2987 | 18198.7343 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 18.2987 | 18198.7343 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 18.2987 | 18198.7343 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 18.0335 | 17933.4844 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 19.0641 | 18964.1126 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 19.0641 | 18964.1126 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 19.0641 | 18964.1126 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.185 | 20.4538 | 20353.8145 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.3375 | 19.1093 | 19009.3482 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.3375 | 24.8474 | 24747.3686 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 33.9408 | 246.7171 | 246617.0904 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 14.1883 | 14088.3025 | 138.21 | 151.2 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 12.8331 | 12733.0597 | 138.21 | 151.2 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 11.4786 | 11378.5951 | 148.08 | 162 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 9.7552 | 9655.2474 | 141.5 | 160 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 9.4569 | 9356.8852 | 141.5 | 160 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 5.5633 | 9.1775 | 9077.4533 | 141.5 | 160 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.6149 | 45.7911 | 45691.1155 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.6149 | 22.4472 | 22347.1535 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.2656 | 26.6825 | 26582.5152 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.2656 | 41.9179 | 41817.9037 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2482 | 21.1165 | 21016.5103 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2482 | 21.048 | 20948.0367 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2482 | 19.3572 | 19257.2339 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2482 | 18.8815 | 18781.4835 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 9.1678 | 20.1783 | 20078.2615 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542965 [W.GRDNR7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 27.1849 | 0.2211 | 121.0771 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 18.2908 | 18190.7995 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 18.2908 | 18190.7995 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 18.2908 | 18190.7995 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 18.0255 | 17925.4986 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 19.0558 | 18955.7926 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 19.0558 | 18955.7926 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 19.0558 | 18955.7926 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7176 | 20.4445 | 20344.5418 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.3385 | 19.1098 | 19009.7736 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.3385 | 24.8484 | 24748.3698 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 33.9407 | 246.7415 | 246641.4825 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 13.7965 | 13696.4861 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 12.5097 | 12409.7019 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 11.1894 | 11089.4081 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 9.15 | 9050.008 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 8.8826 | 8782.6176 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.4894 | 8.6315 | 8531.5032 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.6106 | 45.8239 | 45723.8947 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.6106 | 22.442 | 22342.0424 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.0624 | 26.7311 | 26631.1427 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.0624 | 41.8019 | 41701.8578 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2487 | 21.1152 | 21015.162 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2487 | 21.0459 | 20945.8925 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2487 | 19.3561 | 19256.0867 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2487 | 18.8796 | 18779.6228 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 9.1677 | 20.1775 | 20077.5452 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 27.2056 | 0.2212 | 121.209 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 18.2947 | 18194.7073 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 18.2947 | 18194.7073 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 18.2947 | 18194.7073 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 18.0293 | 17929.3183 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 19.0599 | 18959.9127 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 19.0599 | 18959.9127 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 19.0599 | 18959.9127 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 21.7429 | 20.4491 | 20349.1098 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.3376 | 19.1093 | 19009.3379 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.3376 | 24.8474 | 24747.3761 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 33.9411 | 246.7467 | 246646.7086 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 13.8102 | 13710.1934 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 12.5213 | 12421.3372 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 11.199 | 11099.0202 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 9.1702 | 9070.1637 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 8.9021 | 8802.1295 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 12.5054 | 8.6504 | 8550.4139 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.6148 | 45.7962 | 45696.2419 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.6148 | 22.4463 | 22346.2773 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.2785 | 26.6506 | 26550.5959 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 13.2785 | 42.065 | 41965.0044 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 20.2499 | 21.1156 | 21015.5576 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 20.2499 | 21.0466 | 20946.6124 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 20.2499 | 19.3565 | 19256.4596 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 20.2499 | 18.8803 | 18780.3183 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 9.1679 | 20.1778 | 20077.8419 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543054 [CEDARNL5 161.00] CKT 1 | 27.2081 | 0.2211 | 121.1476 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 18.3164 | 18216.3623 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 18.3164 | 1821636% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 18.3164 | 18216.3623 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 18.0511 | 1795107% | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 19.0795 | 18979.4514 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 19.0795 | 18979.4514 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 19.0795 | 18979.4514 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 21.5073 | 20.4657 | 20365.6503 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 13.3442 | 19.1131 | 19013.1058 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 13.3442 | 24.8561 | 24756.0706 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 33.9459 | 246.7721 | 246672.0736 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 13.822 | 13721.9997 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 12.5298 | 12429.7707 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 11.2065 | 11106.4659 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 9.195 | 9095.0146 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 8.9251 | 8825.0776 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.1128 | 8.6716 | 8571.6412 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 13.6106 | 45.9573 | 45857.3167 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 13.6106 | 22.4198 | 22319.8142 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.9214 | 27.748 | 27648.0218 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 12.9214 | 37.8375 | 37737.5346 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 20.2553 | 21.1192 | 21019.2494 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 20.2553 | 21.053 | 20952.9722 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 20.2553 | 19.3598 | 19259.7958 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 20.2553 | 18.8862 | 18786.2043 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 9.1697 | 20.1815 | 20081.459 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543105 [BULLCRK5 161.00] CKT 1 | 27.2164 | 0.2205 | 120.4768 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 18.2874 | 18187.3573 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 18.2874 | 18187.3573 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 18.2874 | 18187.3573 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 18.0221 | 17922.1343 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 19.0521 | 18952.1019 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 19.0521 | 18952.1019 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 19.0521 | 18952.1019 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 21.7204 | 20.4404 | 20340.3506 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.3383 | 19.1097 | 19009.7049 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.3383 | 24.8482 | 24748.2148 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 33.9401 | 246.7304 | 246630.4138 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 13.7894 | 13689.436 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 12.5038 | 12403.8395 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 11.1846 | 11084.576 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 9.139 | 9038.9993 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 8.872 | 8772.0341 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 12.4738 | 8.6213 | 8521.3135 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.6074 | 45.8481 | 45748.053 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.6074 | 22.4383 | 22338.3163 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.129 | 26.523 | 26422.9745 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 13.129 | 42.8128 | 42712.7622 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 20.2489 | 21.1151 | 21015.1122 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 20.2489 | 21.0458 | 20945.8178 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 20.2489 | 19.356 | 19256.0463 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 20.2489 | 18.8796 | 18779.5617 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 9.1677 | 20.1776 | 20077.5683 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543132 [BNSF 5 161.00] CKT 1 | 27.2058 | 0.2212 | 121.223 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 18.2956 | 18195.6256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 18.2956 | 18195.6256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 18.2956 | 18195.6256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 18.0302 | 17930.2372 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 19.0608 | 18960.7673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 19.0608 | 18960.7673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 19.0608 | 18960.7673 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 21.7329 | 20.4499 | 20349.881 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.3374 | 19.1092 | 19009.1764 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.3374 | 24.847 | 24746.9975 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 33.9409 | 246.7348 | 246634.7562 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 13.8113 | 13711.3238 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 12.5222 | 12422.239 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 11.1998 | 11099.7854 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 9.1721 | 9072.0905 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 8.904 | 8803.9542 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 12.4888 | 8.6521 | 8552.1453 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.6144 | 45.8028 | 45702.7502 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.6144 | 22.4452 | 22345.216 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.2637 | 26.6864 | 26586.3869 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 13.2637 | 41.8968 | 41796.8134 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 20.2496 | 21.1155 | 21015.4632 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 20.2496 | 21.0464 | 20946.4154 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 20.2496 | 19.3564 | 19256.3644 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 20.2496 | 18.8801 | 18780.1142 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 9.1678 | 20.1777 | 20077.697 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542966 [WGARDNR5 161.00] TO BUS 543139 [WGARDNR1 34.500] CKT 7 | 27.2067 | 0.2212 | 121.1798 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 18.299 | 18199.0253 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 18.299 | 18199.0253 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 18.299 | 18199.0253 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 18.0341 | 17934.0522 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 19.0633 | 18963.2867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 19.0633 | 18963.2867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 19.0633 | 18963.2867 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.7245 | 20.4512 | 20351.1822 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.3391 | 19.1103 | 19010.3417 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.3391 | 24.8495 | 24749.5459 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 33.937 | 246.6086 | 246508.5811 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 13.8016 | 13701.5802 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 12.5142 | 12414.2008 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 11.1936 | 11093.63 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 9.1559 | 9055.9086 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 8.8883 | 8788.3127 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 12.1013 | 8.637 | 8537.0068 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.5955 | 46.2319 | 46131.8675 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.5955 | 22.3767 | 22276.7016 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.2427 | 26.7171 | 26617.1071 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 13.2427 | 41.756 | 41656.0312 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.2412 | 21.1144 | 21014.3508 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.2412 | 21.044 | 20944.0359 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.2412 | 19.3552 | 19255.182 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 20.2412 | 18.8776 | 18777.5944 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 9.1669 | 20.1765 | 20076.4666 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 541198 [PECULR 7 345.00] CKT 1 | 27.1473 | 0.2219 | 121.8988 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 18.2932 | 18193.2252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 18.2932 | 18193.2252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 18.2932 | 18193.2252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 18.0278 | 17927.8062 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 19.0591 | 18959.1361 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 19.0591 | 18959.1361 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 19.0591 | 18959.1361 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 21.5862 | 20.4495 | 20349.5106 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.3381 | 19.1096 | 19009.5851 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.3381 | 24.8479 | 24747.9364 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 33.9412 | 246.7446 | 246644.5626 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 13.8073 | 13707.3278 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 12.519 | 12419.0309 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 11.1971 | 11097.1451 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 9.1653 | 9065.2683 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 8.8975 | 8797.4612 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 12.4794 | 8.646 | 8545.9536 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.6054 | 45.9515 | 45851.4654 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.6054 | 22.4214 | 22321.3659 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.2613 | 26.7357 | 26635.6917 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 13.2613 | 41.6606 | 41560.6241 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 20.2508 | 21.1158 | 21015.8042 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 20.2508 | 21.0471 | 20947.0735 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 20.2508 | 19.3567 | 19256.6937 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 20.2508 | 18.8808 | 18780.7663 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 9.1681 | 20.1781 | 20078.1255 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543647 [STIL T11 13.800] CKT 11 | 27.2006 | 0.2213 | 121.2549 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 18.2931 | 18193.0888 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 18.2931 | 18193.0888 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 18.2931 | 18193.0888 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 18.0277 | 17927.6683 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 19.0591 | 18959.0515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 19.0591 | 18959.0515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 19.0591 | 18959.0515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 21.5747 | 20.4495 | 20349.5131 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.3381 | 19.1096 | 19009.5942 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.3381 | 24.848 | 24747.9542 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 33.9411 | 246.7435 | 246643.5437 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 13.8071 | 13707.0805 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 12.5188 | 12418.8317 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 11.197 | 11096.9822 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 9.1648 | 9064.8475 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 8.8971 | 8797.0596 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 12.4775 | 8.6456 | 8545.5702 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.6047 | 45.963 | 45863.0264 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.6047 | 22.4195 | 22319.5245 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.2598 | 26.7408 | 26640.78 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 13.2598 | 41.6371 | 41537.1159 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 20.2508 | 21.1158 | 21015.8126 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 20.2508 | 21.0471 | 20947.0881 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 20.2508 | 19.3567 | 19256.7028 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 20.2508 | 18.8808 | 18780.7823 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 9.1681 | 20.1781 | 20078.1347 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542968 [STILWEL7 345.00] TO BUS 542969 [STILWEL5 161.00] TO BUS 543648 [STIL T22 13.800] CKT 22 | 27.1998 | 0.2213 | 121.2654 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 18.2757 | 18175.7429 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 18.2757 | 18175.7429 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 18.2757 | 18175.7429 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 18.0108 | 17910.8263 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 19.0405 | 18940.4536 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 19.0405 | 18940.4536 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 19.0405 | 18940.4536 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 21.0942 | 20.4285 | 20328.4511 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.3416 | 19.1117 | 19011.6938 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.3416 | 24.8527 | 24752.733 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 33.9406 | 246.769 | 246668.9676 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 13.9344 | 13834.4183 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 12.6289 | 12528.88 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 11.2968 | 11196.8111 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 9.3303 | 9230.2605 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 9.0562 | 8956.1988 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 8.1989 | 8.7989 | 8698.8923 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.6029 | 45.8204 | 45720.3978 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.6029 | 22.4433 | 22343.2645 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.2611 | 26.6579 | 26557.8599 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 13.2611 | 42.0312 | 41931.1995 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2425 | 21.1141 | 21014.0719 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2425 | 21.0438 | 20943.7575 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2425 | 19.355 | 19255.0021 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 20.2425 | 18.8775 | 18777.4682 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 9.1669 | 20.1767 | 20076.6748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542977 [CRAIG 7 345.00] TO BUS 542940 [ATLNTIC7 345.00] CKT 1 | 27.1614 | 0.2217 | 121.7354 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 18.293 | 18193.0252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 18.293 | 18193.0252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 18.293 | 18193.0252 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 18.0277 | 17927.6792 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 19.0581 | 18958.0838 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 19.0581 | 18958.0838 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 19.0581 | 18958.0838 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 21.7439 | 20.447 | 20346.9947 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.338 | 19.1095 | 19009.4783 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.338 | 24.8477 | 24747.7021 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 33.941 | 246.7479 | 246647.8701 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 13.8015 | 13701.4574 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 12.514 | 12413.9583 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 11.1929 | 11092.9104 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 9.1571 | 9057.1477 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 8.8896 | 8789.5559 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 12.5073 | 8.6383 | 8538.2521 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.613 | 45.7969 | 45696.8878 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.613 | 22.4463 | 22346.3308 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.2795 | 26.6624 | 26562.4032 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 13.2795 | 42.005 | 41905.0025 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 20.2502 | 21.1156 | 21015.5849 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 20.2502 | 21.0467 | 20946.6707 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 20.2502 | 19.3565 | 19256.489 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 20.2502 | 18.8804 | 18780.3791 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 9.168 | 20.1779 | 2007791% | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542945 [CRAIG_CAP 5 161.00] CKT R | 27.2091 | 0.2211 | 121.1342 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 18.2931 | 1819313% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 18.2931 | 18193.1322 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 18.2931 | 18193.1322 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 18.0278 | 17927.7765 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 19.0583 | 18958.2608 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 19.0583 | 18958.2608 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 19.0583 | 18958.2608 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 21.7352 | 20.4473 | 20347.291 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.484 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.7079 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 33.9408 | 246.7361 | 246636.0676 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 13.8131 | 13713.0878 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 12.5239 | 12423.9246 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 11.2013 | 11101.256 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 9.1736 | 9073.6202 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 8.9055 | 8805.5323 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 12.4373 | 8.6538 | 8553.7638 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.6115 | 45.8263 | 45726.2752 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.6115 | 22.4415 | 22341.5492 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.2754 | 26.6575 | 26557.4984 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 13.2754 | 42.0314 | 41931.3698 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 20.2501 | 21.1156 | 21015.6006 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 20.2501 | 21.0467 | 20946.6981 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 20.2501 | 19.3565 | 19256.5032 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 20.2501 | 18.8804 | 18780.4045 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 9.168 | 20.1779 | 20077.9276 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 542979 [PFLUMM 5 161.00] CKT 1 | 27.2078 | 0.2212 | 121.1525 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 18.2946 | 18194.6414 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 18.2946 | 18194.6414 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 18.2946 | 18194.6414 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 18.0293 | 17929.2586 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 19.0598 | 18959.8215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 19.0598 | 18959.8215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 19.0598 | 18959.8215 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7378 | 20.449 | 20348.9757 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.4933 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.338 | 24.8477 | 24747.7372 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 33.9413 | 246.7449 | 246644.9491 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 13.8116 | 13711.556 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 12.5225 | 12422.4953 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 11.2 | 11100.0187 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 9.1721 | 9072.1009 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 8.904 | 8803.9958 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.4753 | 8.6522 | 8552.2137 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.6142 | 45.8005 | 45700.4942 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.6142 | 22.4456 | 22345.6144 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.2762 | 26.666 | 26566.0197 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.2762 | 41.9893 | 41889.2976 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2502 | 21.1156 | 21015.6474 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2502 | 21.0468 | 20946.7779 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2502 | 19.3565 | 19256.5453 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2502 | 18.8805 | 18780.478 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 9.168 | 20.1779 | 20077.949 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 27.2086 | 0.2211 | 121.1313 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 18.2948 | 18194.7765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 18.2948 | 18194.7765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 18.2948 | 18194.7765 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 18.0294 | 17929.3916 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 19.06 | 18959.9602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 19.06 | 18959.9602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 19.06 | 18959.9602 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 21.7401 | 20.4491 | 20349.1233 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.3379 | 19.1095 | 19009.4832 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.3379 | 24.8477 | 24747.7158 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 33.9412 | 246.7481 | 246648.0773 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 13.8108 | 13710.8398 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 12.5219 | 12421.8838 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 11.1995 | 11099.4947 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 9.1711 | 9071.0934 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 8.903 | 8803.0229 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 12.4888 | 8.6513 | 8551.273 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.6142 | 45.7987 | 45698.6751 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.6142 | 22.4459 | 22345.8883 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.2768 | 26.6664 | 26566.3764 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 13.2768 | 41.9871 | 41887.1 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 20.2502 | 21.1157 | 21015.658 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 20.2502 | 21.0468 | 20946.7971 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 20.2502 | 19.3566 | 19256.5554 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 20.2502 | 18.8805 | 18780.497 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 9.168 | 20.178 | 20077.959 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 2 | 27.2086 | 0.2211 | 121.1267 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 18.2961 | 18196.1175 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 18.2961 | 18196.1175 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 18.2961 | 18196.1175 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 18.0308 | 17930.7589 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 19.061 | 18961.0181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 19.061 | 18961.0181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 19.061 | 18961.0181 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 21.7344 | 20.4497 | 20349.7376 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.3636 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.3378 | 24.8474 | 24747.4421 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 33.9415 | 246.7499 | 246649.9272 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 13.816 | 13715.9585 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 12.5263 | 12426.3177 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 11.2032 | 11103.1748 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 9.1781 | 9078.1375 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 8.9099 | 8809.8928 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 12.4858 | 8.658 | 8557.9782 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.6126 | 45.835 | 45735.0162 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.6126 | 22.44 | 22340.0024 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.2612 | 26.7516 | 26651.5654 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 13.2612 | 41.5846 | 41484.6154 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 20.2504 | 21.1159 | 21015.8671 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 20.2504 | 21.0471 | 20947.1203 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 20.2504 | 19.3567 | 19256.7319 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 20.2504 | 18.8808 | 18780.7757 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 9.168 | 20.1781 | 20078.1117 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543048 [COLLEGE5 161.00] CKT 1 | 27.209 | 0.2211 | 121.119 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 18.2949 | 18194.8786 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 18.2949 | 18194.8786 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 18.2949 | 18194.8786 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 18.0295 | 17929.4916 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 19.0601 | 18960.0518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 19.0601 | 18960.0518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 19.0601 | 18960.0518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 21.7433 | 20.4492 | 20349.2012 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.4839 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.338 | 24.8477 | 24747.7145 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 33.9415 | 246.7497 | 246649.6601 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 13.8107 | 13710.6514 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 12.5217 | 12421.6545 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 11.1993 | 11099.317 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 9.1712 | 9071.1531 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 8.903 | 8803.0341 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 12.481 | 8.6512 | 8551.2419 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.6147 | 45.7992 | 45699.1879 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.6147 | 22.4458 | 22345.787 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.2354 | 26.7048 | 26604.7569 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 13.2354 | 41.826 | 41726.0399 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2503 | 21.1157 | 21015.6591 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2503 | 21.0468 | 20946.8 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2503 | 19.3566 | 19256.5574 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 20.2503 | 18.8805 | 18780.4997 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 9.168 | 20.178 | 20077.9627 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543049 [CEDRCRK5 161.00] CKT 1 | 27.2092 | 0.2211 | 121.1223 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.2371 | 21137.1317 | 90.1 | 176.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.2371 | 21137.1317 | 90.1 | 176.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.2371 | 21137.1317 | 90.1 | 176.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.0201 | 20920.148 | 96.53 | 189 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.7193 | 21619.3075 | 75.08 | 147 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.7193 | 21619.3075 | 75.08 | 147 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 21.7193 | 21619.3075 | 75.08 | 147 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 3.4905 | 22.7755 | 22675.5092 | 57.92 | 113.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.3419 | 19.1131 | 19013.061 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.3419 | 24.8553 | 24755.3399 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 33.9433 | 246.8228 | 246722.8487 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 13.8371 | 13737.1286 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 12.5437 | 12443.6997 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 11.2178 | 11117.8418 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 9.2119 | 9111.8562 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 8.9421 | 8842.0923 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.3446 | 8.6888 | 8588.7807 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.6173 | 45.8954 | 45795.4365 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.6173 | 22.4297 | 22329.6588 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.2618 | 26.7473 | 26647.3409 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 13.2618 | 41.6085 | 41508.4546 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2557 | 21.118 | 21018.0409 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2557 | 21.0512 | 20951.2263 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2557 | 19.3588 | 19258.8128 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.2557 | 18.8848 | 18784.7887 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.1682 | 20.1789 | 20078.9159 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 25.457 | 0.2291 | 129.1246 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 18.2941 | 18194.1105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 18.2941 | 18194.1105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 18.2941 | 18194.1105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 18.0287 | 17928.7404 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 19.0592 | 18959.2425 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 19.0592 | 18959.2425 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 19.0592 | 18959.2425 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7368 | 20.4483 | 20348.3026 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.3372 | 19.109 | 19009.0364 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.3372 | 24.8467 | 24746.6773 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 33.9403 | 246.725 | 246624.9959 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 13.8102 | 13710.2427 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 12.5214 | 12421.3921 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 11.1991 | 11099.0927 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 9.1701 | 9070.1305 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 8.9021 | 8802.0993 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.467 | 8.6504 | 8550.3863 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.615 | 45.8081 | 45708.1072 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.615 | 22.4443 | 22344.2935 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 7.6299 | 31.8919 | 31791.8863 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 7.6299 | 32.4863 | 32386.3072 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.248 | 21.119 | 21018.9724 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.248 | 21.0519 | 20951.9457 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.248 | 19.3593 | 19259.3345 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.248 | 18.8849 | 18784.8842 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 9.1678 | 20.1806 | 20080.5829 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543055 [SEOTTWA5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 27.2066 | 0.2212 | 121.1925 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 18.2948 | 18194.7507 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 18.2948 | 18194.7507 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 18.2948 | 18194.7507 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 18.0294 | 17929.3687 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 19.0599 | 18959.9111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 19.0599 | 18959.9111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 19.0599 | 18959.9111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 21.7428 | 20.449 | 20349.0334 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 13.3375 | 19.1092 | 19009.2257 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 13.3375 | 24.8471 | 24747.1171 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 33.9409 | 246.7382 | 246638.1971 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 13.8108 | 13710.8234 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 12.5218 | 12421.8371 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 11.1994 | 11099.4435 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 9.1713 | 9071.2526 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 8.9032 | 8803.1594 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 12.4873 | 8.6514 | 8551.3898 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 13.6146 | 45.8095 | 45709.5031 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 13.6146 | 22.4441 | 22344.1046 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 8.3288 | 63.3475 | 63247.4904 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 8.3288 | 22.6071 | 22507.139 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 20.2434 | 21.1179 | 21017.9269 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 20.2434 | 21.0502 | 2095022% | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 20.2434 | 19.3584 | 19258.3829 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 20.2434 | 18.8833 | 1878329% | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 9.1668 | 20.1799 | 20079.9222 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543069 [PAOLA 5 161.00] CKT 1 | 27.2067 | 0.2212 | 121.1608 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 18.295 | 18195.0261 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 18.295 | 18195.0261 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 18.295 | 18195.0261 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 18.0296 | 17929.6371 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 19.0602 | 18960.2106 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 19.0602 | 18960.2106 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 19.0602 | 18960.2106 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 21.7404 | 20.4494 | 20349.3817 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.338 | 19.1095 | 19009.48 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.338 | 24.8477 | 24747.7049 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 33.9415 | 246.7521 | 246652.0962 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 13.8104 | 13710.3904 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 12.5215 | 12421.4827 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 11.1991 | 11099.1425 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 9.1706 | 9070.5603 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 8.9025 | 8802.4995 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 12.5025 | 8.6508 | 8550.7599 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.6148 | 45.7979 | 45697.9268 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.6148 | 22.446 | 22345.9845 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.15 | 26.5482 | 26448.1646 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 13.15 | 42.6635 | 42563.5016 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 20.2501 | 21.1157 | 21015.6829 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 20.2501 | 21.0468 | 20946.8412 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 20.2501 | 19.3566 | 19256.5765 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 20.2501 | 18.8805 | 18780.5359 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 9.168 | 20.178 | 20077.9879 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] CKT 3 | 27.2089 | 0.2211 | 121.12 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 18.2949 | 18194.8557 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 18.2949 | 18194.8557 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 18.2949 | 18194.8557 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 18.0295 | 17929.4657 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 19.0601 | 18960.0519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 19.0601 | 18960.0519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 19.0601 | 18960.0519 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 21.7449 | 20.4492 | 20349.2363 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.3383 | 19.1097 | 19009.6638 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.3383 | 24.8481 | 24748.1345 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 33.9418 | 246.7592 | 246659.1599 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 13.8101 | 13710.1038 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 12.5212 | 12421.2467 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 11.1989 | 11098.9425 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 9.1701 | 9070.1071 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 8.9021 | 8802.0665 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 12.5076 | 8.6503 | 8550.3454 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.6152 | 45.795 | 45695.0239 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.6152 | 22.4464 | 22346.4441 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.3078 | 26.4212 | 26321.1943 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 13.3078 | 43.1847 | 43084.6596 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 20.2511 | 21.1159 | 21015.8814 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 20.2511 | 21.0472 | 20947.229 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 20.2511 | 19.3568 | 19256.7735 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 20.2511 | 18.8809 | 18780.9258 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 9.1682 | 20.1782 | 20078.228 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 762416 [ASG-2018-011161.00] CKT 1 | 27.2105 | 0.2211 | 121.0829 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 18.2947 | 18194.6996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 18.2947 | 18194.6996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 18.2947 | 18194.6996 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 18.0293 | 17929.3115 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 19.0599 | 18959.906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 19.0599 | 18959.906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 19.0599 | 18959.906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 21.7425 | 20.4491 | 20349.1053 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.3375 | 19.1093 | 19009.2631 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.3375 | 24.8472 | 24747.2027 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 33.9409 | 246.7431 | 246643.1 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 13.8103 | 13710.2831 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 12.5214 | 12421.4071 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 11.1991 | 11099.0776 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 9.1703 | 9070.3263 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 8.9023 | 8802.2835 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 12.5051 | 8.6506 | 8550.5594 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.6147 | 45.7959 | 45695.9119 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.6147 | 22.4463 | 22346.3456 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.2621 | 25.9373 | 25837.2634 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 13.2621 | 46.3747 | 46274.7488 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 20.2496 | 21.1153 | 21015.3469 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 20.2496 | 21.0463 | 20946.252 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 20.2496 | 19.3563 | 19256.2688 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 20.2496 | 18.88 | 18779.9836 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 9.1678 | 20.1777 | 20077.6555 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543120 [S.OTTWA11 34.500] TO BUS 543125 [S.OTWA1_TER112.500] CKT 1 | 27.2075 | 0.2212 | 121.1632 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 18.2948 | 18194.8212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 18.2948 | 18194.8212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 18.2948 | 18194.8212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 18.0294 | 17929.4329 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 19.06 | 18960.0182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 19.06 | 18960.0182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 19.06 | 18960.0182 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 21.7414 | 20.4492 | 20349.2037 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.3379 | 19.1095 | 19009.4784 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.3379 | 24.8477 | 24747.7038 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 33.9414 | 246.7522 | 246652.2217 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 13.8102 | 13710.2203 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 12.5213 | 12421.348 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 11.199 | 11099.0298 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 9.1703 | 9070.2657 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 8.9022 | 8802.2206 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 12.5038 | 8.6505 | 8550.4945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.6147 | 45.7964 | 45696.4361 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.6147 | 22.4462 | 22346.2367 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.184 | 26.1861 | 26086.0862 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 13.184 | 44.6665 | 44566.4739 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 20.2501 | 21.1156 | 21015.6462 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 20.2501 | 21.0468 | 20946.7921 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 20.2501 | 19.3565 | 19256.5487 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 20.2501 | 18.8805 | 18780.5004 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 9.1679 | 20.178 | 20077.9723 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543066 [S.OTTWA5 161.00] TO BUS 543121 [S.OTTWA21 34.500] TO BUS 543122 [S.OTTWA_TER112.500] CKT 4 | 27.2089 | 0.2211 | 121.12 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 18.2956 | 18195.5702 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 18.2956 | 18195.5702 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 18.2956 | 18195.5702 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 18.0302 | 17930.182 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 19.0607 | 18960.7232 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 19.0607 | 18960.7232 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 19.0607 | 18960.7232 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 21.7392 | 20.4499 | 20349.8542 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.3381 | 19.1095 | 19009.5499 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.8677 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 33.9416 | 246.7456 | 246645.6198 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 13.8125 | 13712.4629 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 12.5232 | 12423.1545 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 11.2006 | 11100.6008 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 9.1739 | 9073.9487 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 8.9057 | 8805.7061 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 12.4679 | 8.6538 | 8553.8002 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.6147 | 45.7963 | 45696.3197 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 13.6147 | 22.4463 | 22346.2573 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 5.8888 | 21.0617 | 20961.7059 | 73.77 | 170.4 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 5.8888 | 14.7078 | 14607.7601 | 76.23 | 181.05 | FAIL | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.2434 | 21.116 | 21016.0434 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.2434 | 21.0472 | 20947.1984 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.2434 | 19.3568 | 19256.7911 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 20.2434 | 18.8807 | 18780.6772 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 9.1667 | 20.1782 | 20078.2369 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543077 [PLSTVAL5 161.00] TO BUS 764400 [G20-073-TAP 161.00] CKT 1 | 27.2092 | 0.2211 | 121.1096 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 18.2852 | 18185.2198 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 18.2852 | 18185.2198 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 18.2852 | 18185.2198 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 18.0197 | 17919.7418 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 19.0519 | 18951.9214 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 19.0519 | 18951.9214 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 19.0519 | 18951.9214 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 21.7249 | 20.4434 | 20343.4101 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.3369 | 19.109 | 19009.0474 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.3369 | 24.8467 | 24746.702 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 33.9401 | 246.7359 | 246635.9125 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 13.8105 | 13710.4533 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 12.5216 | 12421.565 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 11.1992 | 11099.2096 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 9.1705 | 9070.5063 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 8.9025 | 8802.4651 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 12.5039 | 8.6507 | 8550.7435 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.6141 | 45.7959 | 45695.9157 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.6141 | 22.4464 | 22346.3564 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.2781 | 26.6655 | 26565.4885 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 13.2781 | 41.9911 | 41891.1122 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 20.2489 | 21.1153 | 21015.2508 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 20.2489 | 21.0461 | 20946.0947 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 20.2489 | 19.3562 | 19256.183 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 20.2489 | 18.8798 | 18779.8396 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 9.1674 | 20.1775 | 20077.475 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543629 [LACYGNE11_7 345.00] TO BUS 543630 [LAC11_AQC1 13.800] TO BUS 543631 [LAC11_TER1 13.800] CKT 11 | 27.2032 | 0.2212 | 121.2471 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 18.295 | 18195.0217 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 18.295 | 18195.0217 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 18.295 | 18195.0217 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 18.0296 | 17929.6313 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 19.0602 | 18960.2119 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 19.0602 | 18960.2119 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 19.0602 | 18960.2119 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 21.7432 | 20.4494 | 20349.3914 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.3379 | 19.1095 | 19009.4762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.3379 | 24.8477 | 24747.6977 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 33.9415 | 246.7522 | 246652.2392 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 13.8103 | 13710.3463 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 12.5214 | 12421.446 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 11.1991 | 11099.1086 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 9.1705 | 9070.4972 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 8.9024 | 8802.4394 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 12.5059 | 8.6507 | 8550.7031 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.6149 | 45.7967 | 45696.697 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.6149 | 22.4462 | 22346.1879 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 13.2782 | 41.9813 | 41881.3103 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 20.2503 | 21.1157 | 21015.6756 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 20.2503 | 21.0468 | 20946.8294 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 20.2503 | 19.3566 | 19256.5715 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 20.2503 | 18.8805 | 18780.5285 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 9.168 | 20.178 | 20077.9744 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543632 [LACYGNE22_7 345.00] TO BUS 543633 [LAC22_AQC1 13.800] TO BUS 543634 [LAC22_TER1 13.800] CKT 22 | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 18.2905 | 18190.5298 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 18.2905 | 18190.5298 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 18.2905 | 18190.5298 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 18.0251 | 17925.1258 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 19.0562 | 18956.2203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 19.0562 | 18956.2203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 19.0562 | 18956.2203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 21.738 | 20.4461 | 20346.1328 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.3377 | 19.1093 | 19009.3165 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.3377 | 24.8473 | 24747.3271 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 33.9412 | 246.7456 | 246645.6303 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 13.8102 | 13710.2207 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 12.5213 | 12421.3499 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 11.199 | 11099.0301 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 9.1703 | 9070.2543 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 8.9022 | 8802.2109 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 12.5052 | 8.6505 | 8550.4872 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.6147 | 45.7964 | 45696.3827 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.6147 | 22.4463 | 22346.2573 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.2782 | 26.6667 | 2656666% | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 13.2782 | 41.9852 | 41885.207 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 20.2499 | 21.1155 | 2101549% | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 20.2499 | 21.0465 | 20946.5032 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 20.2499 | 19.3564 | 19256.3989 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 20.2499 | 18.8802 | 18780.2227 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 9.1679 | 20.1778 | 20077.7799 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543659 [LACYGNE2 69.000] TO BUS 541541 [LAC_LAKE_2 69.000] CKT 1 | 27.2072 | 0.2212 | 121.1705 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543661 [LAC3_X1 6.9000] CKT X | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543662 [LAC3_Y1 6.9000] CKT Y | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543667 [LAC3_STAR7 345.00] TO BUS 543668 [LAC3_Z1 3.9800] CKT Z | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543670 [LAC8_X1 6.9000] CKT X | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 8.9024 | 8802.4312 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543671 [LAC8_Y1 6.9000] CKT Y | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 18.295 | 18195.0034 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 18.0296 | 17929.6142 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 19.0602 | 18960.19 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 21.7433 | 20.4494 | 20349.3621 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.3379 | 19.1095 | 19009.4768 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.3379 | 24.8477 | 24747.6991 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 33.9415 | 246.7522 | 246652.2299 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 13.8103 | 13710.3402 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 12.5214 | 12421.4408 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 11.1991 | 11099.1043 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 9.1705 | 9070.4889 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 8.9024 | 8802.4313 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 12.5059 | 8.6507 | 8550.6945 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.6149 | 45.7967 | 45696.6963 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.6149 | 22.4462 | 22346.1881 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.2782 | 26.6675 | 26567.4503 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 13.2782 | 41.9813 | 41881.3105 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 20.2503 | 21.1157 | 21015.675 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 20.2503 | 21.0468 | 20946.8284 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 20.2503 | 19.3566 | 19256.5711 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 20.2503 | 18.8805 | 18780.5276 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 9.168 | 20.178 | 20077.9748 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 543669 [LAC8_STAR7 345.00] TO BUS 543672 [LAC8_Z1 4.0000] CKT Z | 27.2092 | 0.2211 | 121.1204 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.0296 | 17929.6127 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1904 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1904 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1904 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 20.4494 | 20349.3657 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5071 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.7654 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 33.9415 | 246.7545 | 246654.4591 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 13.8102 | 13710.2462 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.361 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 11.199 | 11099.0384 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 9.1703 | 9070.3493 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.2961 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.5635 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.6145 | 45.8 | 45699.9703 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.6145 | 22.4457 | 22345.6695 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.3513 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.2782 | 41.9818 | 41881.8022 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8833 | 21.1117 | 21011.6759 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8833 | 21.0425 | 20942.4881 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8833 | 19.3478 | 19247.7626 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8833 | 18.8699 | 18769.8661 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 8.7251 | 20.494 | 20393.9517 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 27.2079 | 0.2212 | 121.1623 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9881 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9881 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9881 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 18.0296 | 17929.5991 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 21.7432 | 20.4493 | 20349.3437 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.3379 | 19.1095 | 19009.4618 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.3379 | 24.8477 | 24747.6674 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 33.9415 | 246.7511 | 246651.1327 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 13.8103 | 13710.3423 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 12.5214 | 12421.4426 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 11.1991 | 11099.1063 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 9.1705 | 9070.4919 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 8.9024 | 8802.4341 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 12.5059 | 8.6507 | 855070% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.615 | 45.7965 | 45696.5243 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.615 | 22.4462 | 2234620% | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.2782 | 26.6674 | 26567.37 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 13.2782 | 41.9817 | 41881.7016 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 20.2497 | 21.1158 | 21015.7761 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 20.2497 | 21.0464 | 20946.4404 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 20.2497 | 19.3565 | 19256.5259 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 20.2497 | 18.8799 | 18779.8932 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 9.1397 | 20.1654 | 20065.3971 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547466 [ATL109 5 161.00] TO BUS 547533 [ATL109 2 69.000] TO BUS 547702 [ATL109 1 12.500] CKT 1 | 27.2091 | 0.2211 | 121.1216 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 18.2951 | 18195.1262 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 18.2951 | 18195.1262 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 18.2951 | 18195.1262 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 18.0297 | 17929.7355 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 19.0603 | 18960.3075 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 19.0603 | 18960.3075 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 19.0603 | 18960.3075 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.7422 | 20.4495 | 20349.4744 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.505 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.766 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 33.9415 | 246.7529 | 246652.9419 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 13.8104 | 13710.3514 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 12.5214 | 12421.4498 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 11.1991 | 11099.1118 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 9.1705 | 9070.509 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 8.9025 | 8802.451 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5057 | 8.6507 | 8550.7128 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.6149 | 45.7978 | 45697.8308 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.6149 | 22.446 | 22345.9964 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.2774 | 26.6696 | 26569.6467 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.2774 | 41.9708 | 41870.7708 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2412 | 21.1222 | 21022.232 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2412 | 21.0552 | 20955.2 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2412 | 19.3616 | 19261.6469 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2412 | 18.8867 | 18786.6698 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.0972 | 20.2324 | 20132.3946 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 27.2072 | 0.2211 | 121.1109 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 18.2952 | 18195.1831 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 18.2952 | 18195.1831 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 18.2952 | 18195.1831 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 18.0298 | 17929.7932 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 19.0604 | 18960.3559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 19.0604 | 18960.3559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 19.0604 | 18960.3559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 21.7395 | 20.4495 | 20349.5106 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4675 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6759 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 33.9414 | 246.751 | 246651.0216 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 13.8104 | 13710.3884 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 12.5215 | 12421.4786 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 11.1991 | 11099.1363 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 9.1706 | 9070.5741 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 8.9025 | 8802.5121 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 12.5047 | 8.6508 | 8550.7706 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.6149 | 45.7976 | 45697.564 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.6149 | 22.446 | 22346.0424 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.27 | 26.6866 | 26586.5835 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 13.27 | 41.8901 | 41790.0735 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 20.093 | 21.1471 | 21047.0589 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 20.093 | 21.0884 | 20988.4401 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 20.093 | 19.3778 | 19277.8269 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 20.093 | 18.9075 | 18807.4713 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 9.1622 | 20.1813 | 20081.297 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547490 [FIR417 5 161.00] CKT 1 | 27.2059 | 0.2211 | 121.1253 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.295 | 18195.0044 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 18.0296 | 17929.6144 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1934 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 21.743 | 20.4494 | 20349.3701 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5095 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.7726 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 33.9415 | 246.7528 | 246652.7627 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 13.8102 | 13710.2357 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3514 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 11.199 | 11099.031 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 9.1703 | 9070.333 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.2812 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 12.5058 | 8.6505 | 8550.5491 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.6145 | 45.8004 | 45700.4235 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.6145 | 22.4456 | 22345.6023 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.2782 | 26.6673 | 26567.3304 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 13.2782 | 41.9819 | 41881.9064 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8813 | 21.103 | 21002.9938 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8813 | 21.0317 | 20931.7226 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8813 | 19.341 | 19241.0099 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 19.8813 | 18.862 | 18762.0356 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 8.7262 | 20.5032 | 20403.2411 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547494 [OAK432 5 161.00] CKT 1 | 27.2077 | 0.2212 | 121.1685 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 18.295 | 18194.9901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 18.295 | 18194.9901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 18.295 | 18194.9901 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 18.0296 | 17929.601 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 19.0602 | 18960.1759 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 19.0602 | 18960.1759 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 19.0602 | 18960.1759 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 21.7433 | 20.4493 | 20349.3473 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.3379 | 19.1095 | 19009.4721 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.3379 | 24.8477 | 24747.6908 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 33.9415 | 246.7509 | 246650.8768 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 13.8103 | 13710.3331 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 12.5214 | 12421.4349 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 11.1991 | 11099.0999 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 9.1705 | 9070.4784 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 8.9024 | 8802.4218 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 12.5059 | 8.6507 | 8550.6853 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.6151 | 45.796 | 45696.0356 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.6151 | 22.4463 | 22346.2832 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.2782 | 26.6674 | 26567.378 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 13.2782 | 41.9817 | 41881.6618 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 20.2435 | 21.1057 | 21005.6588 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 20.2435 | 21.033 | 20933.0044 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 20.2435 | 19.3484 | 19248.4184 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 20.2435 | 18.8695 | 18769.4743 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 9.1668 | 20.1734 | 20073.4184 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547467 [ORO110 5 161.00] TO BUS 547534 [ORO110 2 69.000] TO BUS 547703 [ORO110 1 12.500] CKT 1 | 27.2092 | 0.2211 | 121.1237 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.1015 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 18.0297 | 17929.7117 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2847 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2847 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2847 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 21.742 | 20.4495 | 20349.4526 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.502 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.7555 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 33.9415 | 246.7517 | 246651.7404 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 13.8104 | 13710.3534 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 12.5215 | 12421.4505 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 11.1991 | 11099.1128 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 9.1705 | 9070.5113 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 8.9025 | 8802.4522 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 12.5056 | 8.6507 | 8550.7148 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.6118 | 45.8436 | 45743.5941 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.6118 | 22.4387 | 22338.6501 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.2783 | 26.6674 | 26567.4491 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 13.2783 | 41.9813 | 41881.3162 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 20.2155 | 21.1318 | 21031.8179 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 20.2155 | 21.0676 | 20967.5671 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 20.2155 | 19.3688 | 19268.7683 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 20.2155 | 18.8954 | 18795.3847 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 8.9827 | 20.3319 | 20231.917 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547499 [CPK446 5 161.00] CKT 1 | 27.1943 | 0.2211 | 121.1107 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 18.295 | 18194.9998 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 18.295 | 18194.9998 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 18.295 | 18194.9998 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 18.0296 | 17929.6132 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 19.0602 | 18960.171 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 19.0602 | 18960.171 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 19.0602 | 18960.171 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 21.7419 | 20.4493 | 20349.3185 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4146 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.3378 | 24.8476 | 24747.5507 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 33.9413 | 246.7496 | 246649.5558 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 13.8103 | 13710.2536 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 12.5214 | 12421.3664 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 11.199 | 11099.0429 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 9.1704 | 9070.3631 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 8.9023 | 8802.309 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 12.5056 | 8.6506 | 8550.5762 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.6128 | 45.8034 | 45703.4325 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.6128 | 22.4452 | 22345.2419 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.278 | 26.6679 | 26567.8898 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 13.278 | 41.9792 | 41879.1873 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 20.1955 | 21.1244 | 21024.3601 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 20.1955 | 21.0563 | 20956.253 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 20.1955 | 19.3622 | 19262.202 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 20.1955 | 18.8854 | 18785.3705 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 8.9713 | 20.2496 | 20149.5942 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 763696 [G19-035-TAP 161.00] CKT 1 | 27.2023 | 0.2212 | 121.2003 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9834 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9834 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 18.295 | 18194.9834 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 18.0296 | 17929.5939 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1659 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1659 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 19.0602 | 18960.1659 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 21.7432 | 20.4493 | 20349.3326 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.338 | 19.1095 | 19009.4907 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.338 | 24.8477 | 24747.7297 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 33.9415 | 246.7521 | 246652.1463 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 13.8103 | 13710.3252 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 12.5214 | 12421.428 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 11.1991 | 11099.0937 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 9.1705 | 9070.4663 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 8.9024 | 8802.4094 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 12.5059 | 8.6507 | 8550.6733 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.6146 | 45.7985 | 45698.5173 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.6146 | 22.4459 | 22345.9107 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.2782 | 26.6675 | 26567.4664 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 13.2782 | 41.9812 | 41881.203 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 20.2489 | 21.1153 | 21015.3274 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 20.2489 | 21.046 | 20945.9765 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 20.2489 | 19.3562 | 19256.1922 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 20.2489 | 18.8796 | 18779.6092 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 9.1625 | 20.165 | 20064.9809 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547468 [AUR124 5 161.00] TO BUS 547537 [AUR124 2 69.000] TO BUS 547704 [AUR1241 12.500] CKT 1 | 27.2085 | 0.2211 | 121.1434 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 18.3007 | 18200.671 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 18.3007 | 18200.671 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 18.3007 | 18200.671 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 18.0353 | 17935.2513 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 19.0657 | 18965.7029 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 19.0657 | 18965.7029 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 19.0657 | 18965.7029 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6464 | 20.4548 | 20354.763 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.336 | 19.1087 | 19008.6599 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.336 | 24.8457 | 24745.6765 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 33.9408 | 246.6947 | 246594.6688 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 13.8099 | 13709.9279 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 12.5211 | 12421.0775 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 11.1988 | 1109881% | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 9.1699 | 9069.9376 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 8.9019 | 880189% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.496 | 8.6502 | 8550.16 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.6142 | 45.8007 | 45700.6818 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.6142 | 22.4456 | 22345.5735 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.2744 | 26.6676 | 26567.5654 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.2744 | 41.9816 | 41881.6304 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.3579 | 24.2686 | 24168.6408 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.3579 | 25.7689 | 25668.8736 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.3579 | 21.0573 | 20957.2803 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.3579 | 21.2836 | 21183.6096 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.0762 | 20.275 | 20175.0399 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 27.0305 | 0.2212 | 121.1973 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0308 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0308 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0308 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6403 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.2216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7432 | 20.4494 | 20349.4021 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4039 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3378 | 24.8475 | 24747.5277 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 33.9414 | 246.75 | 246650.0414 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 13.8102 | 13710.2406 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3564 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 11.199 | 11099.0346 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 9.1703 | 9070.3412 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.289 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.5567 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6142 | 45.8005 | 45700.5402 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6142 | 22.4456 | 22345.603 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4147 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.2782 | 41.9815 | 41881.4709 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.0593 | 21.1251 | 21025.0975 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.0593 | 21.0605 | 20960.5348 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.0593 | 19.3613 | 19261.341 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.0593 | 18.8877 | 18787.7499 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1077 | 20.2141 | 20114.0907 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 27.2072 | 0.2212 | 121.1858 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 18.295 | 18194.9944 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6056 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1792 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1792 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1792 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 21.7432 | 20.4493 | 20349.3482 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4751 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6944 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 33.9415 | 246.7509 | 246650.8694 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3338 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4353 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.0997 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4788 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4221 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6856 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.6149 | 45.7968 | 45696.8393 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.6149 | 22.4462 | 22346.168 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.2782 | 26.6675 | 26567.49 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 13.2782 | 41.9811 | 41881.0943 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 20.2235 | 21.1272 | 21027.197 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 20.2235 | 21.061 | 20961.0254 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 20.2235 | 19.3651 | 19265.0698 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 20.2235 | 18.8902 | 18790.1927 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 9.1626 | 20.1817 | 20081.6699 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547472 [TIP292 5 161.00] TO BUS 547500 [RNM393 5 161.00] CKT 1 | 27.209 | 0.2211 | 121.1259 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.2949 | 18194.8911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 18.0295 | 17929.5063 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.0601 | 18960.0559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.0601 | 18960.0559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 19.0601 | 18960.0559 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7428 | 20.4492 | 20349.1902 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.479 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.7004 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9414 | 246.7504 | 246650.428 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 13.8102 | 13710.1801 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 12.5213 | 12421.304 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 11.199 | 11098.9916 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 9.1703 | 9070.2535 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 8.9022 | 8802.2032 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5057 | 8.6505 | 8550.474 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6127 | 45.8136 | 45713.5582 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6127 | 22.4436 | 22343.5555 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 26.6674 | 26567.4266 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 41.9814 | 41881.3967 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.231 | 21.1096 | 21009.6498 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.231 | 21.0349 | 20934.8579 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.231 | 19.3506 | 19250.6347 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.231 | 18.8685 | 18768.484 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 7.2701 | 20.7495 | 20649.5333 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547480 [MON383 5 161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2028 | 0.2213 | 121.3002 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 18.2952 | 18195.1505 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 18.2952 | 18195.1505 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 18.2952 | 18195.1505 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 18.0298 | 17929.7612 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 19.0603 | 18960.3261 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 19.0603 | 18960.3261 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 19.0603 | 18960.3261 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 21.7392 | 20.4495 | 20349.4843 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4091 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.3378 | 24.8475 | 24747.5399 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 33.9412 | 246.7479 | 246647.8975 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 13.8103 | 13710.3371 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 12.5214 | 12421.4357 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 11.1991 | 11099.1009 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 9.1705 | 9070.492 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 8.9024 | 8802.4334 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 12.5049 | 8.6507 | 8550.6951 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.6146 | 45.797 | 45697.0153 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.6146 | 22.4462 | 22346.1532 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.2726 | 26.6786 | 26578.5879 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 13.2726 | 41.9285 | 41828.4513 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 20.2325 | 21.1151 | 21015.0885 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 20.2325 | 21.0455 | 20945.4688 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 20.2325 | 19.3559 | 19255.9015 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 20.2325 | 18.879 | 18779.022 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 8.9513 | 20.3459 | 20245.8579 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547485 [CAR395 5 161.00] TO BUS 547491 [PUR421 5 161.00] CKT 1 | 27.2049 | 0.2212 | 121.1686 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0068 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0068 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 18.295 | 18195.0068 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6166 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1978 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 21.7432 | 20.4494 | 20349.376 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4673 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6753 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 33.9413 | 246.7523 | 246652.3201 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 13.8103 | 13710.2637 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 12.5214 | 12421.3752 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 11.1991 | 11099.0508 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 9.1704 | 9070.3742 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 8.9023 | 8802.321 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 12.5057 | 8.6506 | 8550.5877 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.6146 | 45.7967 | 45696.7241 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.6146 | 22.4462 | 22346.2009 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.2781 | 26.6674 | 26567.3674 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 13.2781 | 41.9817 | 41881.724 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 20.2473 | 21.1006 | 21000.5731 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 20.2473 | 21.0276 | 20927.5767 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 20.2473 | 19.3447 | 19244.7141 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 20.2473 | 18.8662 | 18766.1777 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 9.167 | 20.174 | 20073.9504 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547459 [WWR477 161.00] CKT 1 | 27.2093 | 0.2211 | 121.1019 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.066 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.066 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.066 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 18.0297 | 17929.6789 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 19.0602 | 18960.2342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 19.0602 | 18960.2342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 19.0602 | 18960.2342 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 21.742 | 20.4494 | 20349.3775 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5366 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.338 | 24.8478 | 24747.8382 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 33.9415 | 246.753 | 246652.9744 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 13.8103 | 13710.3059 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 12.5214 | 12421.4103 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 11.1991 | 11099.0795 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 9.1704 | 9070.4429 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 8.9024 | 8802.386 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 12.5056 | 8.6506 | 8550.6499 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.6145 | 45.7992 | 45699.169 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.6145 | 22.4458 | 22345.7925 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.2772 | 26.6701 | 26570.0799 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 13.2772 | 41.9685 | 41868.5479 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2388 | 21.1152 | 21015.2012 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2388 | 21.0427 | 20942.7219 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2388 | 19.3553 | 19255.2834 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 20.2388 | 18.875 | 18775.0169 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 9.0899 | 20.2363 | 20136.2606 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547470 [JOP145 5 161.00] CKT 1 | 27.2058 | 0.2212 | 121.1525 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 18.295 | 18194.9911 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 18.0296 | 17929.6018 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1779 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1779 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 19.0602 | 18960.1779 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.743 | 20.4494 | 20349.3508 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3378 | 19.1094 | 19009.4364 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3378 | 24.8476 | 24747.6017 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 33.9413 | 246.7513 | 246651.3328 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 13.8103 | 13710.2734 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 12.5214 | 12421.3842 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 11.1991 | 11099.0577 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 9.1704 | 9070.3895 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 8.9023 | 8802.3351 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5057 | 8.6506 | 8550.6013 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6142 | 45.7987 | 45698.7197 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6142 | 22.4459 | 22345.8799 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.278 | 26.6674 | 26567.4119 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.278 | 41.9815 | 41881.4589 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.1663 | 21.0897 | 20989.6838 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.1663 | 21.0123 | 20912.3177 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.1663 | 19.3346 | 19234.6364 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 20.1663 | 18.8523 | 18752.2644 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.1401 | 20.1939 | 20093.8788 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 27.2071 | 0.2212 | 121.1626 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 18.295 | 18195.0004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 18.295 | 18195.0004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 18.295 | 18195.0004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 18.0296 | 17929.6111 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 19.0602 | 18960.1873 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 19.0602 | 18960.1873 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 19.0602 | 18960.1873 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 21.7433 | 20.4494 | 20349.3597 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.3379 | 19.1095 | 19009.4546 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.3379 | 24.8476 | 24747.6479 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 33.9415 | 246.751 | 24665103% | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 13.8103 | 13710.3091 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 12.5214 | 1242141% | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 11.1991 | 11099.0825 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 9.1704 | 9070.4424 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 8.9024 | 8802.3862 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 12.5059 | 8.6507 | 8550.6515 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.6147 | 45.7979 | 45697.9417 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.6147 | 22.446 | 22345.999 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.2782 | 26.6674 | 26567.4303 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 13.2782 | 41.9814 | 41881.3762 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 20.2077 | 21.1096 | 21009.592 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 20.2077 | 21.0389 | 20938.9165 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 20.2077 | 19.3511 | 19251.1163 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 20.2077 | 18.8737 | 18773.6597 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 9.1531 | 20.1869 | 20086.8953 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 2 | 27.2085 | 0.2211 | 121.1444 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 18.295 | 18195.0081 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 18.295 | 18195.0081 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 18.295 | 18195.0081 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 18.0296 | 17929.6186 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1953 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1953 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 19.0602 | 18960.1953 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 21.7433 | 20.4494 | 20349.3687 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.3379 | 19.1095 | 19009.4762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.3379 | 24.8477 | 24747.6972 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 33.9415 | 246.7522 | 246652.208 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 13.8103 | 13710.3325 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 12.5214 | 12421.4343 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 11.1991 | 11099.0989 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 9.1705 | 9070.4767 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 8.9024 | 8802.4202 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 12.5059 | 8.6507 | 8550.6837 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.6149 | 45.7967 | 45696.6863 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.6149 | 22.4462 | 22346.191 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.2782 | 26.6674 | 26567.4362 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 13.2782 | 41.9814 | 41881.3634 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 20.2501 | 21.1145 | 21014.5154 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 20.2501 | 21.0455 | 20945.536 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 20.2501 | 19.3557 | 19255.7007 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 20.2501 | 18.8797 | 18779.6815 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 9.168 | 20.1779 | 20077.8942 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547655 [S1G439 1 13.200] CKT 1 | 27.2093 | 0.2211 | 121.1169 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 18.2953 | 18195.256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 18.2953 | 18195.256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 18.2953 | 18195.256 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 18.0299 | 17929.8743 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 19.0604 | 18960.3727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 19.0604 | 18960.3727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 19.0604 | 18960.3727 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 21.7378 | 20.4494 | 20349.4347 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.3382 | 19.1096 | 19009.5864 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.3382 | 24.848 | 24747.9714 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 33.9414 | 246.7464 | 246646.3906 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 13.8112 | 13711.1524 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 12.5221 | 12422.1274 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 11.1997 | 11099.6715 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 9.1717 | 9071.6988 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 8.9036 | 8803.6003 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 12.5064 | 8.6518 | 8551.8261 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.6163 | 45.801 | 45700.9642 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.6163 | 22.4453 | 22345.3447 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.2775 | 26.6698 | 26569.7864 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 13.2775 | 41.97 | 41870.0291 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 19.6092 | 21.3684 | 21268.3851 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 19.6092 | 21.3755 | 21275.4778 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 19.6092 | 19.5452 | 19445.2193 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 19.6092 | 19.1133 | 19013.3415 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 9.0755 | 20.2697 | 20169.6571 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547656 [S2G439 1 18.000] CKT 1 | 27.1905 | 0.2213 | 121.3379 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 18.2951 | 18195.1271 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 18.2951 | 18195.1271 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 18.2951 | 18195.1271 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 18.0297 | 17929.7463 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 19.0603 | 18960.2518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 19.0603 | 18960.2518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 19.0603 | 18960.2518 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 21.7389 | 20.4493 | 20349.3222 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.3382 | 19.1096 | 19009.5819 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.3382 | 24.848 | 24747.9684 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 33.9414 | 246.748 | 246647.9927 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 13.8111 | 13711.1456 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 12.5221 | 12422.1216 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 11.1997 | 11099.667 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 9.1717 | 9071.685 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 8.9036 | 8803.5882 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 12.5065 | 8.6518 | 8551.8141 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.6164 | 45.7997 | 45699.7112 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.6164 | 22.4456 | 22345.5539 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.2777 | 26.6693 | 26569.2879 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 13.2777 | 41.9724 | 41872.4174 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 19.7519 | 21.3163 | 21216.2781 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 19.7519 | 21.3061 | 21206.1186 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 19.7519 | 19.5063 | 19406.3488 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 19.7519 | 19.0638 | 18963.7993 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 9.097 | 20.2499 | 20149.8611 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547657 [S3G439 1 18.000] CKT 1 | 27.1933 | 0.2213 | 121.3406 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 18.2953 | 18195.3049 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 18.2953 | 18195.3049 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 18.2953 | 18195.3049 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 18.0299 | 17929.9243 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 19.0604 | 18960.4176 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 19.0604 | 18960.4176 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 19.0604 | 18960.4176 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 21.7377 | 20.4495 | 20349.4733 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.3381 | 19.1096 | 19009.5641 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.3381 | 24.8479 | 24747.9141 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 33.9414 | 246.7469 | 246646.8539 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 13.811 | 13710.9961 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 12.522 | 12421.9945 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 11.1996 | 11099.5621 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 9.1715 | 9071.47 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 8.9034 | 8803.3794 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 12.5061 | 8.6516 | 8551.6112 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.6159 | 45.8023 | 45702.2545 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.6159 | 22.4452 | 22345.1681 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.2775 | 26.67 | 26570.037 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 13.2775 | 41.9688 | 41868.7736 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 19.5714 | 21.3944 | 21294.373 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 19.5714 | 21.4072 | 21307.2085 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 19.5714 | 19.5644 | 19464.3808 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 19.5714 | 19.1345 | 19034.5356 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 9.0685 | 20.273 | 20173.0379 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547658 [S4G439 1 18.000] CKT 1 | 27.1906 | 0.2213 | 121.3239 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9739 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9739 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 18.296 | 18195.9739 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 18.0306 | 17930.5942 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0292 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0292 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 19.061 | 18961.0292 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 21.7308 | 20.45 | 20350.0061 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.3381 | 19.1096 | 19009.5899 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.3381 | 24.848 | 24747.9622 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 33.9414 | 246.7413 | 246641.3078 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 13.8112 | 13711.1799 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 12.5221 | 12422.1466 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 11.1997 | 11099.6887 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 9.1718 | 9071.7545 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 8.9037 | 8803.6525 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 12.5056 | 8.6519 | 8551.8744 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.6161 | 45.805 | 45705 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.6161 | 22.4447 | 22344.6903 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.2767 | 26.672 | 26571.9921 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 13.2767 | 41.9594 | 41859.4182 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 18.3184 | 21.927 | 21826.9868 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 18.3184 | 22.1225 | 22022.5067 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 18.3184 | 19.9579 | 19857.8733 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 18.3184 | 19.6367 | 19536.7121 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 9.0445 | 20.2954 | 20195.3977 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547501 [RIV453 5 161.00] CKT 1 | 27.1748 | 0.2213 | 121.3367 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0163 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0163 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0163 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 18.0296 | 17929.6265 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.2051 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 21.7433 | 20.4494 | 20349.3807 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4751 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.695 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 33.9415 | 246.7521 | 246652.1348 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3247 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4277 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.0934 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4659 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.409 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6729 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.6149 | 45.7967 | 45696.6751 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.6149 | 22.4462 | 22346.197 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4222 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 13.2782 | 41.9814 | 41881.4333 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 20.2492 | 21.1108 | 21010.811 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 20.2492 | 21.0413 | 20941.2555 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 20.2492 | 19.3529 | 19252.8848 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 20.2492 | 18.8768 | 18776.7646 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 9.1679 | 20.1778 | 20077.8378 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547503 [RIV452T 5 161.00] TO BUS 547502 [RIV167 5 161.00] CKT 1 | 27.2093 | 0.2211 | 121.1125 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9953 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.605 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1808 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1808 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1808 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 21.7432 | 20.4494 | 20349.353 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.338 | 19.1095 | 19009.4814 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.338 | 24.8477 | 24747.712 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 33.9415 | 246.7521 | 246652.126 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3293 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4316 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.0972 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4728 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4156 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6793 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.615 | 45.7967 | 45696.6525 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.615 | 22.4462 | 22346.192 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.2782 | 26.6675 | 26567.4505 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 13.2782 | 41.9813 | 41881.2919 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 20.203 | 21.1032 | 21003.2465 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 20.203 | 21.0302 | 20930.1749 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 20.203 | 19.3459 | 19245.9299 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 20.203 | 18.8666 | 18766.6445 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 9.1629 | 20.1843 | 20084.2929 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547525 [JOP 59 2 69.000] CKT 1 | 27.2091 | 0.2211 | 121.1233 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 18.295 | 18194.9978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.6086 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1841 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 21.7432 | 20.4494 | 2034936% | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4667 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.3379 | 24.8477 | 2474768% | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 33.9414 | 246.7525 | 246652.4829 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3421 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4417 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1055 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4902 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4333 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6964 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.6149 | 45.7967 | 45696.6535 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.6149 | 22.4462 | 22346.1968 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.2782 | 26.6674 | 26567.4329 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 13.2782 | 41.9814 | 41881.3803 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 20.2483 | 21.1133 | 21013.2557 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 20.2483 | 21.0434 | 20943.3952 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 20.2483 | 19.3546 | 19254.5804 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 20.2483 | 18.8777 | 18777.7254 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 9.167 | 20.1766 | 20076.5863 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547530 [COL 94 2 69.000] CKT 1 | 27.209 | 0.2211 | 121.1223 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 18.295 | 18195.0024 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 18.0296 | 17929.6131 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 21.7432 | 20.4494 | 20349.3617 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4539 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.3379 | 24.8476 | 24747.6446 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 33.9414 | 246.7527 | 246652.7084 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3473 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4468 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1092 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4981 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4409 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.7038 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.6149 | 45.7967 | 45696.6523 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.6149 | 22.4462 | 22346.1951 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.2782 | 26.6674 | 26567.4419 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 13.2782 | 41.9813 | 41881.3267 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 20.2454 | 21.1137 | 21013.6957 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 20.2454 | 21.044 | 20944.0311 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 20.2454 | 19.3549 | 19254.9046 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 20.2454 | 18.8782 | 18778.2008 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 9.1655 | 20.178 | 20078.0399 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547602 [RIV406 2 69.000] CKT 1 | 27.2089 | 0.2211 | 121.121 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0016 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0016 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0016 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 18.0296 | 17929.6124 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.187 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 21.7433 | 20.4494 | 20349.3598 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4804 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.71 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 33.9415 | 246.7521 | 246652.1463 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3364 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4376 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1016 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4826 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4259 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6892 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.615 | 45.7966 | 45696.618 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.615 | 22.4462 | 22346.2011 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.2782 | 26.6675 | 26567.4706 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 13.2782 | 41.9812 | 41881.2088 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 20.2285 | 21.1161 | 21016.07 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 20.2285 | 21.0471 | 20947.1198 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 20.2285 | 19.3565 | 19256.49 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 20.2285 | 18.8801 | 18780.1415 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 9.1648 | 20.1833 | 20083.3086 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547541 [RIV167 2 69.000] TO BUS 547690 [GLF339 2 69.000] CKT 1 | 27.2092 | 0.2211 | 121.1208 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 18.295 | 18195.0107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 18.295 | 18195.0107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 18.295 | 18195.0107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 18.0296 | 17929.621 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 19.0602 | 18960.1988 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 19.0602 | 18960.1988 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 19.0602 | 18960.1988 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 21.743 | 20.4494 | 20349.3741 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.3378 | 19.1095 | 19009.4507 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.3378 | 24.8476 | 24747.6384 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 33.9413 | 246.7527 | 246652.7055 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 13.8103 | 13710.3436 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 12.5214 | 12421.4436 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 11.1991 | 11099.1066 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 9.1705 | 9070.4934 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 8.9024 | 8802.4356 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 12.5058 | 8.6507 | 8550.6986 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.6145 | 45.7965 | 45696.5419 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.6145 | 22.4462 | 22346.2142 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.2781 | 26.6674 | 26567.4358 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 13.2781 | 41.9814 | 41881.3834 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 20.2424 | 21.1146 | 21014.6094 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 20.2424 | 21.0456 | 20945.5514 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 20.2424 | 19.3557 | 19255.6779 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 20.2424 | 18.8795 | 18779.5281 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 9.1244 | 20.2034 | 20103.3587 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 300680 [2VERONA 69.000] CKT 1 | 27.2078 | 0.2211 | 121.1248 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 18.295 | 18195.0335 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 18.295 | 18195.0335 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 18.295 | 18195.0335 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 18.0296 | 17929.6427 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 19.0602 | 18960.2254 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 19.0602 | 18960.2254 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 19.0602 | 18960.2254 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 21.7434 | 20.4494 | 20349.4079 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.3378 | 19.1094 | 19009.449 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.3378 | 24.8476 | 24747.6335 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 33.9414 | 246.7525 | 246652.5204 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.2879 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.3965 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.0679 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 9.1704 | 9070.4106 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.3557 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 12.5059 | 8.6506 | 8550.6211 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.6152 | 45.7951 | 45695.0843 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.6152 | 22.4464 | 22346.4482 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.2783 | 26.6674 | 26567.3867 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 13.2783 | 41.9816 | 41881.5853 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 20.2518 | 21.1137 | 21013.7125 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 20.2518 | 21.0451 | 20945.0941 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 20.2518 | 19.3552 | 19255.2181 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 20.2518 | 18.8797 | 18779.7466 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 9.1679 | 20.1723 | 20072.2507 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547400 [MON376J2 69.000] CKT 1 | 27.2109 | 0.2211 | 121.0679 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 18.295 | 18195.0473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 18.295 | 18195.0473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 18.295 | 18195.0473 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 18.0297 | 17929.6566 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 19.0602 | 18960.2439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 19.0602 | 18960.2439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 19.0602 | 18960.2439 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 21.7435 | 20.4494 | 20349.4335 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.3378 | 19.1094 | 19009.4243 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.3378 | 24.8476 | 24747.5759 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 33.9414 | 246.7513 | 246651.2964 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 13.8102 | 13710.2384 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 12.5214 | 12421.3547 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 11.199 | 11099.034 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 9.1703 | 9070.3378 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 8.9023 | 8802.2852 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 12.5058 | 8.6506 | 8550.5538 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.6152 | 45.7939 | 45693.8857 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.6152 | 22.4467 | 22346.6528 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.2783 | 26.6673 | 26567.3393 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 13.2783 | 41.9818 | 41881.848 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 20.2523 | 21.1114 | 21011.3796 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 20.2523 | 21.0425 | 20942.5025 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 20.2523 | 19.3535 | 19253.4788 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 20.2523 | 18.8781 | 18778.0696 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 9.1676 | 20.1625 | 20062.507 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547405 [MON352J2 69.000] CKT 1 | 27.212 | 0.221 | 121.03 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9942 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9942 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 18.295 | 18194.9942 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 18.0296 | 17929.6052 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1796 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1796 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1796 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 21.7433 | 20.4493 | 20349.3495 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.477 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.6984 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 33.9415 | 246.7523 | 246652.3367 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.3374 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4384 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1023 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.484 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4273 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6906 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.615 | 45.7967 | 45696.7363 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.615 | 22.4462 | 22346.1766 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.2782 | 26.6675 | 26567.4619 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 13.2782 | 41.9812 | 41881.2343 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 20.2231 | 21.1155 | 21015.5104 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 20.2231 | 21.0459 | 20945.9281 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 20.2231 | 19.3559 | 19255.8735 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 20.2231 | 18.8789 | 18778.8511 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 9.1551 | 20.1821 | 20082.0922 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547449 [PRC460 2 69.000] CKT 1 | 27.2092 | 0.2211 | 121.1206 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0026 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0026 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 18.295 | 18195.0026 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 18.0296 | 17929.6133 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 19.0602 | 18960.1892 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 21.7433 | 20.4494 | 20349.3613 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.3379 | 19.1095 | 19009.4777 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.3379 | 24.8477 | 24747.7009 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 33.9415 | 246.7522 | 246652.2195 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 13.8103 | 13710.34 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 12.5214 | 12421.4407 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 11.1991 | 11099.1046 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 9.1705 | 9070.4886 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 8.9024 | 8802.4309 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 12.5059 | 8.6507 | 8550.6941 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.6149 | 45.7965 | 45696.5139 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.6149 | 22.4462 | 22346.2278 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.2782 | 26.6675 | 26567.4537 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 13.2782 | 41.9813 | 41881.2934 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 20.2421 | 21.1166 | 21016.577 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 20.2421 | 21.0479 | 20947.8904 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 20.2421 | 19.3571 | 19257.1408 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 20.2421 | 18.8811 | 18781.1003 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 9.154 | 20.1878 | 20087.8257 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547591 [MON383 2 69.000] TO BUS 547540 [MON152 2 69.000] CKT 1 | 27.2089 | 0.2211 | 121.1188 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 18.0296 | 17929.6145 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 19.0602 | 1896019% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 19.0602 | 18960.1904 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 19.0602 | 1896019% | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7433 | 20.4494 | 20349.3626 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6979 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9415 | 246.7522 | 246652.2354 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3392 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 12.5214 | 12421.44 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 11.1991 | 11099.1036 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4867 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 8.9024 | 8802.4298 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6931 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6149 | 45.7967 | 45696.6644 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6149 | 22.4462 | 22346.1936 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4469 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3104 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2503 | 21.1156 | 21015.643 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2503 | 21.0468 | 20946.7976 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2503 | 19.3565 | 19256.5485 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2503 | 18.8805 | 18780.5099 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 9.1677 | 20.177 | 20076.9701 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547651 [L1G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2092 | 0.2211 | 121.1198 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 18.2952 | 18195.1618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 18.2952 | 18195.1618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 18.2952 | 18195.1618 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 18.0298 | 17929.7735 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 19.0603 | 18960.3288 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 19.0603 | 18960.3288 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 19.0603 | 18960.3288 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.7415 | 20.4495 | 20349.4728 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 19.1095 | 19009.5198 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 24.8478 | 24747.7946 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9417 | 246.7518 | 246651.7506 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 13.8104 | 13710.4465 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 12.5215 | 12421.53 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 11.1992 | 11099.1782 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 9.1707 | 9070.6511 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 8.9026 | 8802.588 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5059 | 8.6508 | 8550.8456 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6147 | 45.8044 | 45704.4399 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6147 | 22.4449 | 22344.9112 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.278 | 26.6685 | 26568.5098 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.278 | 41.9761 | 41876.15 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1612 | 21.1503 | 21050.3159 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1612 | 21.0913 | 20991.3353 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1612 | 19.3827 | 19282.6635 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1612 | 18.9123 | 18812.2923 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 8.2701 | 20.9172 | 20817.1865 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547652 [L2G382 1 13.200] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2007 | 0.2212 | 121.1793 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0945 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0945 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0945 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.0297 | 17929.7066 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2655 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2655 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2655 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 20.4494 | 20349.4133 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 19.1095 | 19009.5484 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.8718 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9415 | 246.7511 | 246651.123 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 13.8105 | 13710.5227 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 12.5216 | 12421.5944 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 11.1992 | 11099.2317 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 9.1708 | 9070.7617 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 8.9027 | 8802.6947 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 8.6509 | 8550.9491 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.615 | 45.802 | 45701.9584 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.615 | 22.4453 | 22345.2986 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 26.6682 | 26568.1968 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 41.9777 | 41877.6701 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1909 | 21.1413 | 21041.262 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1909 | 21.0799 | 20979.8807 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1909 | 19.376 | 19275.9624 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1909 | 18.9043 | 18804.348 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 8.5405 | 20.7284 | 20628.4021 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547653 [L3G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2022 | 0.2212 | 121.2022 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0947 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0947 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.2951 | 18195.0947 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 18.0297 | 17929.7068 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2656 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2656 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 19.0603 | 18960.2656 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.742 | 20.4494 | 20349.4135 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 19.1095 | 19009.5484 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.8718 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9415 | 246.7511 | 246651.1225 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 13.8105 | 13710.5227 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 12.5216 | 12421.5944 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 11.1992 | 11099.2317 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 9.1708 | 9070.7617 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 8.9027 | 8802.6947 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.506 | 8.6509 | 8550.9491 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.615 | 45.802 | 45701.9565 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.615 | 22.4453 | 22345.2989 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 26.6682 | 26568.1968 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2781 | 41.9777 | 41877.6701 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1908 | 21.1413 | 21041.2696 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1908 | 21.0799 | 20979.8933 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1908 | 19.376 | 19275.9687 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.1908 | 18.9044 | 18804.3567 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 8.54 | 20.7285 | 20628.4867 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547654 [L4G3821 18.000] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2022 | 0.2212 | 121.2022 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 18.2954 | 18195.3914 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 18.2954 | 18195.3914 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 18.2954 | 18195.3914 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 18.03 | 17929.9933 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 19.0606 | 18960.6031 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 19.0606 | 18960.6031 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 19.0606 | 18960.6031 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 21.7411 | 20.4498 | 20349.8267 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.3363 | 19.1086 | 19008.5586 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.3363 | 24.8456 | 24745.5768 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 33.9408 | 246.7305 | 246630.4537 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 13.8105 | 13710.4704 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 12.5216 | 12421.5509 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 11.1992 | 11099.1959 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 9.1707 | 9070.6832 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 8.9026 | 8802.6195 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 12.5057 | 8.6509 | 8550.8764 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.6143 | 45.7984 | 45698.3819 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.6143 | 22.446 | 22345.9515 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.2776 | 26.668 | 26567.9914 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 13.2776 | 41.9788 | 41878.8221 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 19.1512 | 21.2209 | 21120.8788 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 19.1512 | 21.192 | 21091.9995 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 19.1512 | 19.4241 | 19324.1284 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 19.1512 | 18.9718 | 18871.8136 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 9.1227 | 20.1883 | 20088.2857 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547729 [BAX488 5 161.00] TO BUS 547487 [HOC404 5 161.00] CKT 1 | 27.2053 | 0.2211 | 121.1207 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 18.295 | 18194.9794 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 18.295 | 18194.9794 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 18.295 | 18194.9794 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 18.0296 | 17929.591 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1629 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1629 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1629 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 21.7432 | 20.4493 | 20349.3293 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.338 | 19.1095 | 19009.495 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.338 | 24.8477 | 24747.7413 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 33.9415 | 246.7521 | 246652.0658 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3168 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4209 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 11.1991 | 11099.0879 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 9.1705 | 9070.4539 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 8.9024 | 8802.3975 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6617 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.6145 | 45.7994 | 45699.4112 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.6145 | 22.4458 | 22345.768 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4558 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 13.2782 | 41.9813 | 41881.2561 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 20.2499 | 21.1155 | 21015.4837 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 20.2499 | 21.0465 | 20946.4863 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 20.2499 | 19.3564 | 19256.3957 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 20.2499 | 18.8802 | 18780.2052 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 9.1668 | 20.1752 | 20075.2253 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549958 [MAIN STREET5161.00] CKT 1 | 27.2084 | 0.2212 | 121.1522 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 18.295 | 18194.96 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 18.295 | 18194.96 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 18.295 | 18194.96 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 18.0296 | 17929.5716 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1384 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1384 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1384 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 21.7431 | 20.4493 | 20349.2964 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4724 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6885 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 33.9414 | 246.7512 | 246651.1527 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3082 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4135 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 11.1991 | 11099.0817 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 9.1704 | 9070.4415 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 8.9024 | 8802.3862 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6507 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.6141 | 45.8012 | 45701.1557 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.6141 | 22.4455 | 22345.5054 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.2782 | 26.6675 | 26567.5112 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 13.2782 | 41.981 | 41881.0046 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 20.2475 | 21.1161 | 21016.0999 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 20.2475 | 21.0471 | 20947.0739 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 20.2475 | 19.3568 | 19256.8032 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 20.2475 | 18.8805 | 18780.4713 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 9.1535 | 20.1789 | 20078.8698 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549960 [SW DISP PLT5161.00] CKT 1 | 27.2071 | 0.2212 | 121.1857 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9736 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9736 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 18.295 | 18194.9736 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 18.0296 | 17929.585 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1576 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1576 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 19.0602 | 18960.1576 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 21.7432 | 20.4493 | 20349.3257 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.338 | 19.1095 | 19009.491 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.338 | 24.8477 | 24747.7316 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 33.9415 | 246.7521 | 246652.0863 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 13.8103 | 13710.3225 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 12.5214 | 12421.4251 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 11.1991 | 11099.0919 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 9.1705 | 9070.4614 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 8.9024 | 8802.4056 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 12.5059 | 8.6507 | 8550.6695 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.6145 | 45.7982 | 45698.1787 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.6145 | 22.446 | 22345.9678 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.2782 | 26.6675 | 26567.4528 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 13.2782 | 41.9813 | 41881.2881 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 20.2497 | 21.1155 | 21015.5125 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 20.2497 | 21.0465 | 20946.4556 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 20.2497 | 19.3564 | 19256.4004 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 20.2497 | 18.8801 | 18780.1338 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 9.1673 | 20.1755 | 20075.511 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549959 [BATTLEFIELD5161.00] TO BUS 549979 [BATTLEFIELD269.000] TO BUS 549980 [BATLEFLDXF1113.200] CKT 1 | 27.2085 | 0.2211 | 121.143 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 18.2951 | 18195.0868 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 18.2951 | 1819509% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 18.2951 | 18195.0868 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 18.0297 | 1792970% | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 19.0603 | 18960.263 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 19.0603 | 18960.263 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 19.0603 | 18960.263 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 21.7398 | 20.4494 | 20349.4205 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.3377 | 19.1094 | 19009.359 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.3377 | 24.8474 | 24747.4221 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 33.9413 | 246.7461 | 246646.1495 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 13.8104 | 13710.3892 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 12.5215 | 12421.4813 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 11.1991 | 11099.1383 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 9.1706 | 9070.5666 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 8.9025 | 8802.5059 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 12.5052 | 8.6508 | 8550.7657 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.6073 | 45.8206 | 45720.6343 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.6073 | 22.4428 | 22342.8418 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.2781 | 26.6677 | 26567.7457 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 13.2781 | 41.9799 | 41879.916 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 20.2469 | 21.1153 | 21015.3022 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 20.2469 | 21.0461 | 20946.1046 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 20.2469 | 19.3562 | 19256.1898 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 20.2469 | 18.8798 | 18779.7838 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 9.1671 | 20.1762 | 20076.2415 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 300101 [5MORGAN 161.00] CKT 1 | 27.1863 | 0.2212 | 121.1592 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1124 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1124 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 18.2951 | 18195.1124 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 18.0297 | 17929.724 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2791 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2791 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 19.0603 | 18960.2791 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 21.7414 | 20.4494 | 20349.423 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.3379 | 19.1095 | 19009.4783 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.3379 | 24.8477 | 24747.6985 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 33.9415 | 246.7511 | 246651.1488 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 13.8103 | 13710.3281 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 12.5214 | 12421.4297 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 11.1991 | 11099.0955 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 9.1705 | 9070.4759 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 8.9024 | 8802.4178 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 12.5057 | 8.6507 | 8550.6814 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.6134 | 45.8153 | 45715.298 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.6134 | 22.4432 | 22343.2176 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.2782 | 26.6677 | 26567.7126 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 13.2782 | 41.98 | 41880.0151 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 20.2469 | 21.1168 | 21016.7598 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 20.2469 | 21.048 | 20948.0244 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 20.2469 | 19.3573 | 19257.335 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 20.2469 | 18.8812 | 18781.2363 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 9.1638 | 20.1779 | 20077.8984 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549954 [JTEC 5161.00] CKT 1 | 27.191 | 0.2212 | 121.2217 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 18.295 | 18194.9659 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 18.295 | 18194.9659 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 18.295 | 18194.9659 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 18.0296 | 17929.5768 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 19.0602 | 18960.1515 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 21.7431 | 20.4493 | 20349.3218 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.338 | 19.1095 | 19009.5238 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.338 | 24.8478 | 24747.8099 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 33.9415 | 246.7531 | 246653.0527 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 13.8103 | 13710.2819 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3915 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 11.1991 | 11099.064 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 9.1704 | 9070.4026 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 8.9023 | 8802.3477 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 12.5058 | 8.6506 | 8550.6136 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.6144 | 45.7985 | 45698.5392 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.6144 | 22.4459 | 22345.9118 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.2782 | 26.6674 | 26567.4465 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 13.2782 | 41.9813 | 41881.3276 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 20.2496 | 21.1154 | 21015.427 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 20.2496 | 21.0463 | 20946.3288 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 20.2496 | 19.3563 | 19256.3271 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 20.2496 | 18.88 | 18780.0279 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 9.1663 | 20.1749 | 20074.9402 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549955 [JUNCTION 5161.00] CKT 1 | 27.208 | 0.2211 | 121.095 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 18.2952 | 18195.2409 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 18.2952 | 18195.2409 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 18.2952 | 18195.2409 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 18.0298 | 17929.8468 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 19.0604 | 18960.4436 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 19.0604 | 18960.4436 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 19.0604 | 18960.4436 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 21.7408 | 20.4496 | 20349.6477 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.3381 | 19.1096 | 19009.5546 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.3381 | 24.8479 | 24747.8691 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 33.9416 | 246.7541 | 246654.0755 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 13.8103 | 13710.3495 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 12.5214 | 12421.4478 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 11.1991 | 11099.1106 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 9.1705 | 9070.5035 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 8.9024 | 8802.4457 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 12.5056 | 8.6507 | 8550.708 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.6161 | 45.7969 | 45696.8602 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.6161 | 22.4461 | 22346.056 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.2782 | 26.6675 | 26567.5181 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 13.2782 | 41.981 | 41880.9865 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 20.2519 | 21.1163 | 21016.3135 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 20.2519 | 21.048 | 20948.0305 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 20.2519 | 19.3572 | 19257.1771 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 20.2519 | 18.8817 | 18781.6968 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 9.1592 | 20.183 | 20082.9619 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549988 [BRKLNE XF1 113.200] CKT 1 | 27.1864 | 0.2208 | 120.7801 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 18.2952 | 18195.2486 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 18.2952 | 18195.2486 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 18.2952 | 18195.2486 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 18.0299 | 17929.8545 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 19.0605 | 18960.4513 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 19.0605 | 18960.4513 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 19.0605 | 18960.4513 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 21.7408 | 20.4497 | 20349.6558 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.3381 | 19.1096 | 19009.5539 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.3381 | 24.8479 | 24747.8677 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 33.9416 | 246.7541 | 246654.0768 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 13.8104 | 13710.3515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 12.5215 | 12421.4502 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 11.1991 | 11099.1126 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 9.1705 | 9070.5071 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 8.9024 | 8802.4492 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 12.5056 | 8.6507 | 8550.7114 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.6161 | 45.7969 | 45696.895 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.6161 | 22.446 | 22346.0493 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.2782 | 26.6675 | 26567.5215 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 13.2782 | 41.981 | 41880.9694 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 20.2519 | 21.1163 | 21016.3188 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 20.2519 | 21.048 | 20948.0393 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 20.2519 | 19.3572 | 19257.1825 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 20.2519 | 18.8817 | 18781.7045 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 9.1593 | 20.1831 | 20083.0834 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549969 [BROOKLINE 5161.00] TO BUS 549984 [BROOKLINE 7345.00] TO BUS 549989 [BRKLNE XF2 113.200] CKT 2 | 27.1868 | 0.2208 | 120.7783 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0208 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0208 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 18.295 | 18195.0208 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 18.0296 | 17929.6306 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2059 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2059 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 19.0602 | 18960.2059 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 21.7429 | 20.4494 | 20349.3764 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.338 | 19.1095 | 19009.5304 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.338 | 24.8478 | 24747.8183 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 33.9415 | 246.7533 | 246653.3062 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 13.8102 | 13710.2477 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3623 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 11.199 | 11099.0395 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 9.1704 | 9070.352 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 8.9023 | 8802.2996 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 12.5058 | 8.6506 | 8550.5669 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.6146 | 45.7979 | 45697.8626 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.6146 | 22.446 | 22346.0128 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4779 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 13.2782 | 41.9811 | 41881.1444 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 20.248 | 21.1164 | 21016.3559 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 20.248 | 21.0478 | 20947.7726 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 20.248 | 19.3571 | 19257.0936 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 20.248 | 18.8812 | 18781.2397 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 9.1579 | 20.1823 | 20082.3052 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 301161 [5LOGAN 161.00] CKT 1 | 27.2071 | 0.2211 | 121.0754 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 18.295 | 18194.9678 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 18.295 | 18194.9678 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 18.295 | 18194.9678 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 18.0296 | 17929.5784 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 19.0601 | 18960.1496 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 19.0601 | 18960.1496 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 19.0601 | 18960.1496 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 21.743 | 20.4493 | 20349.3153 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.338 | 19.1095 | 19009.5237 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.338 | 24.8478 | 24747.8073 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 33.9414 | 246.7532 | 246653.2077 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 13.8103 | 13710.2898 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 12.5214 | 12421.3974 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 11.1991 | 11099.0691 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 9.1704 | 9070.414 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 8.9024 | 8802.3587 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 12.5058 | 8.6506 | 8550.6242 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.6136 | 45.8028 | 45702.771 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.6136 | 22.4452 | 22345.2303 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.2781 | 26.6675 | 26567.4589 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 13.2781 | 41.9813 | 41881.2569 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 20.2493 | 21.1156 | 21015.5594 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 20.2493 | 21.0466 | 20946.6213 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 20.2493 | 19.3565 | 19256.4605 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 20.2493 | 18.8803 | 18780.3254 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 9.1652 | 20.1767 | 20076.715 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549962 [MILL 5161.00] CKT 1 | 27.2077 | 0.2212 | 121.1513 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 18.295 | 18195.0002 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 18.295 | 18195.0002 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 18.295 | 18195.0002 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 18.0296 | 17929.6115 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1851 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1851 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 19.0602 | 18960.1851 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 21.7432 | 20.4494 | 20349.3531 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.338 | 19.1095 | 19009.4815 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.338 | 24.8477 | 24747.7101 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 33.9415 | 246.7522 | 246652.243 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 13.8103 | 13710.3263 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 12.5214 | 12421.4289 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 11.1991 | 11099.0945 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 9.1705 | 9070.468 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 8.9024 | 8802.411 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 12.5059 | 8.6507 | 8550.6755 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.6145 | 45.8006 | 45700.6289 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.6145 | 22.4456 | 22345.5575 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.2782 | 26.6675 | 26567.4734 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 13.2782 | 41.9812 | 41881.1773 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 20.2501 | 21.1157 | 21015.7344 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 20.2501 | 21.0469 | 20946.8581 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 20.2501 | 19.3566 | 19256.6017 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 20.2501 | 18.8805 | 18780.5127 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 9.1668 | 20.1777 | 2007766% | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 549970 [CLAY 5161.00] TO BUS 549963 [MENTOR 5161.00] CKT 1 | 27.2087 | 0.2211 | 121.1333 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 18.295 | 1819500% | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 18.295 | 18194.9981 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 18.295 | 18194.9981 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 18.0296 | 17929.6089 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1843 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 21.7433 | 20.4494 | 20349.3554 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.3325 | 19.0901 | 18990.0855 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.3325 | 24.8144 | 24714.4081 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 33.9403 | 246.7391 | 246639.1217 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3382 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4392 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 11.1991 | 11099.1029 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4861 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4285 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 12.5059 | 8.6507 | 8550.6918 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.6149 | 45.7967 | 45696.695 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1911 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.2782 | 26.6674 | 26567.4473 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3254 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 20.2503 | 21.1157 | 21015.6625 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 20.2503 | 21.0468 | 20946.8052 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 20.2503 | 19.3566 | 19256.5593 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 20.2503 | 18.8805 | 18780.5041 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 9.168 | 20.178 | 20077.9677 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 523215 [GEN-2011-022345.00] CKT 1 | 27.2091 | 0.2211 | 121.1225 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 18.295 | 18194.9925 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 18.295 | 18194.9925 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 18.295 | 18194.9925 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 18.0296 | 17929.6035 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1783 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1783 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 19.0602 | 18960.1783 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 21.7433 | 20.4493 | 20349.3481 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.3265 | 19.0691 | 18969.1466 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.3265 | 24.7785 | 24678.5295 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 33.939 | 246.7267 | 246626.6956 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 13.8103 | 13710.3362 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 12.5214 | 12421.4374 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 11.1991 | 11099.1014 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 9.1705 | 9070.4831 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 8.9024 | 8802.4256 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 12.5059 | 8.6507 | 8550.689 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.6149 | 45.7967 | 45696.6936 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.6149 | 22.4462 | 22346.1862 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.2782 | 26.6674 | 26567.4472 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 13.2782 | 41.9813 | 41881.3255 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 20.2502 | 21.1156 | 21015.6487 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 20.2502 | 21.0468 | 20946.7799 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 20.2502 | 19.3565 | 19256.5465 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 20.2502 | 18.8805 | 18780.4799 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 9.168 | 20.178 | 20077.9628 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 576397 [G10014G11022345.00] TO BUS 576395 [GEN-2010-014345.00] CKT 1 | 27.209 | 0.2211 | 121.1247 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 18.2949 | 18194.9361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 18.2949 | 18194.9361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 18.2949 | 18194.9361 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 18.0296 | 17929.55 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 19.0601 | 18960.1055 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 21.743 | 20.4492 | 20349.2481 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3383 | 19.1097 | 19009.675 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.3383 | 24.8482 | 24748.182 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 33.9416 | 246.7535 | 246653.5213 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 13.8108 | 13710.8413 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 12.5219 | 12421.8652 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 11.1995 | 11099.4553 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 9.1712 | 9071.2287 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 8.9031 | 8803.1477 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 12.5066 | 8.6514 | 8551.3884 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6162 | 45.7981 | 45698.0641 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.6162 | 22.4459 | 22345.8663 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2783 | 26.6677 | 26567.7462 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 13.2783 | 41.9799 | 41879.8547 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2533 | 21.1279 | 21027.9141 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2533 | 21.0631 | 20963.113 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2533 | 19.366 | 19265.9894 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 20.2533 | 18.8926 | 18792.6312 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 9.191 | 20.4348 | 20334.79 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 588980 [GEN-2017-060161.00] TO BUS 547479 [LAR382 5 161.00] CKT 1 | 27.2029 | 0.2213 | 121.3275 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 18.2949 | 18194.9411 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 18.0296 | 17929.555 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 19.0601 | 18960.111 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 21.743 | 20.4493 | 20349.2546 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.3383 | 19.1097 | 19009.6762 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.3383 | 24.8482 | 24748.1816 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 33.9416 | 246.755 | 246655.0101 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 13.8108 | 13710.8435 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 12.5219 | 12421.8672 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 11.1995 | 11099.4568 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 9.1712 | 9071.232 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 8.9032 | 8803.1501 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 12.5066 | 8.6514 | 8551.3915 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.6162 | 45.798 | 45698.0249 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.6162 | 22.4459 | 22345.8676 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.2783 | 26.6678 | 26567.7526 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 13.2783 | 41.9798 | 41879.8227 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 20.2535 | 21.1284 | 21028.3645 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 20.2535 | 21.0639 | 20963.8513 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 20.2535 | 19.3664 | 19266.3819 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 20.2535 | 18.8933 | 18793.2886 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 9.1893 | 20.4454 | 20345.377 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 588981 [G17-060XFMR134.500] TO BUS 588982 [G17-060-GSU134.500] CKT 1 | 27.203 | 0.2213 | 121.3247 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 18.3018 | 18201.8053 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 18.3018 | 18201.8053 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 18.3018 | 18201.8053 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 18.0365 | 17936.53 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 19.0659 | 18965.9174 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 19.0659 | 18965.9174 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 19.0659 | 18965.9174 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 21.7339 | 20.4535 | 20353.4735 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.3432 | 19.1125 | 19012.4891 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.3432 | 24.8547 | 24754.6773 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 33.9461 | 246.8086 | 246708.6052 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 13.809 | 13709.0118 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 12.5198 | 12419.7586 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 11.198 | 11098.0194 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 9.1709 | 9070.9464 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 8.9025 | 8802.4545 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 12.4898 | 8.6503 | 8550.3328 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.6163 | 45.8471 | 45747.0713 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.6163 | 22.4378 | 22337.7871 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.2781 | 26.7304 | 26630.3726 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 13.2781 | 41.6834 | 41583.4235 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 20.2562 | 21.1182 | 21018.1647 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 20.2562 | 21.0513 | 20951.2837 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 20.2562 | 19.3589 | 19258.8717 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 20.2562 | 18.8847 | 18784.7477 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 9.1696 | 20.1807 | 20080.6932 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762280 [G17-195XFM1 34.500] CKT 1 | 27.2276 | 0.2205 | 120.5361 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 18.2982 | 18198.1984 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 18.2982 | 18198.1984 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 18.2982 | 18198.1984 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 18.0328 | 17932.7944 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 19.0633 | 18963.272 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 19.0633 | 18963.272 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 19.0633 | 18963.272 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 21.7448 | 20.4523 | 20352.3376 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.3413 | 19.1114 | 19011.3836 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.3413 | 24.8521 | 24752.1311 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 33.9448 | 246.8204 | 246720.4078 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 13.8134 | 13713.362 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 12.5239 | 12423.8615 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 11.2012 | 11101.1794 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 9.1756 | 9075.5623 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 8.9072 | 8807.2347 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 12.5059 | 8.6553 | 8555.2511 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.6168 | 45.8065 | 45706.4817 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.6168 | 22.4444 | 22344.415 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.2783 | 26.6829 | 26582.8869 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 13.2783 | 41.9076 | 41807.5818 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 20.2544 | 21.1173 | 21017.2589 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 20.2544 | 21.0497 | 20949.7358 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 20.2544 | 19.3581 | 19258.0593 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 20.2544 | 18.8833 | 18783.3256 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 9.1691 | 20.1797 | 20079.7407 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 762279 [GEN-2017-195345.00] TO BUS 762300 [GEN-2017-196345.00] CKT 1 | 27.2215 | 0.2207 | 120.7252 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 18.295 | 18195.0425 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 18.295 | 18195.0425 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 18.295 | 18195.0425 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 18.0297 | 17929.6516 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 19.0602 | 18960.2349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 19.0602 | 18960.2349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 19.0602 | 18960.2349 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 21.7434 | 20.4494 | 20349.4186 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.3388 | 19.11 | 19009.9709 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.3388 | 24.8488 | 24748.8466 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 33.9423 | 246.7734 | 246673.4424 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 13.8101 | 13710.1016 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 12.5212 | 12421.2395 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 11.1989 | 11098.9378 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 9.1701 | 9070.1313 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 8.9021 | 8802.0867 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 12.5056 | 8.6504 | 8550.3609 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.6154 | 45.7959 | 45695.9073 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.6154 | 22.4463 | 22346.2743 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.2842 | 26.6658 | 26565.7579 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 13.2842 | 41.9933 | 41893.2773 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 20.2516 | 21.1161 | 21016.149 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 20.2516 | 21.0477 | 20947.713 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 20.2516 | 19.357 | 19257.0215 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 20.2516 | 18.8814 | 18781.3878 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 9.1683 | 20.1785 | 20078.5234 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 762405 [ASG-2018-010161.00] TO BUS 762406 [A18-010-XFM134.500] CKT 1 | 27.2122 | 0.221 | 121.0234 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 18.2949 | 18194.9091 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 18.2949 | 18194.9091 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 18.2949 | 18194.9091 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 18.0295 | 17929.521 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 19.0601 | 18960.092 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 19.0601 | 18960.092 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 19.0601 | 18960.092 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 21.7428 | 20.4493 | 20349.2553 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.3378 | 19.1094 | 19009.3957 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.3378 | 24.8475 | 24747.5122 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 33.9413 | 246.7495 | 246649.5181 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 13.8103 | 13710.2949 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 12.5214 | 12421.4041 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 11.1991 | 11099.0749 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 9.1704 | 9070.4131 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 8.9024 | 8802.3588 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 12.5053 | 8.6506 | 8550.6259 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.4705 | 43.4309 | 43330.9132 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.4705 | 22.9006 | 22800.6433 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.2779 | 26.6671 | 26567.1057 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 13.2779 | 41.983 | 41883.0089 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.25 | 21.1157 | 21015.663 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.25 | 21.0468 | 2094679% | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.25 | 19.3566 | 19256.552 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 20.25 | 18.8805 | 1878048% | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 9.1678 | 20.1781 | 20078.1201 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 300692 [2CLINTN 69.000] CKT 1 | 27.2068 | 0.2212 | 121.1768 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 18.2955 | 18195.5037 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 18.2955 | 18195.5037 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 18.2955 | 18195.5037 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 18.0301 | 17930.1152 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 19.0606 | 18960.6482 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 19.0606 | 18960.6482 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 19.0606 | 18960.6482 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.7351 | 20.4498 | 20349.7633 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.3386 | 19.1099 | 19009.9384 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.3386 | 24.8487 | 24748.7155 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 33.9416 | 246.7497 | 246649.6991 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 13.8104 | 13710.4107 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 12.5215 | 12421.4975 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 11.1992 | 11099.1522 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 9.1706 | 9070.6026 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 8.9025 | 8802.5401 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.5052 | 8.6508 | 8550.7988 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.6145 | 45.8039 | 45703.854 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.6145 | 22.445 | 22345.0255 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.278 | 26.668 | 26568.0201 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.278 | 41.9786 | 41878.5646 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2431 | 21.1192 | 21019.161 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2431 | 21.0513 | 20951.2618 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2431 | 19.3592 | 19259.2078 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.2431 | 18.8837 | 18783.6914 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 9.1653 | 20.1796 | 20079.5908 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 27.123 | 0.2214 | 121.4406 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 18.2952 | 18195.1898 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 18.0298 | 17929.7996 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 19.0604 | 18960.3632 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 19.0604 | 18960.3632 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 19.0604 | 18960.3632 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 21.7409 | 20.4495 | 20349.5193 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 11.4189 | 20.5349 | 20434.8609 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 11.4189 | 26.2879 | 26187.9273 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 33.9519 | 246.8268 | 246726.8275 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 13.8101 | 13710.1489 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 12.5213 | 12421.2769 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 11.199 | 11098.9694 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 9.1702 | 9070.2137 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 8.9022 | 8802.1644 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 12.5051 | 8.6504 | 8550.4348 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.6148 | 45.7971 | 45697.1019 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.6148 | 22.4461 | 22346.1225 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.2782 | 26.6677 | 26567.6665 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 13.2782 | 41.9802 | 41880.2263 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2507 | 21.1162 | 21016.2005 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2507 | 21.0477 | 20947.6889 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2507 | 19.357 | 19257.0321 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 20.2507 | 18.8813 | 18781.2974 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 9.168 | 20.1782 | 20078.1695 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 515677 [BADGER 7 345.00] CKT 1 | 27.2058 | 0.2211 | 121.079 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 18.295 | 18195.0038 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 18.0296 | 17929.6137 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.1884 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.1884 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 19.0602 | 18960.1884 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 21.743 | 20.4494 | 20349.3588 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.1159 | 19.1712 | 19071.2111 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.1159 | 24.9218 | 24821.7931 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 33.9399 | 246.69 | 246589.9614 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 13.8104 | 13710.3519 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 12.5215 | 12421.4505 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 11.1991 | 11099.1129 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 9.1705 | 9070.5058 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 8.9024 | 8802.4483 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 12.5059 | 8.6507 | 8550.7109 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.6149 | 45.7967 | 45696.6952 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.6149 | 22.4462 | 22346.1885 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2782 | 26.6675 | 26567.4566 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 13.2782 | 41.9813 | 41881.2787 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2502 | 21.1156 | 21015.6497 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2502 | 21.0468 | 20946.7774 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2502 | 19.3565 | 19256.5467 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 20.2502 | 18.8805 | 18780.4747 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 9.168 | 20.178 | 20077.9521 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523961 [POTTER_CO 7345.00] TO BUS 523959 [POTTER_CO 6230.00] CKT 1 | 27.2085 | 0.2211 | 121.1282 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 18.2932 | 18193.1647 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 18.2932 | 18193.1647 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 18.2932 | 18193.1647 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 18.0278 | 17927.81 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 19.0583 | 18958.3225 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 19.0583 | 18958.3225 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 19.0583 | 18958.3225 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 21.7148 | 20.4474 | 20347.4045 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.3381 | 19.1096 | 19009.5643 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.3381 | 24.8479 | 24747.8831 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 33.9404 | 246.7198 | 246619.8234 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 13.8172 | 13717.1686 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 12.5274 | 12427.3507 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 11.2042 | 11104.2111 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 9.1796 | 9079.6368 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 8.9113 | 8811.303 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 12.3479 | 8.6593 | 8559.3067 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.611 | 45.8168 | 45716.8001 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.611 | 22.4432 | 22343.1622 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.2676 | 26.6602 | 26560.2162 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 13.2676 | 42.022 | 41922.0158 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2497 | 21.1155 | 21015.5259 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2497 | 21.0466 | 20946.5544 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2497 | 19.3564 | 19256.4294 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 20.2497 | 18.8803 | 18780.2604 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 9.1679 | 20.1778 | 20077.8422 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 542978 [CRAIG 5 161.00] TO BUS 543038 [LENEXA 5 161.00] CKT 1 | 27.2059 | 0.2212 | 121.1788 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 18.2949 | 18194.9186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 18.2949 | 18194.9186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 18.2949 | 18194.9186 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 18.0295 | 17929.531 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1039 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1039 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 19.0601 | 18960.1039 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 21.7431 | 20.4493 | 20349.2721 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3375 | 19.1092 | 19009.2133 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.3375 | 24.8471 | 24747.0822 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 33.9413 | 246.746 | 246646.0055 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 13.8099 | 13709.9379 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 12.5211 | 12421.0995 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 11.1988 | 11098.823 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 9.1699 | 9069.8955 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 8.9019 | 8801.8571 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 12.5054 | 8.6501 | 8550.1389 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6123 | 45.8107 | 45710.7 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.6123 | 22.4441 | 22344.0708 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.2782 | 26.6673 | 26567.3482 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 13.2782 | 41.9818 | 41881.7824 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 19.7766 | 21.034 | 20934.0173 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 19.7766 | 20.9394 | 20839.3648 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 19.7766 | 19.2845 | 19184.4579 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 19.7766 | 18.7884 | 18688.3815 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 9.0075 | 20.2785 | 20178.4771 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25SP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 547498 [STL439 5 161.00] TO BUS 547483 [JOP389 5 161.00] CKT 1 | 27.2009 | 0.2214 | 121.419 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 18.3209 | 18220.9222 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 18.3209 | 18220.9222 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 18.3209 | 18220.9222 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 18.0562 | 17956.2451 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 19.0804 | 18980.4146 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 19.0804 | 18980.4146 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 19.0804 | 18980.4146 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | Base | 20.8781 | 20.4608 | 20360.7688 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | Base | 12.9013 | 19.1737 | 19073.7185 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | Base | 12.9013 | 24.9206 | 24820.5556 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | Base | 33.591 | 47535.0565 | 47534956.5087 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 11.4235 | 13.8915 | 13791.4519 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 11.4235 | 12.5867 | 12486.7281 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | Base | 11.4235 | 11.2544 | 11154.3843 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 11.4235 | 9.3065 | 9206.5383 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 11.4235 | 9.0316 | 8931.5599 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | Base | 11.4235 | 8.7735 | 8673.4907 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | Base | 13.5749 | 46.9165 | 46816.4952 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | Base | 13.5749 | 22.2713 | 22171.2994 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | Base | 12.3754 | 29.028 | 28928.0481 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | Base | 12.3754 | 34.7341 | 34634.1306 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.0241 | 21.1476 | 21047.596 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.0241 | 21.0903 | 20990.3362 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.0241 | 19.3794 | 19279.4429 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | Base | 20.0241 | 18.9109 | 18810.9105 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | Base | 8.1939 | 20.9785 | 20878.4982 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | Base | 26.8861 | 0.2257 | 125.7145 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 18.3214 | 18221.4481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 18.3214 | 18221.4481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 18.3214 | 18221.4481 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 18.0568 | 17956.773 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 19.0809 | 18980.8951 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 19.0809 | 18980.8951 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 19.0809 | 18980.8951 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.8713 | 20.4612 | 20361.1906 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.9013 | 19.1737 | 19073.687 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.9013 | 24.9205 | 24820.4781 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 33.591 | 47713.1365 | 47713036.4502 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 13.8916 | 13791.6461 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 12.5869 | 12486.8807 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 11.2545 | 11154.5168 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 9.3069 | 9206.88 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 9.0319 | 8931.8809 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 11.4201 | 8.7738 | 8673.7928 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 6.0809 | 16.758 | 16658.0344 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 6.0809 | 12.6219 | 12521.8669 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.3738 | 29.0352 | 28935.2026 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 12.3738 | 34.7191 | 34619.1256 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.023 | 21.148 | 21047.9757 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.023 | 21.0908 | 20990.8497 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.023 | 19.3797 | 19279.7314 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 20.023 | 18.9113 | 18811.29 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 8.1931 | 20.9795 | 20879.4542 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300071 [5CLINTN 161.00] TO BUS 541217 [WINDSR 5 161.00] CKT 1 | 26.8818 | 0.2257 | 125.7205 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 18.321 | 18221.0057 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 18.321 | 18221.0057 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 18.321 | 18221.0057 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 18.0563 | 17956.327 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 19.0805 | 18980.4974 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 19.0805 | 18980.4974 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 19.0805 | 18980.4974 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.8777 | 20.4609 | 20360.8537 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.9013 | 19.1737 | 19073.6864 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.9013 | 24.9205 | 24820.4792 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 33.591 | 47535.1255 | 47535025.4936 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 13.8916 | 13791.6061 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 12.5869 | 12486.8562 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 11.2545 | 11154.4906 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 9.3068 | 9206.7769 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 9.0318 | 8931.7888 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 11.4232 | 8.7737 | 8673.7113 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.4196 | 47.5265 | 47426.4865 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 13.4196 | 22.2034 | 22103.3518 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.3754 | 29.0287 | 2892870% | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 12.3754 | 34.7328 | 34632.7927 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.0239 | 21.1475 | 2104754% | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.0239 | 21.0902 | 20990.2326 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.0239 | 19.3794 | 19279.39 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 20.0239 | 18.9108 | 18810.807 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 8.1938 | 20.9783 | 20878.3416 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 300541 [2SEDALI 69.000] CKT 3 | 26.8855 | 0.2257 | 125.7361 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 18.3207 | 18220.7405 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 18.3207 | 18220.7405 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 18.3207 | 18220.7405 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 18.0561 | 17956.0653 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 19.0802 | 18980.2359 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 19.0802 | 18980.2359 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 19.0802 | 18980.2359 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.8752 | 20.4606 | 20360.5902 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.9017 | 19.1739 | 19073.9271 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.9017 | 24.921 | 24821.0397 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 33.5911 | 47447.2824 | 47447182.4447 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 13.8911 | 13791.0857 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 12.5864 | 12486.4202 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 11.2541 | 11154.1301 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 9.306 | 9205.9839 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 9.031 | 8931.0244 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 11.422 | 8.773 | 8672.9734 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 9.8572 | 62.1197 | 62019.7401 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 9.8572 | 18.6698 | 18569.7706 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.3744 | 29.027 | 28926.9688 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 12.3744 | 34.7364 | 34636.4394 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.0229 | 21.1476 | 21047.5561 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.0229 | 21.0902 | 20990.2186 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.0229 | 19.3794 | 19279.3882 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 20.0229 | 18.9108 | 18810.769 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 8.1929 | 20.9781 | 20878.1365 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300117 [5SEDALA 161.00] TO BUS 541209 [SEDALIA5 161.00] CKT 1 | 26.8838 | 0.2257 | 125.7003 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9365 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9365 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9365 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 18.0563 | 17956.2588 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4299 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4299 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4299 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8779 | 20.4608 | 20360.7887 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.9013 | 19.1737 | 19073.6751 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.9013 | 24.9205 | 24820.4522 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 33.591 | 47535.0257 | 47534925.7462 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 13.8915 | 13791.4689 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 12.5867 | 12486.743 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 11.2544 | 11154.396 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 9.3066 | 9206.5636 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 9.0316 | 8931.5843 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 8.7735 | 8673.5142 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.5749 | 46.9162 | 46816.2499 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.5749 | 22.2713 | 22171.334 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.3754 | 29.028 | 28928.0409 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.3754 | 34.7342 | 34634.1706 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0237 | 21.1474 | 21047.3691 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0237 | 21.09 | 20989.964 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0237 | 19.3792 | 19279.2418 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0237 | 18.9106 | 18810.5754 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 8.1925 | 20.9754 | 20875.4044 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300678 [5NIXA-1 161.00] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 26.8855 | 0.2257 | 125.6802 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 18.3258 | 18225.7658 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 18.3258 | 18225.7658 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 18.3258 | 18225.7658 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 18.0612 | 17961.1618 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 19.0846 | 18984.6175 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 19.0846 | 18984.6175 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 19.0846 | 18984.6175 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.7278 | 20.464 | 20364.0387 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.8965 | 19.1712 | 19071.207 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.8965 | 24.9146 | 24814.5864 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 33.5886 | 52466.7942 | 52466694.2259 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 13.891 | 13790.9942 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 12.5863 | 12486.2962 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 11.254 | 11154.0437 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 9.3061 | 9206.0748 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 9.0311 | 8931.0789 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.4057 | 8.773 | 8672.9951 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.5674 | 47.0229 | 46922.8755 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.5674 | 22.2557 | 22155.699 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.3695 | 29.045 | 28944.9592 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.3695 | 34.698 | 34598.0314 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 19.9587 | 21.1568 | 21056.8465 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 19.9587 | 21.0997 | 20999.7253 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 19.9587 | 19.3854 | 19285.3509 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 19.9587 | 18.9152 | 18815.2417 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 8.1836 | 20.9809 | 20880.9392 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 25.141 | 0.2284 | 128.38 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 18.312 | 18211.9943 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 18.312 | 18211.9943 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 18.312 | 18211.9943 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 18.0476 | 17947.6186 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 19.0705 | 18970.5441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 19.0705 | 18970.5441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 19.0705 | 18970.5441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.7056 | 20.4491 | 20349.1337 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.9042 | 19.1763 | 19076.3248 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.9042 | 24.9261 | 24826.1067 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 33.5894 | 51137.5823 | 51137482.274 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 13.8751 | 13775.0633 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 12.5728 | 12472.8472 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 11.2429 | 11142.9353 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 9.2822 | 9182.2203 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 9.008 | 8908.0341 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.3974 | 8.7507 | 8650.7046 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.5212 | 47.6413 | 47541.2526 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.5212 | 22.1686 | 22068.5775 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.3571 | 29.0361 | 28936.1302 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.3571 | 34.7123 | 34612.3053 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 19.9736 | 21.1403 | 21040.336 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 19.9736 | 21.0752 | 20975.2293 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 19.9736 | 19.3717 | 19271.7007 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 19.9736 | 18.8949 | 18794.8687 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 8.1296 | 20.9915 | 20891.5013 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 24.6242 | 0.2234 | 123.4249 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 18.326 | 18225.9817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 18.326 | 18225.9817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 18.326 | 18225.9817 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 18.0613 | 17961.3162 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 19.0852 | 18985.2465 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 19.0852 | 18985.2465 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 19.0852 | 18985.2465 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.7435 | 20.4654 | 20365.3671 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.9009 | 19.1738 | 19073.8185 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.9009 | 24.9206 | 24820.64 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 33.5907 | 48768.0854 | 48767985.4167 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 13.8906 | 13790.5855 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 12.586 | 12485.9788 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 11.2538 | 11153.778 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 9.3053 | 9205.3191 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 9.0304 | 8930.3675 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.4106 | 8.7723 | 8672.3238 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.5697 | 46.9892 | 46889.2021 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.5697 | 22.2607 | 22160.7253 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.3676 | 29.039 | 28939.0292 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.3676 | 34.7113 | 34611.2874 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.7535 | 21.2292 | 21129.2332 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.7535 | 21.1954 | 21095.4064 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.7535 | 19.4395 | 19339.5086 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 19.7535 | 18.9839 | 18883.886 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 8.1899 | 20.9715 | 20871.5051 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 23.9806 | 0.2294 | 129.4481 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 18.321 | 18220.978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 18.321 | 18220.978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 18.321 | 18220.978 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 18.0563 | 17956.2991 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 19.0805 | 18980.4701 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 19.0805 | 18980.4701 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 19.0805 | 18980.4701 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8769 | 20.4608 | 20360.8279 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.9009 | 19.1735 | 19073.5119 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.9009 | 24.9201 | 24820.0704 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 33.5907 | 47624.0217 | 47623921.6551 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 13.8915 | 13791.5099 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 12.5868 | 12486.7762 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 11.2544 | 11154.4241 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 9.3066 | 9206.6266 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 9.0316 | 8931.6448 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 8.7736 | 8673.5725 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.5743 | 46.9179 | 46817.8568 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.5743 | 22.2711 | 22171.1108 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.3746 | 29.0299 | 28929.8874 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.3746 | 34.7303 | 34630.2968 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0074 | 21.1458 | 21045.8026 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0074 | 21.0872 | 20987.2269 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0074 | 19.3777 | 19277.7249 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0074 | 18.9079 | 18807.9014 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 7.9146 | 21.2576 | 21157.5811 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 26.8834 | 0.2257 | 125.7165 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 18.321 | 18221.0196 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 18.321 | 18221.0196 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 18.321 | 18221.0196 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 18.0563 | 17956.3397 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 19.0805 | 18980.5203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 19.0805 | 18980.5203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 19.0805 | 18980.5203 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 20.8779 | 20.4609 | 20360.8923 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.9006 | 19.1733 | 19073.2516 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.9006 | 24.9195 | 24819.4649 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 33.591 | 47668.2897 | 47668189.7193 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 13.8914 | 13791.3798 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 12.5867 | 12486.6667 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 11.2543 | 11154.3336 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 9.3064 | 9206.4319 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 9.0315 | 8931.4569 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 11.4234 | 8.7734 | 8673.3907 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.5741 | 46.9191 | 46819.1204 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 13.5741 | 22.271 | 22170.9574 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.375 | 29.0282 | 28928.1556 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 12.375 | 34.7339 | 34633.8645 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.7775 | 21.1858 | 21085.8149 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.7775 | 21.1414 | 21041.4345 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.7775 | 19.406 | 19305.95 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 19.7775 | 18.945 | 18844.9799 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 8.1832 | 20.9555 | 20855.5286 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505486 [NEO SPA5 161.00] TO BUS 547472 [TIP292 5 161.00] CKT 1 | 26.884 | 0.2258 | 125.7786 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8919 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8919 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8919 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 18.0562 | 17956.2165 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3765 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3765 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3765 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.8776 | 20.4607 | 20360.718 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.9013 | 19.1738 | 19073.7607 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.9013 | 24.9207 | 24820.6574 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 33.5907 | 47535.1137 | 47535013.7173 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 13.8914 | 13791.3609 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 12.5867 | 12486.6504 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 11.2543 | 11154.3201 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 9.3064 | 9206.4047 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 9.0314 | 8931.4304 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 11.4232 | 8.7734 | 867336% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.5738 | 46.9195 | 46819.477 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 13.5738 | 22.2709 | 2217091% | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.3749 | 29.0279 | 28927.9251 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 12.3749 | 34.7344 | 34634.3791 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0088 | 21.1368 | 21036.7604 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0088 | 21.0757 | 20975.7389 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0088 | 19.3706 | 19270.6272 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 20.0088 | 18.8994 | 18799.3643 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 8.1687 | 20.9302 | 20830.1558 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505487 [CRG X1 1 13.800] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505488 [CARTHAG5 161.00] CKT 1 | 26.8829 | 0.2258 | 125.7729 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9485 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9485 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 18.3209 | 18220.9485 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 18.0563 | 17956.2707 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4416 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4416 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 19.0804 | 18980.4416 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 20.8779 | 20.4608 | 20360.7994 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.9014 | 19.1738 | 19073.7755 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.9014 | 24.9207 | 24820.687 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 33.591 | 47447.0751 | 47446975.1019 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 13.8913 | 13791.3333 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 12.5866 | 12486.6275 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 11.2543 | 11154.3013 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 9.3064 | 9206.3624 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 9.0314 | 8931.3897 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 11.4233 | 8.7733 | 8673.3257 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.5739 | 46.9224 | 46822.3702 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 13.5739 | 22.2705 | 22170.4593 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.3751 | 29.0282 | 28928.1614 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 12.3751 | 34.7339 | 34633.8555 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.6332 | 21.2259 | 21125.9076 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.6332 | 21.1968 | 21096.7641 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.6332 | 19.4352 | 19335.2193 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 19.6332 | 18.9845 | 18884.5011 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 7.491 | 21.6251 | 21525.0703 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547466 [ATL109 5 161.00] CKT 1 | 26.8844 | 0.2258 | 125.7603 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 18.3211 | 18221.0761 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 18.3211 | 18221.0761 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 18.3211 | 18221.0761 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 18.0564 | 17956.3992 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 19.0806 | 18980.5502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 19.0806 | 18980.5502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 19.0806 | 18980.5502 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.8733 | 20.4609 | 20360.8807 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.9012 | 19.1736 | 19073.6282 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.9012 | 24.9203 | 24820.3417 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 33.591 | 47624.2782 | 47624178.1579 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 13.8914 | 13791.4432 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 12.5867 | 12486.7168 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 11.2544 | 11154.3753 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 9.3065 | 9206.5436 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 9.0316 | 8931.562 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 11.422 | 8.7735 | 8673.4905 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.5745 | 46.9174 | 46817.4308 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 13.5745 | 22.2712 | 22171.1917 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.3677 | 29.0499 | 28949.93 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 12.3677 | 34.6881 | 34588.1475 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.01 | 21.1468 | 21046.8023 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.01 | 21.0886 | 20988.6499 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.01 | 19.3786 | 19278.6152 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 20.01 | 18.9092 | 18809.152 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 7.9793 | 21.2096 | 21109.6371 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 547485 [CAR395 5 161.00] CKT 1 | 26.8817 | 0.2258 | 125.7908 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 18.3209 | 18220.8932 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 18.3209 | 18220.8932 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 18.3209 | 18220.8932 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 18.0562 | 17956.2178 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 19.0804 | 18980.3781 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 19.0804 | 18980.3781 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 19.0804 | 18980.3781 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.8776 | 20.4607 | 20360.7199 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.9013 | 19.1738 | 19073.7602 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.9013 | 24.9207 | 24820.6551 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 33.5907 | 47535.1134 | 47535013.4298 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 13.8914 | 13791.3643 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 12.5867 | 12486.6533 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 11.2543 | 11154.3225 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 9.3064 | 9206.4091 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 9.0314 | 8931.4347 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 11.4232 | 8.7734 | 8673.3691 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.5739 | 46.9193 | 46819.3338 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 13.5739 | 22.2709 | 22170.9242 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.3749 | 29.0279 | 28927.931 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 12.3749 | 34.7344 | 34634.3669 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.0092 | 21.1371 | 21037.0778 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.0092 | 21.0762 | 20976.1682 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.0092 | 19.3709 | 19270.8863 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 20.0092 | 18.8997 | 18799.7037 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 8.1695 | 20.9315 | 20831.5437 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505488 [CARTHAG5 161.00] TO BUS 505490 [CARTHG 2 69.000] TO BUS 505489 [CRG X2 1 13.800] CKT 1 | 26.883 | 0.2258 | 125.7709 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 18.0562 | 17956.2459 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.8781 | 20.4608 | 20360.7695 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.9013 | 19.1737 | 19073.7198 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.9013 | 24.9206 | 24820.5604 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 33.591 | 47535.0591 | 47534959.0958 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 13.8915 | 13791.4515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 12.5867 | 12486.7277 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 11.2544 | 11154.384 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 9.3065 | 9206.5377 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 9.0316 | 8931.5593 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 11.4235 | 8.7735 | 8673.4901 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.5749 | 46.9161 | 46816.09 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 13.5749 | 22.2714 | 22171.3622 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.3754 | 29.0281 | 28928.0522 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 12.3754 | 34.7341 | 34634.131 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0241 | 21.1476 | 21047.599 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0241 | 21.0903 | 20990.3406 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0241 | 19.3794 | 19279.4437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 20.0241 | 18.9109 | 18810.9149 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 8.1939 | 20.9784 | 20878.4223 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505491 [SPF X1 1 13.800] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505492 [SPRGFLD5 161.00] CKT 1 | 26.8861 | 0.2257 | 125.714 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 18.321 | 18220.9634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 18.321 | 18220.9634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 18.321 | 18220.9634 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 18.0563 | 17956.2851 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 19.0805 | 18980.4583 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 19.0805 | 18980.4583 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 19.0805 | 18980.4583 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.8776 | 20.4608 | 20360.8195 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.9011 | 19.1736 | 19073.5837 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.9011 | 24.9202 | 24820.2416 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 33.591 | 47579.8313 | 47579731.3191 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 13.8915 | 13791.4999 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 12.5868 | 12486.7683 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 11.2544 | 11154.4173 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 9.3066 | 9206.6099 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 9.0316 | 8931.629 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 11.4235 | 8.7736 | 8673.5573 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.5748 | 46.9188 | 46818.7843 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 13.5748 | 22.271 | 22170.9624 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.3754 | 29.0281 | 28928.0677 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 12.3754 | 34.7341 | 34634.1285 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.023 | 21.1472 | 21047.1828 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.023 | 21.0895 | 20989.5292 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.023 | 19.379 | 19279.0435 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 20.023 | 18.9101 | 18810.1142 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 8.1922 | 20.9727 | 20872.6634 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505496 [NIXA 5 161.00] CKT 1 | 26.8839 | 0.2256 | 125.644 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 18.3209 | 18220.9107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 18.3209 | 18220.9107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 18.3209 | 18220.9107 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 18.0562 | 17956.2339 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 19.0804 | 18980.4005 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 19.0804 | 18980.4005 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 19.0804 | 18980.4005 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.878 | 20.4608 | 20360.7515 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.9013 | 19.1737 | 19073.7215 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.9013 | 24.9206 | 24820.5644 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 33.5911 | 47535.0453 | 47534945.2979 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 13.8914 | 13791.4405 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 12.5867 | 12486.7183 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 11.2544 | 11154.3757 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 9.3065 | 9206.5208 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 9.0315 | 8931.543 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 11.4235 | 8.7735 | 8673.4743 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.5747 | 46.9172 | 46817.192 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 13.5747 | 22.2712 | 22171.2075 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.3754 | 29.0281 | 28928.0787 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 12.3754 | 34.7341 | 34634.0682 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.0223 | 21.1477 | 21047.7164 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.0223 | 21.0904 | 20990.4247 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.0223 | 19.3795 | 19279.4995 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 20.0223 | 18.9109 | 18810.9048 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 8.1808 | 20.9774 | 20877.36 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549959 [BATTLEFIELD5161.00] CKT 1 | 26.8856 | 0.2257 | 125.7327 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 18.3209 | 18220.9451 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 18.3209 | 18220.9451 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 18.3209 | 18220.9451 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 18.0563 | 17956.2667 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 19.0804 | 18980.441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 19.0804 | 18980.441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 19.0804 | 18980.441 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.8775 | 20.4608 | 20360.8048 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.9013 | 19.1737 | 19073.7097 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.9013 | 24.9205 | 24820.5325 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 33.5911 | 47535.1442 | 47535044.2168 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 13.8915 | 13791.462 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 12.5867 | 12486.737 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 11.2544 | 11154.3916 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 9.3066 | 9206.5529 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 9.0316 | 8931.574 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 11.4234 | 8.7735 | 8673.5041 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.575 | 46.9151 | 46815.0994 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 13.575 | 22.2715 | 22171.5022 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.3754 | 29.028 | 28928.0356 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 12.3754 | 34.7342 | 34634.1814 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.0226 | 21.148 | 21048.0433 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.0226 | 21.0908 | 20990.7568 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.0226 | 19.3797 | 19279.7393 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 20.0226 | 18.9111 | 18811.0987 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 8.1688 | 20.9944 | 20894.4308 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549969 [BROOKLINE 5161.00] CKT 1 | 26.8822 | 0.2256 | 125.6069 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 18.3209 | 18220.8729 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 18.0562 | 17956.1964 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3609 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3609 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 19.0804 | 18980.3609 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.8776 | 20.4607 | 20360.71 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.9015 | 19.1739 | 19073.8553 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.9015 | 24.9209 | 24820.8783 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 33.5909 | 47447.2208 | 47447120.8199 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 13.8913 | 13791.3019 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 12.5866 | 12486.601 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 11.2543 | 1115428% | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 9.3063 | 9206.3147 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 9.0313 | 893134% | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 11.4232 | 8.7733 | 8673.2813 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.5736 | 46.9216 | 46821.635 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 13.5736 | 22.2706 | 22170.5659 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.375 | 29.0281 | 28928.0956 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 12.375 | 34.734 | 34633.9974 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.022 | 21.1476 | 21047.6468 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.022 | 21.0905 | 20990.4866 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.022 | 19.3795 | 19279.4817 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 20.022 | 18.911 | 18811.0499 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 8.1849 | 20.9769 | 20876.8585 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 549970 [CLAY 5161.00] CKT 1 | 26.8852 | 0.2257 | 125.677 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 18.0562 | 17956.2459 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.8781 | 20.4608 | 20360.7695 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.9013 | 19.1737 | 19073.7198 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.9013 | 24.9206 | 24820.5604 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 33.591 | 47535.0591 | 47534959.0958 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 13.8915 | 13791.4515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 12.5867 | 12486.7277 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 11.2544 | 11154.384 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 9.3065 | 9206.5377 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 9.0316 | 8931.5593 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 11.4235 | 8.7735 | 8673.4901 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.5749 | 46.9161 | 46816.09 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 13.5749 | 22.2714 | 22171.3622 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.3754 | 29.0281 | 28928.0522 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 12.3754 | 34.7341 | 34634.131 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.0241 | 21.1476 | 21047.599 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.0241 | 21.0903 | 20990.3406 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.0241 | 19.3794 | 19279.4437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 20.0241 | 18.9109 | 18810.9149 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 8.1939 | 20.9784 | 20878.4223 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505493 [SPF X2 1 13.800] CKT 1 | 26.8861 | 0.2257 | 125.714 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 18.3209 | 18220.923 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 18.0562 | 17956.2459 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 19.0804 | 18980.4143 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.8781 | 20.4608 | 20360.7695 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.9013 | 19.1737 | 19073.7198 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.9013 | 24.9206 | 24820.5604 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 33.591 | 47535.0591 | 47534959.0958 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 13.8915 | 13791.4515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 12.5867 | 12486.7277 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 11.2544 | 11154.384 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 9.3065 | 9206.5377 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 9.0316 | 8931.5593 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 11.4235 | 8.7735 | 8673.4901 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.5749 | 46.9161 | 46816.09 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 13.5749 | 22.2714 | 22171.3622 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.3754 | 29.0281 | 28928.0522 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 12.3754 | 34.7341 | 34634.131 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.0241 | 21.1476 | 21047.599 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.0241 | 21.0903 | 20990.3406 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.0241 | 19.3794 | 19279.4437 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 20.0241 | 18.9109 | 18810.9149 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 8.1939 | 20.9784 | 20878.4223 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 505492 [SPRGFLD5 161.00] TO BUS 505494 [SPRGFLD2 69.000] TO BUS 505495 [SPF X3 1 13.800] CKT 1 | 26.8861 | 0.2257 | 125.714 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 18.0562 | 17956.24 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.8778 | 20.4608 | 20360.7575 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.7062 | 19.3011 | 19201.1316 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.7062 | 25.0259 | 24925.8602 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 33.5902 | 48158.8167 | 48158716.7134 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 13.8914 | 13791.428 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 12.5867 | 12486.7076 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 11.2544 | 11154.3672 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 9.3065 | 9206.5035 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 9.0315 | 8931.5261 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 11.4234 | 8.7735 | 8673.4579 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.5748 | 46.9165 | 46816.4982 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 13.5748 | 22.2713 | 22171.2985 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.3753 | 29.0281 | 28928.0857 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 12.3753 | 34.7341 | 34634.0606 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.024 | 21.1476 | 21047.6078 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.024 | 21.0904 | 20990.3501 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.024 | 19.3795 | 19279.4503 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 20.024 | 18.9109 | 18810.9209 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 8.1939 | 20.9785 | 20878.4987 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 1 | 26.8855 | 0.2257 | 125.716 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 18.3209 | 18220.9168 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 18.0562 | 17956.24 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 19.0804 | 18980.4064 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.8778 | 20.4608 | 20360.7575 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.7062 | 19.3011 | 19201.1316 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.7062 | 25.0259 | 24925.8602 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 33.5902 | 48158.8167 | 48158716.7134 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 13.8914 | 13791.428 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 12.5867 | 12486.7076 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 11.2544 | 11154.3672 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 9.3065 | 9206.5035 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 9.0315 | 8931.5261 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 11.4234 | 8.7735 | 8673.4579 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.5748 | 46.9165 | 46816.4982 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 13.5748 | 22.2713 | 22171.2985 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.3753 | 29.0281 | 28928.0857 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 12.3753 | 34.7341 | 34634.0606 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.024 | 21.1476 | 21047.6078 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.024 | 21.0904 | 20990.3501 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.024 | 19.3795 | 19279.4503 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 20.024 | 18.9109 | 18810.9209 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 8.1939 | 20.9785 | 20878.4987 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 515554 [BVRCNTY7 345.00] TO BUS 523097 [HITCHLAND 7345.00] CKT 2 | 26.8855 | 0.2257 | 125.716 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 18.3209 | 18220.9105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 18.3209 | 18220.9105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 18.3209 | 18220.9105 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 18.0562 | 17956.2325 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 19.0804 | 18980.4002 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 19.0804 | 18980.4002 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 19.0804 | 18980.4002 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.8779 | 20.4608 | 20360.7514 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.8468 | 19.138 | 19038.0374 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.8468 | 24.8739 | 24773.9093 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 33.5897 | 48114.9016 | 48114801.6022 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 13.8914 | 13791.4411 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 12.5867 | 12486.7187 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 11.2544 | 11154.3765 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 9.3065 | 9206.5225 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 9.0315 | 8931.5446 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 11.4234 | 8.7735 | 8673.4756 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.5748 | 46.9167 | 46816.6714 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 13.5748 | 22.2713 | 22171.2779 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.3753 | 29.0281 | 28928.0651 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 12.3753 | 34.7341 | 34634.0998 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.024 | 21.1476 | 21047.5714 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.024 | 21.0903 | 20990.2868 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.024 | 19.3794 | 19279.4186 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 20.024 | 18.9109 | 18810.8614 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 8.1939 | 20.9785 | 20878.4669 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523091 [HITCHLD_TR0113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 1 | 26.8856 | 0.2257 | 125.7228 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 18.3209 | 18220.9064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 18.3209 | 18220.9064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 18.3209 | 18220.9064 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 18.0562 | 17956.2297 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 19.0804 | 18980.3957 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 19.0804 | 18980.3957 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 19.0804 | 18980.3957 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.8777 | 20.4607 | 20360.7461 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.831 | 19.1283 | 19028.3266 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.831 | 24.861 | 24761.0181 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 33.5889 | 48342.8869 | 48342786.8779 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 13.8914 | 13791.4375 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 12.5867 | 12486.7163 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 11.2544 | 11154.374 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 9.3065 | 9206.5171 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 9.0315 | 8931.5394 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 11.4234 | 8.7735 | 8673.4706 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.5747 | 46.9167 | 46816.6976 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 13.5747 | 22.2713 | 22171.2748 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.3753 | 29.0281 | 28928.0681 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 12.3753 | 34.7341 | 34634.0923 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.0238 | 21.1476 | 21047.5638 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.0238 | 21.0903 | 20990.2742 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.0238 | 19.3794 | 19279.4102 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 20.0238 | 18.9108 | 18810.8485 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 8.1938 | 20.9785 | 20878.4578 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523094 [HITCHLD_TR2113.200] TO BUS 523097 [HITCHLAND 7345.00] TO BUS 523095 [HITCHLAND 6230.00] CKT 2 | 26.8852 | 0.2257 | 125.7251 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 18.3209 | 18220.8874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 18.3209 | 18220.8874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 18.3209 | 18220.8874 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 18.0562 | 17956.2111 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 19.0804 | 18980.3762 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 19.0804 | 18980.3762 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 19.0804 | 18980.3762 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.8779 | 20.4607 | 20360.7234 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.9017 | 19.1631 | 19063.0936 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.9017 | 24.9084 | 24808.3689 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 33.5907 | 47578.32 | 47578220.0184 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 13.8914 | 13791.3992 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 12.5867 | 12486.6833 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 11.2543 | 11154.3474 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 9.3065 | 9206.4608 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 9.0315 | 8931.4841 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 11.4234 | 8.7734 | 8673.4171 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.5746 | 46.917 | 46816.9804 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 13.5746 | 22.2712 | 22171.2394 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.3753 | 29.0281 | 28928.078 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 12.3753 | 34.7341 | 34634.0559 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.0239 | 21.1476 | 21047.565 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.0239 | 21.0903 | 20990.2761 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.0239 | 19.3794 | 19279.4127 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 20.0239 | 18.9109 | 18810.8506 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 8.1938 | 20.9784 | 20878.3808 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523101 [NOBLE_WND 7345.00] CKT 1 | 26.8855 | 0.2257 | 125.7296 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 18.3209 | 18220.9212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 18.3209 | 18220.9212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 18.3209 | 18220.9212 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 18.0562 | 17956.2441 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 19.0804 | 18980.4135 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 19.0804 | 18980.4135 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 19.0804 | 18980.4135 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.8781 | 20.4608 | 20360.7674 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.9013 | 19.1732 | 19073.2079 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.9013 | 24.9198 | 24819.8383 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 33.591 | 47534.9352 | 4753483516% | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 13.8915 | 13791.4506 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 12.5867 | 1248673% | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 11.2544 | 11154.3833 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 9.3065 | 9206.5362 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 9.0316 | 8931.5579 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 11.4235 | 8.7735 | 8673.4888 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.5749 | 46.9165 | 46816.5262 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 13.5749 | 22.2713 | 22171.2975 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.3754 | 29.028 | 28928.0476 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 12.3754 | 34.7341 | 34634.1411 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.0241 | 21.1476 | 21047.5954 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.0241 | 21.0903 | 20990.3347 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.0241 | 19.3794 | 19279.4423 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 20.0241 | 18.9109 | 18810.9079 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 8.1939 | 20.9785 | 20878.4961 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523112 [NOVUS1 7345.00] CKT 1 | 26.886 | 0.2257 | 125.7149 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 18.3209 | 18220.8679 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 18.3209 | 18220.8679 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 18.3209 | 18220.8679 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 18.0562 | 17956.1932 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 19.0803 | 18980.3406 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 19.0803 | 18980.3406 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 19.0803 | 18980.3406 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.8761 | 20.4607 | 20360.6616 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.1151 | 19.529 | 19428.9749 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.1151 | 25.2638 | 25163.7988 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 33.5686 | 86454.6825 | 86454582.4885 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 13.8915 | 13791.5413 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 12.5868 | 12486.8025 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 11.2544 | 11154.4456 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 9.3067 | 9206.6782 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 9.0317 | 8931.694 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 11.423 | 8.7736 | 8673.6196 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.5746 | 46.9179 | 46817.8922 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 13.5746 | 22.2711 | 22171.1096 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.3754 | 29.0283 | 28928.2806 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 12.3754 | 34.7337 | 34633.6629 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.0225 | 21.1471 | 21047.1415 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.0225 | 21.0895 | 20989.4573 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.0225 | 19.379 | 19279.0019 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 20.0225 | 18.91 | 18810.0419 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 8.1938 | 20.9784 | 20878.3536 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 523961 [POTTER_CO 7345.00] CKT 1 | 26.8803 | 0.2258 | 125.8385 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9004 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 18.0562 | 17956.2237 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 19.0804 | 18980.3896 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 19.0804 | 18980.3896 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 19.0804 | 18980.3896 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.8782 | 20.4607 | 20360.7405 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.8848 | 19.1022 | 19002.177 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.8848 | 24.798 | 24697.9922 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 33.5872 | 51003.5088 | 51003408.7937 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 13.8914 | 13791.4354 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 12.5867 | 12486.7141 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 11.2544 | 11154.3727 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 9.3065 | 9206.5137 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 9.0315 | 8931.5361 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 11.4235 | 8.7735 | 8673.4677 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.5748 | 46.9166 | 46816.5806 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 13.5748 | 22.2713 | 22171.2856 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.3754 | 29.0281 | 28928.0531 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 12.3754 | 34.7341 | 34634.1358 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.024 | 21.1475 | 21047.5435 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.024 | 21.0902 | 20990.24 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.024 | 19.3794 | 19279.392 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 20.024 | 18.9108 | 18810.8177 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 8.1939 | 20.9785 | 20878.4799 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523097 [HITCHLAND 7345.00] TO BUS 576397 [G10014G11022345.00] CKT 1 | 26.886 | 0.2257 | 125.7247 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 18.3215 | 18221.5356 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 18.3215 | 18221.5356 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 18.3215 | 18221.5356 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 18.0568 | 17956.8405 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 19.0811 | 18981.0906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 19.0811 | 18981.0906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 19.0811 | 18981.0906 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.8795 | 20.4616 | 20361.5668 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.9456 | 19.2955 | 19195.545 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.9456 | 25.0752 | 24975.1859 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 33.6093 | 58348.6858 | 58348585.8029 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 13.8922 | 13792.2401 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 12.5874 | 12487.3957 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 11.2549 | 11154.9356 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 9.3077 | 9207.7041 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 9.0327 | 8932.6877 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 11.4243 | 8.7746 | 8674.5832 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.5769 | 46.9077 | 46807.6832 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 13.5769 | 22.2724 | 22172.4454 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.3761 | 29.0276 | 28927.5915 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 12.3761 | 34.7354 | 34635.3587 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.0262 | 21.1484 | 21048.4116 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.0262 | 21.0919 | 20991.8909 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.0262 | 19.3802 | 19280.2234 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 20.0262 | 18.9124 | 18812.4304 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 8.195 | 20.9806 | 20880.6477 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523118 [BUFF_DUNES 7345.00] TO BUS 523853 [FINNEY 7345.00] CKT 1 | 26.8949 | 0.2254 | 125.3966 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 18.3209 | 18220.9192 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 18.3209 | 18220.9192 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 18.3209 | 18220.9192 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 18.0562 | 17956.2422 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 19.0804 | 18980.4053 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 19.0804 | 18980.4053 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 19.0804 | 18980.4053 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.8777 | 20.4608 | 20360.7513 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3792 | 22.5956 | 22495.6193 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.3792 | 28.1686 | 28068.6446 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 33.5378 | 8961.44 | 8961340.038 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 13.8917 | 13791.7321 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 12.587 | 12486.9646 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 11.2546 | 11154.5794 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 9.307 | 9206.9598 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 9.032 | 8931.9668 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 11.4235 | 8.7739 | 8673.8839 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.5744 | 46.919 | 46818.9571 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.5744 | 22.271 | 22170.9665 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.3756 | 29.0281 | 28928.1336 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.3756 | 34.734 | 34634.0222 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.0224 | 21.147 | 21046.9947 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.0224 | 21.0892 | 20989.2122 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.0224 | 19.3789 | 19278.8713 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.0224 | 18.9098 | 18809.8192 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.1938 | 20.9782 | 20878.2295 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 26.8823 | 0.2258 | 125.8418 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9117 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9117 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 18.3209 | 18220.9117 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 18.0562 | 17956.2346 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 19.0804 | 18980.402 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 19.0804 | 18980.402 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 19.0804 | 18980.402 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.8782 | 20.4608 | 20360.7553 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.8971 | 19.1397 | 19039.698 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.8971 | 24.8607 | 24760.7272 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 33.5835 | 53481.0987 | 53480998.7385 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 13.8914 | 13791.4351 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 12.5867 | 12486.7138 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 11.2544 | 11154.3719 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 9.3065 | 9206.5125 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 9.0315 | 8931.535 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 11.4236 | 8.7735 | 8673.4666 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.5749 | 46.9165 | 46816.5238 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 13.5749 | 22.2713 | 22171.2958 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.3754 | 29.0281 | 28928.053 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 12.3754 | 34.7341 | 34634.136 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.024 | 21.1476 | 21047.5785 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.024 | 21.0903 | 20990.3039 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.024 | 19.3794 | 19279.4248 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 20.024 | 18.9109 | 18810.8793 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 8.1939 | 20.9785 | 20878.4955 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 523853 [FINNEY 7345.00] TO BUS 599950 [LAMAR7 345.00] CKT 1 | 26.8861 | 0.2257 | 125.7175 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 18.3209 | 18220.921 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 18.3209 | 18220.921 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 18.3209 | 18220.921 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 18.0562 | 17956.2438 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 19.0804 | 18980.4137 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 19.0804 | 18980.4137 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 19.0804 | 18980.4137 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.878 | 20.4608 | 20360.7679 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.8004 | 19.1543 | 19054.3296 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.8004 | 24.8241 | 24724.1202 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 33.5909 | 48485.491 | 48485390.9583 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 13.8915 | 13791.4515 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 12.5867 | 12486.7276 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 11.2544 | 11154.3834 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 9.3065 | 9206.5369 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 9.0316 | 8931.5584 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 11.4235 | 8.7735 | 8673.4892 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.5749 | 46.9165 | 46816.464 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 13.5749 | 22.2713 | 22171.3014 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.3754 | 29.028 | 28928.0473 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 12.3754 | 34.7342 | 34634.1515 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.0241 | 21.1476 | 21047.6004 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.0241 | 21.0903 | 20990.3425 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.0241 | 19.3794 | 19279.4457 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 20.0241 | 18.9109 | 18810.9164 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 8.1939 | 20.9785 | 20878.5005 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 531510 [HARBNGR3 115.00] TO BUS 531512 [HARBNGR7 345.00] TO BUS 531511 [HARBNGR-T 13.800] CKT 1 | 26.886 | 0.2257 | 125.7136 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 18.4296 | 18329.6247 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 18.4296 | 18329.6247 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 18.4296 | 18329.6247 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 18.1636 | 18063.5541 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 19.1909 | 19090.9216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 19.1909 | 19090.9216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 19.1909 | 19090.9216 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0833 | 20.5771 | 20477.0966 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.9174 | 19.1883 | 19088.2597 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.9174 | 24.9525 | 24852.4797 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.5865 | 86873.5111 | 86873411.1016 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 13.9291 | 13829.1104 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 12.6184 | 12518.3585 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 11.2806 | 11180.5787 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 9.3637 | 9263.6584 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 9.0866 | 8986.6271 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.372 | 8.8267 | 8726.6518 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5977 | 46.9201 | 46820.1218 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5977 | 22.2685 | 22168.4567 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3885 | 29.0846 | 28984.6031 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3885 | 34.6231 | 34523.0613 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0419 | 21.1854 | 21085.3923 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0419 | 21.1532 | 21053.2167 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0419 | 19.4124 | 19312.4096 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0419 | 18.9668 | 18866.7987 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 8.2068 | 21.019 | 20919.0455 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 24.9363 | 0.2083 | 108.2648 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 18.3398 | 18239.7806 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 18.3398 | 18239.7806 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 18.3398 | 18239.7806 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 18.0755 | 17975.4549 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 19.0969 | 18996.856 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 19.0969 | 18996.856 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 19.0969 | 18996.856 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.1516 | 20.4738 | 20373.7506 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.8984 | 19.1754 | 19075.4287 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.8984 | 24.9232 | 24823.2308 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 33.5529 | 6909.9676 | 6909867.6412 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 13.9105 | 13810.4866 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 12.6017 | 12501.6632 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 11.2684 | 11168.3711 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 9.339 | 9239.0139 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 9.0618 | 8961.8008 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 10.439 | 8.8017 | 8701.706 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.561 | 47.1751 | 47075.1018 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.561 | 22.2332 | 22133.2352 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.2465 | 29.5008 | 29400.8156 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.2465 | 33.8005 | 33700.5158 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.0202 | 21.1476 | 21047.6103 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.0202 | 21.09 | 20990.0016 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.0202 | 19.3793 | 19279.3287 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.0202 | 18.9104 | 18810.3734 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 8.1933 | 20.9784 | 20878.3842 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 26.873 | 0.2258 | 125.8283 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 18.3401 | 18240.1331 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 18.3401 | 18240.1331 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 18.3401 | 18240.1331 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 18.0758 | 17975.7616 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 19.0966 | 18996.6486 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 19.0966 | 18996.6486 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 19.0966 | 18996.6486 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.4702 | 20.4725 | 20372.5473 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 12.9 | 19.173 | 19072.9508 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 12.9 | 24.9188 | 24818.7897 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 33.5959 | 47219.1313 | 47219031.2808 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 13.9138 | 13813.8036 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 12.6023 | 12502.3062 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 11.2705 | 11170.5028 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 9.3537 | 9253.6597 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 9.0742 | 8974.1799 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 9.6893 | 8.8121 | 8712.0625 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.5647 | 47.1338 | 47033.8041 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 13.5647 | 22.2392 | 22139.1981 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 12.2292 | 29.6399 | 29539.9031 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 12.2292 | 33.5348 | 33434.8006 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.0213 | 21.1486 | 21048.6258 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.0213 | 21.0917 | 20991.6882 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.0213 | 19.3802 | 19280.2313 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 20.0213 | 18.9119 | 18811.9042 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 8.1937 | 20.9793 | 20879.2952 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532775 [87TH 7 345.00] TO BUS 542977 [CRAIG 7 345.00] CKT 1 | 26.8696 | 0.2257 | 125.6926 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 18.3206 | 18220.5966 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 18.3206 | 18220.5966 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 18.3206 | 18220.5966 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 18.0559 | 17955.9213 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 19.0801 | 18980.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 19.0801 | 18980.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 19.0801 | 18980.1134 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.8771 | 20.4605 | 20360.5019 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.8861 | 19.1747 | 19074.7403 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.8861 | 24.919 | 24819.005 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 33.5537 | 8346.7609 | 8346660.865 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 13.8916 | 13791.5741 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 12.5868 | 12486.8242 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 11.2545 | 11154.4646 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 9.3068 | 9206.7539 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 9.0318 | 8931.7632 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.4217 | 8.7737 | 8673.6836 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.5747 | 46.9171 | 46817.0668 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.5747 | 22.2712 | 22171.2342 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.3755 | 29.028 | 28927.9945 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.3755 | 34.7343 | 34634.2666 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.0124 | 21.1513 | 21051.3407 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.0124 | 21.0954 | 20995.3606 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.0124 | 19.3823 | 19282.2812 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.0124 | 18.9146 | 18814.5984 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 8.1933 | 20.9798 | 20879.7592 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 26.8627 | 0.2258 | 125.7565 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 18.3094 | 18209.3704 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 18.3094 | 18209.3704 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 18.3094 | 18209.3704 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 18.045 | 17945.0074 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 19.0681 | 18968.1084 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 19.0681 | 18968.1084 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 19.0681 | 18968.1084 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7379 | 20.447 | 20346.9507 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.8938 | 19.1774 | 19077.3791 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.8938 | 24.9252 | 24825.2421 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.5638 | 10655.6571 | 10655557.1265 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 13.8853 | 13785.2828 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 12.5815 | 12481.5171 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 11.2501 | 11150.088 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 9.2973 | 9197.309 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 9.0226 | 8922.6401 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4166 | 8.7649 | 8664.8583 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5716 | 46.9323 | 46832.2621 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5716 | 22.2692 | 22169.2031 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3701 | 29.0302 | 28930.2145 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3701 | 34.7283 | 34628.2591 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0159 | 21.144 | 21043.9796 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0159 | 21.0838 | 20983.816 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0159 | 19.3761 | 19276.0703 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0159 | 18.9047 | 18804.687 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 8.1926 | 20.9762 | 20876.24 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.2841 | 0.2298 | 129.8243 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 18.3632 | 18263.2407 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 18.3632 | 18263.2407 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 18.3632 | 18263.2407 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 18.0997 | 17999.6926 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 19.1172 | 19017.1939 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 19.1172 | 19017.1939 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 19.1172 | 19017.1939 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 18.7706 | 20.4898 | 20389.7748 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.8844 | 19.164 | 19063.9944 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.8844 | 24.8978 | 24797.8092 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 33.5837 | 60330.6874 | 60330587.3621 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 13.8773 | 13777.2991 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 12.5745 | 12474.4746 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 11.2445 | 11144.482 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 9.2867 | 9186.6793 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 9.0121 | 8912.1282 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.2543 | 8.7545 | 8654.4689 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.559 | 46.9986 | 46898.5778 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.559 | 22.2603 | 22160.2542 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3459 | 29.0999 | 28999.9206 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3459 | 34.5778 | 34477.8365 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.7879 | 21.2408 | 21140.8115 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.7879 | 21.213 | 21113.0234 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.7879 | 19.4497 | 19349.7073 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 19.7879 | 18.9994 | 18899.4479 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 8.1829 | 21.0036 | 20903.5611 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 26.56 | 0.2291 | 129.1412 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 18.3234 | 18223.3667 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 18.3234 | 18223.3667 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 18.3234 | 18223.3667 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 18.0586 | 17958.6294 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 19.0832 | 18983.1748 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 19.0832 | 18983.1748 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 19.0832 | 18983.1748 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.8317 | 20.4641 | 20364.1297 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.9011 | 19.1737 | 19073.7077 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.9011 | 24.9205 | 24820.4783 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 33.591 | 47804.879 | 47804779.0209 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 13.892 | 13792.0016 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 12.5872 | 12487.1913 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 11.2548 | 11154.7692 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 9.3074 | 9207.3626 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 9.0324 | 8932.3545 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.4219 | 8.7743 | 8674.2586 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.5751 | 46.9179 | 46817.8964 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.5751 | 22.2711 | 22171.0616 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.3715 | 29.025 | 28924.98 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.3715 | 34.7415 | 34641.5248 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 18.9113 | 21.4351 | 21335.0884 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 18.9113 | 21.4544 | 21354.3877 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 18.9113 | 19.5839 | 19483.8683 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 18.9113 | 19.15 | 19050.0182 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 8.1674 | 20.9997 | 20899.7307 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 26.7796 | 0.225 | 124.9992 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 18.3088 | 18208.7541 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 18.3088 | 18208.7541 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 18.3088 | 18208.7541 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 18.0444 | 17944.4137 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 19.0674 | 18967.3726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 19.0674 | 18967.3726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 19.0674 | 18967.3726 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.7396 | 20.446 | 20345.9986 | 57.92 | 113.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.8945 | 19.1742 | 19074.1952 | 166.67 | 267.12 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-008 | Corporation Carpenter 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.8945 | 24.9194 | 24819.4364 | 83.33 | 133.56 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-056 | Russell 115 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 33.5737 | 188406.9961 | 188406896.0812 | 20 | 23.98 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 13.8849 | 13784.9118 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 12.5812 | 12481.1995 | 138.21 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-058 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 11.2498 | 11149.8278 | 148.08 | 162 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 9.2968 | 9196.7732 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 9.0221 | 8922.1186 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-057 | Atlantic 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.4145 | 8.7644 | 8664.351 | 141.5 | 160 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5711 | 46.9345 | 46834.4526 | 72.97 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-072 | Windsor to AEC Sedalia 161 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.5711 | 22.2689 | 22168.9158 | 77.03 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3696 | 29.0312 | 28931.1678 | 73.77 | 170.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-073 | SE Ottawa to Pleasant Valley 161kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3696 | 34.7261 | 34626.0985 | 76.23 | 181.05 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0154 | 21.1437 | 21043.7285 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0154 | 21.0833 | 20983.3438 | 61.05 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0154 | 19.3758 | 19275.8389 | 50.58 | 121.8 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-079 | Riverton-Neosho 161kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.0154 | 18.9042 | 18804.2383 | 62.79 | 151.2 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-088 | La Russell 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 8.1928 | 20.9762 | 20876.2139 | 150 | 165.6 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-090 | Wolf Creek - Blackberry 345 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.3083 | 0.2303 | 130.2688 | 204.27 | 222.75 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 18.4514 | 18351.3684 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 18.4514 | 18351.3684 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 18.4514 | 18351.3684 | 90.1 | 176.4 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 18.187 | 18087.0041 | 96.53 | 189 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 19.2058 | 19105.7873 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 19.2058 | 19105.7873 | 75.08 | 147 | PASS | PASS
DISIS-2020-001-1 | 03 CENTRAL | 25WP | GEN-2020-007 | Evergy La Cygne to Wolf Creek 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 17.7823 | 19.2058 | 19105.7873 | 75.08 | 147 | PASS | PASS