03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_173 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_174 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_175 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_176 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_177 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_178 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_179 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_180 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_181 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_182 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_183 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_185 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_187 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_188 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_189 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_190 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_191 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_192 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. NICHOL XF1 1 (549940) 13.2 kV to NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_193 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.3. MILL XF1 1 (549946) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_194 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. MILL 2 (549918) 69.0 kV to MILL 5 (549962) 161.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 b.3. MILL XF2 1 (549948) 13.2 kV to MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_195 | 3 Phase fault on HAWTHRN4 138.00 (510413) 138 kV Bus a. Apply fault at the HAWTHRN4 138.00 (510413) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.2. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.4. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_196 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_197 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_198 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_199 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_200 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_201 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_202 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_203 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_204 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_205 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_206 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_207 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_208 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_209 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_210 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_211 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_212 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_213 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_214 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_215 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_216 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_217 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_218 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_219 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_220 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_221 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_222 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_223 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_224 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_225 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_226 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_227 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_228 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_229 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_230 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_231 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_232 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_233 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_234 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_235 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 b.3. OCHILTREE 3 (523154) 115.0 kV to OCHILTREE 6 (523155) 230.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_236 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_237 | 3 Phase fault on FRISCO_WND 3115.00 (523160) 115 kV Bus a. Apply fault at the FRISCO_WND 3115.00 (523160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to FRISCO_WND 3 (523160) 115.0 kV Transmission Circuit #1 b.2. FRISCO_WND 3 (523160) 115.0 kV to LASLEY 3 (523175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_238 | 3 Phase fault on TEXAS_CNTY 3115.00 (523090) 115 kV Bus a. Apply fault at the TEXAS_CNTY 3115.00 (523090) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEXAS_CNTY 3 (523090) 115.0 kV to HITCHLAND 3 (523093) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_239 | 3 Phase fault on HITCHLAND 3115.00 (523093) 115 kV Bus a. Apply fault at the HITCHLAND 3115.00 (523093) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 3 (523093) 115.0 kV to HANSFORD 3 (523195) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_240 | 3 Phase fault on COLE 3115.00 (523120) 115 kV Bus a. Apply fault at the COLE 3115.00 (523120) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 3 (523120) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_241 | 3 Phase fault on TXFARMS 3115.00 (523140) 115 kV Bus a. Apply fault at the TXFARMS 3115.00 (523140) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXFARMS 3 (523140) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 b.2. TXFARMS 3 (523140) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 b.3. SPEARMAN 3 (523186) 115.0 kV to SPEARMNSUB 3 (523203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_242 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_243 | 3 Phase fault on OCHILTREE 3115.00 (523154) 115 kV Bus a. Apply fault at the OCHILTREE 3115.00 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 3 (523154) 115.0 kV to PERRYTON 3 (523158) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_244 | 3 Phase fault on WADE_TP 3115.00 (523145) 115 kV Bus a. Apply fault at the WADE_TP 3115.00 (523145) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIPSCOMB 3 (523135) 115.0 kV to WADE_TP 3 (523145) 115.0 kV Transmission Circuit #1 b.2. WADE_TP 3 (523145) 115.0 kV to WADE 3 (523147) 115.0 kV Transmission Circuit #1 b.3. WADE_TP 3 (523145) 115.0 kV to OCHILTREE 3 (523154) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_245 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_248 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_249 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_250 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_251 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_252 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_253 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_254 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_255 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_256 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_257 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_258 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_259 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_260 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_261 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_262 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_263 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_264 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.4. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_265 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_266 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_267 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_268 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_269 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_270 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_271 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_272 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_273 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_274 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_275 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_276 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_277 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_278 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_279 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_280 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_281 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_282 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_283 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_284 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_285 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_286 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_287 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_288 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_289 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_290 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_291 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_292 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_293 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_294 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_295 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_296 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_297 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_298 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_299 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_300 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_301 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_302 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHLB2 (300132) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_303 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5THMHILTFERB (301511) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_304 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_305 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB3 (300133) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_306 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5BEVIER (300381) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_307 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_308 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THOMHLXF1 (301508) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_309 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5MEADVLB1 (300207) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_310 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLXF3 (301506) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_311 | 3 Phase fault on 5THMHLB3 161.00 (300133) 161 kV Bus a. Apply fault at the 5THMHLB3 161.00 (300133) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB3 (300133) 161.0 kV to 5THOMHLU3SU (301507) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_312 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_313 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_314 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_315 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_316 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_317 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_318 | 3 Phase fault on 2BEAMAN 69.000 (300527) 69 kV Bus a. Apply fault at the 2BEAMAN 69.000 (300527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BEAMAN (300527) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_319 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_320 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_321 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_322 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_323 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_324 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_325 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_326 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_327 | 3 Phase fault on 2MALTAJ 69.000 (300536) 69 kV Bus a. Apply fault at the 2MALTAJ 69.000 (300536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALTAJ (300536) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_328 | 3 Phase fault on 2NAPTON 69.000 (300538) 69 kV Bus a. Apply fault at the 2NAPTON 69.000 (300538) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NAPTON (300538) 69.0 kV to 2NORTON (300540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_329 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_330 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_331 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2FLORNC (300553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_332 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_333 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_334 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_335 | 3 Phase fault on 2ASHGRV 69.000 (300657) 69 kV Bus a. Apply fault at the 2ASHGRV 69.000 (300657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_336 | 3 Phase fault on 2BOWRML 69.000 (300659) 69 kV Bus a. Apply fault at the 2BOWRML 69.000 (300659) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_337 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_338 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_339 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_340 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_341 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_342 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_343 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_344 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_345 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_346 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_347 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_348 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_349 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_350 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_351 | 3 Phase fault on 2DMNDGR 69.000 (300744) 69 kV Bus a. Apply fault at the 2DMNDGR 69.000 (300744) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_352 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_353 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_354 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_355 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_356 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_357 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_358 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_359 | 3 Phase fault on 2FRSTOE 69.000 (300776) 69 kV Bus a. Apply fault at the 2FRSTOE 69.000 (300776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRSTOE (300776) 69.0 kV to 2WARSAW (300790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_360 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_361 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_362 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_363 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_364 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_365 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_366 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_367 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_368 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_369 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_370 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_371 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_372 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_373 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_374 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_375 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_376 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_377 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_378 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_379 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_380 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_381 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_382 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_383 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_384 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_385 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_386 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_387 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_388 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_389 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_390 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_391 | 3 Phase fault on NIXA NE2 69.000 (505544) 69 kV Bus a. Apply fault at the NIXA NE2 69.000 (505544) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA NE2 (505544) 69.0 kV to JRPS 69B-2 2 (549903) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_392 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_393 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_394 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_395 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_396 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_397 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_398 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_399 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_400 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_401 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_402 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_403 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_404 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_405 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_406 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_407 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_408 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_409 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_410 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_411 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_412 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_413 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_414 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_415 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_416 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_417 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_418 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_419 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_420 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_421 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_422 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_423 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_424 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_425 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_428 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_429 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_432 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_433 | 3 Phase fault on ARKCTYW2 69.000 (533540) 69 kV Bus a. Apply fault at the ARKCTYW2 69.000 (533540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_434 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_435 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_436 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_437 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_438 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_439 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_440 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_441 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_442 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_443 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_444 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_445 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_446 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_447 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_448 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_449 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_450 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_451 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_452 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_453 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_455 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_456 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_457 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_458 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_459 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_460 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_461 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_462 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_463 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_464 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_465 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_466 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_467 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_468 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_469 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_470 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_471 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_472 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_473 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_474 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_475 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_476 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_477 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_478 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_479 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_480 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_481 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_482 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_483 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_484 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_485 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_486 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_487 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_488 | 3 Phase fault on NRAYMORETP 5161.00 (541231) 161 kV Bus a. Apply fault at the NRAYMORETP 5161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_489 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_490 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_491 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_492 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_493 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_494 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_495 | 3 Phase fault on LEX69 2 69.000 (541264) 69 kV Bus a. Apply fault at the LEX69 2 69.000 (541264) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_496 | 3 Phase fault on 13&40 2 69.000 (541266) 69 kV Bus a. Apply fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_497 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_498 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_499 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_500 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_501 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_502 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_503 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_504 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_505 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_506 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_507 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_508 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_509 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_510 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_511 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_512 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_513 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_514 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_515 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_516 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_517 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_518 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_519 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_520 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_521 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_522 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_523 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_524 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_525 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_526 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_527 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_528 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_529 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_530 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_531 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_532 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_533 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_534 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_535 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_536 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_537 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_538 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_539 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_540 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_541 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_542 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_543 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_544 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_545 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_546 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_547 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_548 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_549 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_550 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_551 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_552 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_553 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_554 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_556 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_557 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_558 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_559 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_560 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_561 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_562 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_563 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_564 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_565 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_566 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_567 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_568 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_569 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_570 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_571 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_572 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_573 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_574 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_575 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_576 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_577 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_578 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_579 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_580 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_581 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_582 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_583 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_584 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_585 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_586 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_587 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_588 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_589 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_590 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_591 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_592 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_593 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_594 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_595 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_596 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_597 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_598 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_599 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_600 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_601 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_602 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_603 | 3 Phase fault on CUPTAP 2 69.000 (547436) 69 kV Bus a. Apply fault at the CUPTAP 2 69.000 (547436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUPTAP 2 (547436) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_604 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_605 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_606 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_607 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_608 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_609 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_610 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_611 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_612 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_613 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_614 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to DIA131 2 (547538) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_615 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_616 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_617 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_618 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_619 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_620 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_621 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_622 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_623 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_624 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_625 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_626 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_627 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_628 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_629 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_630 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_631 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_632 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_633 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_634 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_635 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_636 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_637 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_638 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_639 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_640 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_641 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_642 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_643 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_644 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_645 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_646 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_647 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_648 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_649 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_650 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_651 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_652 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_653 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_654 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_655 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_656 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_657 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_658 | 3 Phase fault on NIX114 2 69.000 (547535) 69 kV Bus a. Apply fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_659 | 3 Phase fault on ASH121 2 69.000 (547536) 69 kV Bus a. Apply fault at the ASH121 2 69.000 (547536) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH121 2 (547536) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_660 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_661 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_662 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_663 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_664 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_665 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_666 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_667 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_668 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to REP345 2 (547576) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_669 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_670 | 3 Phase fault on NIC170 2 69.000 (547542) 69 kV Bus a. Apply fault at the NIC170 2 69.000 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIC170 2 (547542) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_671 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_672 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_673 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_674 | 3 Phase fault on FRP217 2 69.000 (547545) 69 kV Bus a. Apply fault at the FRP217 2 69.000 (547545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRP217 2 (547545) 69.0 kV to DAD368 2 (547585) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_675 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_676 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_677 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_678 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_679 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_680 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_681 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_682 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_683 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_684 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_685 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_686 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_687 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to TWIN OAKS 2 (549933) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_688 | 3 Phase fault on JRPS 69B-2 269.000 (549903) 69 kV Bus a. Apply fault at the JRPS 69B-2 269.000 (549903) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JRPS 69B-2 2 (549903) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_689 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_690 | 3 Phase fault on JAMES RIVER269.000 (549904) 69 kV Bus a. Apply fault at the JAMES RIVER269.000 (549904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER2 (549904) 69.0 kV to HIGHWAY M 2 (549909) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_691 | 3 Phase fault on KICKAPOO 269.000 (549906) 69 kV Bus a. Apply fault at the KICKAPOO 269.000 (549906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KICKAPOO 2 (549906) 69.0 kV to SUNSET 2 (549907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_692 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to S HWY 65 2 (549908) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_693 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_694 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_695 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV to SEMINOLE 2 (549934) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_696 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_697 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_698 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_699 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_700 | 3 Phase fault on MILL 269.000 (549918) 69 kV Bus a. Apply fault at the MILL 269.000 (549918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 2 (549918) 69.0 kV to CHAD 2 (549919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_701 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_702 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_703 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_704 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_705 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_706 | 3 Phase fault on LAUREL 269.000 (549924) 69 kV Bus a. Apply fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_707 | 3 Phase fault on NICHOLS 269.000 (549925) 69 kV Bus a. Apply fault at the NICHOLS 269.000 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 2 (549925) 69.0 kV to FRISCO 2 (549926) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_708 | 3 Phase fault on FRISCO 269.000 (549926) 69 kV Bus a. Apply fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_709 | 3 Phase fault on N HWY13 269.000 (549927) 69 kV Bus a. Apply fault at the N HWY13 269.000 (549927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HWY13 2 (549927) 69.0 kV to NORTON 2 (549928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_710 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_711 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to NEERGARD 2 (549930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_712 | 3 Phase fault on NEERGARD 269.000 (549930) 69 kV Bus a. Apply fault at the NEERGARD 269.000 (549930) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEERGARD 2 (549930) 69.0 kV to LECOMPTE 2 (549931) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_713 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_714 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_715 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_716 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_717 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_718 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_719 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_720 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_721 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_722 | 3 Phase fault on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_723 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_724 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_725 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_726 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_727 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_728 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_729 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_730 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_731 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_732 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_733 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_734 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_735 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_736 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_737 | 3 Phase fault on 5THMHILB1 161.00 (300120) 161 kV Bus a. Apply fault at the 5THMHILB1 161.00 (300120) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TMHILL (300172) 69.0 kV to 5THMHILB1 (300120) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_738 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_739 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_740 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_741 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_742 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_743 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_744 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_745 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_746 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_747 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_748 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_749 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_750 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_751 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_752 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_753 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_754 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_755 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_756 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_757 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_758 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_759 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_760 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_761 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_762 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_763 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_764 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_765 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_766 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_767 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_768 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR41 (523098) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_769 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_770 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_771 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_772 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_773 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_774 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_775 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_776 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_777 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_778 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_779 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_780 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_781 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_782 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_783 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_784 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_785 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_786 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_787 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_788 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_789 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_790 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_791 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_792 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_793 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_794 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_795 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_796 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_797 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_798 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_799 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_800 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_801 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_802 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_803 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_804 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_805 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_806 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_807 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_808 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_809 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_810 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_811 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_812 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_813 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_814 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_815 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_816 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_817 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_819 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_820 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_821 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_822 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_823 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_824 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_825 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_826 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_827 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_828 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_829 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_830 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_831 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_832 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_833 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_834 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_835 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_836 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_837 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_838 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_839 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_840 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_841 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH 12 (400) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_842 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_843 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_844 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_845 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_846 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_847 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_848 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_849 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_850 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_851 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_852 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_853 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_854 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_855 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_856 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_857 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_858 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_859 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_860 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_861 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_862 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_863 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_864 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_865 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_866 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_867 | 3 Phase fault on NORTON 5161.00 (549967) 161 kV Bus a. Apply fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_868 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_869 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_870 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_871 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_872 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_873 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_874 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_875 | 3 Phase fault on MON383 2 69.000 (547591) 69 kV Bus a. Apply fault at the MON383 2 69.000 (547591) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 2 (547591) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_876 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_877 | 3 Phase fault on SUNSET 269.000 (549907) 69 kV Bus a. Apply fault at the SUNSET 269.000 (549907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 2 (549907) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_878 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_879 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_880 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_010 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. The issue is also observed in the PQ case and is not impacted by the CQ units. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_013 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_014 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_015 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_016 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_017 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_018 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_020 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_023 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_024 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_025 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_027 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_028 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_029 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_031 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_032 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_033 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_038 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_039 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_040 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_041 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_043 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_046 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_048 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_049 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_051 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 b.4. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply Fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.3. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.4. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 b.2. NRAYMORETP 5 (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.4. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.5. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.6. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.3. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on NORTON 5 161.00 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply Fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PIONEER3 115.00 (531391) 115 kV Bus a. Apply Fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 b.3. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.4. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.5. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 b.6. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 b.7. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.8. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 b.9. PIONEER3 (531391) 115.0 kV to PIONEER2 (531390) 69.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to Trip Bus # b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on WALDO 3 115.00 (539698) 115 kV Bus a. Apply Fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.5. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.7. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.8. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.9. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.10. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.13. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply Fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWNDTAP3 (531476) 115.0 kV to Trip Bus # b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.5. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.6. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.3. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on JONES3 115.00 (531379) 115 kV Bus a. Apply Fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on HOLCOMB3 115.00 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 115.00 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.3. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply Fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CIM-PLT3 (539654) 115.0 kV to CIM-PLT (539780) 13.8 kV Two Winding #1 b.6. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply Fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.2. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.4. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. GRDNCTY3 (531445) 115.0 kV to S2 GEN 1 (531459) 13.8 kV Two Winding #1 b.4. GRDNCTY3 (531445) 115.0 kV to S4 GEN 1 (531461) 13.2 kV Two Winding #1 b.5. GRDNCTY3 (531445) 115.0 kV to S5 GEN 1 (531462) 13.2 kV Two Winding #1 b.6. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.7. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.8. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.9. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.10. GRDNCTY3 (531445) 115.0 kV to GC-C 1 (531421) 34.5 kV to GC-CITY (531254) 13.8 kV Three Winding #1 b.11. GRDNCTY3 (531445) 115.0 kV to GARDNCY2 (531423) 69.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.4. SPF X3 1 (505495) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 b.4. NIXA 5 (505496) 161.0 kV to NIXA 2 (505501) 69.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on AVOCA 5 161.00 (504000) 161 kV Bus a. Apply Fault at the AVOCA 5 161.00 (504000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVOCA 5 (504000) 161.0 kV to BEAVER 5 (505480) 161.0 kV Transmission Circuit #1 b.2. AVOCA 5 (504000) 161.0 kV to EROGERS5 (506931) 161.0 kV Transmission Circuit #1 b.3. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.4. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply Fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.2. BEAVER 5 (505480) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on STOCKTN5 161.00 (505498) 161 kV Bus a. Apply Fault at the STOCKTN5 161.00 (505498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 b.2. STOCKTN5 (505498) 161.0 kV to STK #1 1 (505500) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RENOHLWTP (300130) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.2. 5RENOHLWTP (300130) 161.0 kV to 5RIVERSIDE (300805) 161.0 kV Transmission Circuit #1 b.3. 5RENOHLWTP (300130) 161.0 kV to 5RENOHLW (301129) 161.0 kV Transmission Circuit #1 b.4. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5COMPTN (300719) 161.0 kV to 5ROARK (300727) 161.0 kV Transmission Circuit #1 b.6. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.7. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.8. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.9. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.10. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.11. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.12. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.13. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on TABLE R5 161.00 (505472) 161 kV Bus a. Apply Fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.3. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.4. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.5. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.6. TABLE R5 (505472) 161.0 kV to TBR1&2 1 (505476) 13.8 kV Two Winding #1 b.7. TABLE R5 (505472) 161.0 kV to TBR3&4 1 (505478) 13.8 kV Two Winding #1 b.8. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.9. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 b.10. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.11. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply Fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 b.2. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 b.3. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.4. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.5. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.6. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 b.2. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 b.3. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.7. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2BOWRML (300659) 69.0 kV to 2REEDS (300751) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.4. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.6. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.2. 2DMNDGR (300744) 69.0 kV to 2DMNDTP (300745) 69.0 kV Transmission Circuit #1 b.3. 2DMNDTP (300745) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.4. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2SPGCTP (300754) 69.0 kV Transmission Circuit #1 b.6. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 b.7. 2SPGCTP (300754) 69.0 kV to 2WNTWRT (300762) 69.0 kV Transmission Circuit #1 b.8. 2SPGCTP (300754) 69.0 kV to 2SPURGNTP (300764) 69.0 kV Transmission Circuit #1 b.9. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.10. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 b.2. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.5. SPF X1 1 (505491) 13.8 kV to SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHGRV (300657) 69.0 kV to 2CAVESP (300664) 69.0 kV Transmission Circuit #1 b.2. 2ASHGRV (300657) 69.0 kV to 2ELWOOD (300669) 69.0 kV Transmission Circuit #1 b.3. 2ASHGRV (300657) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 b.4. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 b.5. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.6. SPRGFLD2 (505494) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #2 b.7. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.3. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.5. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.6. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.7. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 b.8. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X2 1 (505493) 13.8 kV Three Winding #1 b.9. SPRGFLD5 (505492) 161.0 kV to SPRGFLD2 (505494) 69.0 kV to SPF X3 1 (505495) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X1 1 (505497) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on NIXA 5 161.00 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 b.2. NXA X2 1 (505499) 13.8 kV to NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on JTEC 5161.00 (549954) 161 kV Bus a. Apply Fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 b.2. JTEC GEN#1 1 (549890) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.3. JTEC CTS 1 (549891) 12.5 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.4. JTEC GEN#2 1 (549893) 20.0 kV to JTEC 5 (549954) 161.0 kV Two Winding #1 b.5. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.6. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.7. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.2. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.3. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply Fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 b.4. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF2 1 (549938) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.2. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 b.3. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.4. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply Fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JRPS GT1 1 (549900) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.2. JRPS GT2 1 (549901) 13.8 kV to JAMES RIVER5 (549961) 161.0 kV Two Winding #1 b.3. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 b.4. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.5. JAMES RIVER5 (549961) 161.0 kV to JRPS 69B-2 2 (549903) 69.0 kV to JRPS XF2 1 (549945) 13.2 kV Three Winding #1 b.6. JAMES RIVER5 (549961) 161.0 kV to JAMES RIVER2 (549904) 69.0 kV to JRPS XF1 1 (549944) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on MILL 5161.00 (549962) 161 kV Bus a. Apply Fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 b.4. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF2 1 (549948) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on MENTOR 5161.00 (549963) 161 kV Bus a. Apply Fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 b.2. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on SUMMIT 5161.00 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5161.00 (549966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.3. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on NORTON 5161.00 (549967) 161 kV Bus a. Apply Fault at the NORTON 5161.00 (549967) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 5 (549966) 161.0 kV to NORTON 5 (549967) 161.0 kV Transmission Circuit #1 b.2. NORTON 5 (549967) 161.0 kV to NORTON 2 (549928) 69.0 kV to NORTON XF1 1 (549942) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on MC CARTNEY 5161.00 (549968) 161 kV Bus a. Apply Fault at the MC CARTNEY 5161.00 (549968) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCCARTNEY (301568) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #z1 b.2. MAC GT1&2 1 (549892) 13.8 kV to MC CARTNEY 5 (549968) 161.0 kV Two Winding #1 b.3. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.4. SUMMIT 5 (549966) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.3. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.4. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 b.5. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.6. BROOKLINE 5 (549969) 161.0 kV to BROOKLINE 7 (549984) 345.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on CLAY 5161.00 (549970) 161 kV Bus a. Apply Fault at the CLAY 5161.00 (549970) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.3. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.4. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PIC WEST 5161.00 (549971) 161 kV Bus a. Apply Fault at the PIC WEST 5161.00 (549971) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 b.2. SUMMIT 5 (549966) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit # b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 b.2. OCHLTRE_TR11 (523151) 13.2 kV to OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.7. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 b.4. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.5. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.7. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 b.8. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 b.9. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OVERTON (345409) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 b.2. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z b.3. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.4. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 b.5. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 b.2. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 b.3. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply Fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.4. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on NOL435 5 161.00 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.2. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.3. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 b.4. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on CPK446 5 161.00 (547499) 161 kV Bus a. Apply Fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.3. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on BOL 73 5 161.00 (547464) 161 kV Bus a. Apply Fault at the BOL 73 5 161.00 (547464) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. BOL 73 5 (547464) 161.0 kV to BOL 73 2 (547528) 69.0 kV to BOL 73 1 (547701) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.4. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.5. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 b.6. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit # b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 b.2. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.3. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.4. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 b.5. DAD368 5 (547478) 161.0 kV to GEN-2019-016 (763560) 161.0 kV Transmission Circuit #1 b.6. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on JOP422 5 161.00 (547607) 161 kV Bus a. Apply Fault at the JOP422 5 161.00 (547607) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.3. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L3G3821 (547653) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L2G382 1 (547652) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on LAR382 5 161.00 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. LAR382 5 (547479) 161.0 kV to L1G382 1 (547651) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 b.3. 5MAURER 2 (344558) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. EAST SUB 2 (533990) 69.0 kV to GEN-2020-003 (765085) 69.0 kV Transmission Circuit #1 b.9. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply Fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 b.2. HITCHLD_TR11 (523092) 13.2 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV Three Winding #1 b.3. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPNSPUR_COL1 (524298) 34.5 kV to SPNSPUR_TR11 (524297) 13.2 kV to SPNSPUR_COL7 (524299) 345.0 kV Three Winding #1 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #1 b.4. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.8. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply Fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEST SUB 2 (533991) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 2LATHRP (300302) 69.0 kV Two Winding #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on 2VERONA 69.000 (300680) 69 kV Bus a. Apply Fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VERONA (300680) 69.0 kV to 2PRDYTP (300679) 69.0 kV Transmission Circuit #1 b.2. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.2. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply Fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SHARSNV (301515) 161.0 kV to 2SHARSNV (300709) 69.0 kV Two Winding #1 b.2. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on GEN-2011-022345.00 (523215) 345 kV Bus a. Apply Fault at the GEN-2011-022345.00 (523215) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-022 (523215) 345.0 kV to G11-022XFMR1 (523211) 34.5 kV Two Winding #1 b.2. GEN-2011-022 (523215) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply Fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARKCTYE2 (533542) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #z1 b.2. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on PARIS 2 69.000 (533548) 69 kV Bus a. Apply Fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARIS 2 (533548) 69.0 kV to ARKCTYW2 (533540) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply Fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply Fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC5SILV2 (533554) 69.0 kV to ARKCTYE2 (533542) 69.0 kV Transmission Circuit #1 b.2. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to HAYNE3 (539640) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r b.2. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on LEXNTON2 69.000 (541265) 69 kV Bus a. Apply Fault at the LEXNTON2 69.000 (541265) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEXNTON2 (541265) 69.0 kV to LEX69 2 (541264) 69.0 kV Transmission Circuit #1 b.2. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on 13&40 2 69.000 (541266) 69 kV Bus a. Apply Fault at the 13&40 2 69.000 (541266) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 13&40 2 (541266) 69.0 kV to ODESSA 2 (541267) 69.0 kV Transmission Circuit #1 b.2. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.2. PHILL 2 (541280) 69.0 kV to RGREEN 2 (541279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on ANCONDA2 69.000 (541292) 69 kV Bus a. Apply Fault at the ANCONDA2 69.000 (541292) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANCONDA2 (541292) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on HSNVLW 2 69.000 (541293) 69 kV Bus a. Apply Fault at the HSNVLW 2 69.000 (541293) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLW 2 (541293) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply Fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.2. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply Fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 b.2. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on RAYMORE 69.000 (541347) 69 kV Bus a. Apply Fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYMORE (541347) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply Fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNGSVIL 2 (541387) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MALTABN5 161.00 (543059) 161 kV Bus a. Apply Fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 b.2. PAOLA 5 (543069) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to LEXNTON2 (541265) 69.0 kV Transmission Circuit #1 b.2. MAYVWTP2 (543096) 69.0 kV to 13&40 2 (541266) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply Fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCOPL2 (543100) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.2. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to CTY HIG2 (543098) 69.0 kV Transmission Circuit #1 b.2. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on EXP449T2 69.000 (547438) 69 kV Bus a. Apply Fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 b.2. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on PRC460 2 69.000 (547449) 69 kV Bus a. Apply Fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 b.2. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on WEB436 2 69.000 (547527) 69 kV Bus a. Apply Fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 b.2. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on NIX114 2 69.000 (547535) 69 kV Bus a. Apply Fault at the NIX114 2 69.000 (547535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NIX114 2 (547535) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NIX114 2 (547535) 69.0 kV to BHJ415 2 (547604) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on AUR124 2 69.000 (547537) 69 kV Bus a. Apply Fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 b.2. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on MON152 2 69.000 (547540) 69 kV Bus a. Apply Fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON152 2 (547540) 69.0 kV to AUR124 2 (547537) 69.0 kV Transmission Circuit #1 b.2. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on TIP292 2 69.000 (547559) 69 kV Bus a. Apply Fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIP292 2 (547559) 69.0 kV to NEO332 2 (547571) 69.0 kV Transmission Circuit #1 b.2. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on JOP360 2 69.000 (547581) 69 kV Bus a. Apply Fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP360 2 (547581) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 b.2. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 2 (547595) 69.0 kV to KOD471 2 (547463) 69.0 kV Transmission Circuit #1 b.2. RNM393 2 (547595) 69.0 kV to RNM393 5 (547500) 161.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on COX 269.000 (549910) 69 kV Bus a. Apply Fault at the COX 269.000 (549910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COX 2 (549910) 69.0 kV to PLAINVIEW 2 (549905) 69.0 kV Transmission Circuit #1 b.2. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on DAYTON 269.000 (549913) 69 kV Bus a. Apply Fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 b.2. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on LAUREL 269.000 (549924) 69 kV Bus a. Apply Fault at the LAUREL 269.000 (549924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAUREL 2 (549924) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 b.2. LAUREL 2 (549924) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 2 (549925) 69.0 kV to NIC170 2 (547542) 69.0 kV Transmission Circuit #1 b.2. NICHOLS 2 (549925) 69.0 kV to NICHOLS 5 (549956) 161.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on FRISCO 269.000 (549926) 69 kV Bus a. Apply Fault at the FRISCO 269.000 (549926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRISCO 2 (549926) 69.0 kV to NICHOLS 2 (549925) 69.0 kV Transmission Circuit #1 b.2. FRISCO 2 (549926) 69.0 kV to N HWY13 2 (549927) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on GEN-2010-014345.00 (576395) 345 kV Bus a. Apply Fault at the GEN-2010-014345.00 (576395) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2010-014 (576395) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 b.2. GEN-2010-014 (576395) 345.0 kV to G10-014XFMR2 (576398) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on GEN-2017-108161.00 (761271) 161 kV Bus a. Apply Fault at the GEN-2017-108161.00 (761271) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-108 (761271) 161.0 kV to G17-108-XFM1 (761272) 34.5 kV Two Winding #1 b.2. GEN-2017-108 (761271) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). The issue is also observed in the PQ case and is not impacted by the CQ units | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDLIAW_CAP5 (541146) 161.0 kV Transmission Circuit #r b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply Fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWAVRLY5 (543063) 161.0 kV to MALTABN5 (543059) 161.0 kV Transmission Circuit #1 b.2. SWAVRLY5 (543063) 161.0 kV to SWAVRLY2 (543094) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on AUR124 5 161.00 (547468) 161 kV Bus a. Apply Fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.2. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on NEO184 5 161.00 (547471) 161 kV Bus a. Apply Fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO184 5 (547471) 161.0 kV to 2NEOSAC (300748) 69.0 kV Two Winding #1 b.2. NEO184 5 (547471) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on DAD368 5 161.00 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 5 (547480) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.2. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on RNM393 5 161.00 (547500) 161 kV Bus a. Apply Fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.2. NICHOLS 5 (549956) 161.0 kV to JUNCTION 5 (549955) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to CRESWLN2 (533543) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on UDALL 2 69.000 (533559) 69 kV Bus a. Apply Fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UDALL 2 (533559) 69.0 kV to RICHLAN2 (533550) 69.0 kV Transmission Circuit #1 b.2. UDALL 2 (533559) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on MON383 5 161.00 (547480) 161 kV Bus a. Apply Fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MON383 2 (547591) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 b.2. MON383 2 (547591) 69.0 kV to MON383 5 (547480) 161.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on NORTON 5 (543064) 161 kV Bus a. Apply Fault at the NORTON 5 (543064) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTON 5 (543064) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on 5NORTON (300105) 161 kV Bus a. Apply Fault at the 5NORTON (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on CORDERTP2 (543657) 69 kV Bus a. Apply Fault at the CORDERTP2 (543657) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORDERTP2 (543657) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on CTY HIG2 (543098) 69 kV Bus a. Apply Fault at the CTY HIG2 (543098) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTY HIG2 (543098) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on HIGNSVL2 (543099) 69 kV Bus a. Apply Fault at the HIGNSVL2 (543099) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGNSVL2 (543099) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on WHGNSVL2 (543102) 69 kV Bus a. Apply Fault at the WHGNSVL2 (543102) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHGNSVL2 (543102) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on MAYVWTP2 (543096) 69 kV Bus a. Apply Fault at the MAYVWTP2 (543096) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYVWTP2 (543096) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on SALSBRY5 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALSBRY5 (543062) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on 5THMHILB1 (300120) 161 kV Bus a. Apply Fault at the 5THMHILB1 (300120) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on 5THMHLB2 (300132) 161 kV Bus a. Apply Fault at the 5THMHLB2 (300132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB2 (300132) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on 5THMHLB4 (301443) 161 kV Bus a. Apply Fault at the 5THMHLB4 (301443) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on 5MAURER 2 (344558) 161 kV Bus a. Apply Fault at the 5MAURER 2 (344558) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MAURER 2 (344558) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on WINFLD 2 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINFLD 2 (533561) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on OAK 2 (533547) 69 kV Bus a. Apply Fault at the OAK 2 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on HOLCOMB3 (531448) 115 kV Bus a. Apply Fault at the HOLCOMB3 (531448) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIM-PLT3 (539654) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on NORTH6T2 (531389) 69 kV Bus a. Apply Fault at the NORTH6T2 (531389) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTH6T2 (531389) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on GRTBEND3 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on LENEXA 5 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on SWISVAL7 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on LNGVW 5 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on KETCHEM7 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on HAWTHN5 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on SIBLEYPL (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on HSNVL 2 (541295) 69 kV Bus a. Apply Fault at the HSNVL 2 (541295) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HSNVL 2 (541295) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on JOP389 5 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on SEDALIA5 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on S.OTTWA5 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on PAOLA 5 (543069) 161 kV Bus a. Apply Fault at the PAOLA 5 (543069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAOLA 5 (543069) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on JOP 59 2 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD5 (505492) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGFLD2 (505494) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 5 (549969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKLINE 7 (549984) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on CARTHAG5 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on DAD368 5 (547478) 161 kV Bus a. Apply Fault at the DAD368 5 (547478) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAD368 5 (547478) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_EDE6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy10 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy11 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy12 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy13 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy14 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy15 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy16 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy17 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy18 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy19 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy20 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy21 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy22 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy23 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy24 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy25 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy26 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy27 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy28 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy29 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy30 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy31 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy32 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy33 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy34 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy35 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy36 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy37 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy38 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy39 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy40 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy41 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy42 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy43 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy44 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy45 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy46 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy47 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy48 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy49 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy50 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy51 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy52 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy53 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy54 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy55 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy56 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy57 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy58 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy59 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy60 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy7 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy8 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_Evergy9 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA1 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_GRDA2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_INDN3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_OKGE2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPRM1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS3 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS4 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS5 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SPS6 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC1 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SUNC2 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA1 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_SWPA2 | Single Phase Fault with Stuck Breaker on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit # b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 b.2. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_084 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_127 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_129 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_131 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_134 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_137 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_144 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_146 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_147 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_157 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_163 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_165 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_184 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_186 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_454 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_555 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Power oscillations observed due to non-convergences following the fault at the BUFF_DUNES (523061 and 523052) generating site. System adjustments and changing the acceleration factors resolves the issue. | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_019 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_021 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P1_REGIONAL_FAULT_030 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2020-001 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power output of WCGS U1 (532751). | No mitigation required.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, GEN-2016-097 trips on voltage protection settings | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, GEN-2016-097 trips on voltage protection settings | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BORDER_____7__TUCO_INT_7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV BUS 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BVRCNTY7_BADGER7_6 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV BUS 515677 TO BVRCNTY7 345.0 KV BUS 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHISHOLM7__BECKHAM7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUGO___7__G17-075-TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, GEN-2020-020 trips on voltage protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | O.K.U._7__G18-015-TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD7__G16_075_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings, RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027, GEN -2017-172, GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN -2017-172, GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TUCO_INT___7__BORDER7_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV BUS 515458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TUCO_INT___7__ELK_CT1_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV BUS 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TUCO_INT___7__G17-151TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV BUS 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TUCO_INT___7__G20-067-TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV BUS 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c.Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATNGSW4__CALUMET4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATNGSW4__OKEENE_4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATNGSW4__OMEGA__4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATNGSW4__WATONGA4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | ROMNOSE4_514823 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-027
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BORDER_____7__TUCO_INT_7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV BUS 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BVRCNTY7_BADGER7_6 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV BUS 515677 TO BVRCNTY7 345.0 KV BUS 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHISHOLM7__BECKHAM7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUGO___7__G17-075-TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, GEN-2020-020 trips on voltage protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | O.K.U._7__G18-015-TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD7__G16_075_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings, RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027, GEN -2017-172, GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN -2017-172, GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TUCO_INT___7__BORDER7_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV BUS 515458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TUCO_INT___7__ELK_CT1_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV BUS 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TUCO_INT___7__G17-151TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV BUS 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TUCO_INT___7__G20-067-TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV BUS 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c.Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATNGSW4__CALUMET4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATNGSW4__OKEENE_4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATNGSW4__OMEGA__4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATNGSW4__WATONGA4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | ROMNOSE4_514823 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_49_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515785 TO 520999 CKT 1 and Open DISCONNECT LINE 520999 to 520462 ckt 1 and DISCONNECT LINE 520462 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 521001 CKT 1 and DISCONNECT LOAD 1 520462 and DISCONNECT LOAD 1 520492 and DISCONNECT LOAD 1 520500 and DISCONNECT 520462 and DISCONNECT 520492 and DISCONNECT 520500 and DISCONNECT 521128 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_99_P5_Anadarko | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-027
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25S | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 | 25W | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 , GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 , GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 , GEN-2016-097 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095, GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BORDER_____7__TUCO_INT_7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV BUS 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BVRCNTY7_BADGER7_6 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV BUS 515677 TO BVRCNTY7 345.0 KV BUS 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUGO___7__G17-075-TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, GEN-2020-020 trips on voltage protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | O.K.U._7__G18-015-TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD7__G16_075_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings, RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027, GEN -2017-172, GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN -2017-172, GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TUCO_INT___7__BORDER7_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV BUS 515458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TUCO_INT___7__ELK_CT1_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV BUS 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TUCO_INT___7__G17-151TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV BUS 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TUCO_INT___7__G20-067-TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV BUS 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c.Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | ROMNOSE4_514823 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-027
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BORDER_____7__TUCO_INT_7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV BUS 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BVRCNTY7_BADGER7_6 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV BUS 515677 TO BVRCNTY7 345.0 KV BUS 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CIMARON7__MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUGO___7__G17-075-TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G17-075-TAP 345.0 KV 560088 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings, GEN-2020-020 trips on voltage protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-020
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MATHWSN7__REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | O.K.U._7__G18-015-TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD7__G16_075_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-075-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings, GEN-2020-009 trips on voltage protection settings, RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 and RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG Gens trip on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN2-WTG Gens prevents trip. There are no stability constraints when the generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | RSHSPR-1-B trips on voltage protection settings | Disabling instantaneous voltage protection settings for RSHSPR-1-B prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027, GEN -2017-172, GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN -2017-172, GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings, GEN-2016-097 trips on voltage protection settings | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. Disabling instantaneous voltage protection settings for GEN-2016-097 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TUCO_INT___7__BORDER7_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO BORDER 7 345.0 KV BUS 515458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Disabling frequency protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TUCO_INT___7__ELK_CT1_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV BUS 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TUCO_INT___7__G17-151TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV BUS 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TUCO_INT___7__G20-067-TAP_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV BUS 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c.Trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | KEENAN GEN trips on frequency protection settings | Disabling frequency protection settings for KEENAN GEN prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 7GRIMES__3340260_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES%( 334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 334028 TO 4GRIMES% 334026 TO 1GRIMES_1 334163 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSJT2__5114400_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2( 511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 511441 TO ALTUSJT4 511440 TO ALTUS2-1 511420 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ANADARK4__5208100_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ARMFTWD4__5156950_7 | 3 Phase fault on ARMFTWD4 (515694) 138 kV Bus a. Apply fault at the ARMFTWD4( 515694) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMFTWD4 515694 TO ARMFTL11 515695 TO ARMFTT11 515698 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___2__5080540_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BUFBEAR2__5211390_7 | 3 Phase fault on BUFBEAR2 (521120) 69 kV Bus a. Apply fault at the BUFBEAR2( 521120) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFBEAR2 521120 TO BUFFBR CL1 521139 TO BUFFBR TERT 521150 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | C_RIVER7__5109460_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATOOSA2__5097900_7 | 3 Phase fault on CATOOSA2 (509799) 69 kV Bus a. Apply fault at the CATOOSA2( 509799) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA2 509799 TO CATOOSA4 509790 TO CATOO1-1 509867 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CATSAGR5__5097900_7 | 3 Phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply fault at the CATSAGR5( 512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 512638 TO CATOOSA4 509790 TO 512835 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CENT___4__5153650_7 | 3 Phase fault on CENT 4 (515363) 138 kV Bus a. Apply fault at the CENT 4( 515363) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENT 4 515363 TO CENT 21 515365 TO CENT 11 515364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHIKSAW2__5151710_7 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHLDR2WT__5121010_7 | 3 Phase fault on CHLDR2WT (512100) 69 kV Bus a. Apply fault at the CHLDR2WT( 512100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHLDR2WT 512100 TO CHILD4WT 512101 TO WC2TERT 512102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHSHLMV7__5154790_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CHSHLMV7__5154840_6 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR2__5147780_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2( 514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 514777 TO CLEOCOR4 514778 TO CLEOCOR1 515716 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COWCRK_2__5147060_7 | 3 Phase fault on COWCRK 2 (514705) 69 kV Bus a. Apply fault at the COWCRK 2( 514705) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 2 514705 TO COWCRK 4 514706 TO COWCRK 1 515717 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COWSKIN_4__5127170_7 | 3 Phase fault on COWSKIN 4 (512719) 138 kV Bus a. Apply fault at the COWSKIN 4( 512719) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN 4 512719 TO COWSKIN2 512717 TO COWSKIN1 512738 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CROCKET4__5092410_7 | 3 Phase fault on CROCKET4 (509240) 138 kV Bus a. Apply fault at the CROCKET4( 509240) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROCKET4 509240 TO CROCKET7 509241 TO CROCK-B1 509243 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEC392_5__5475940_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5( 547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 547484 TO DEC392 2 547594 TO DEC392 1 547714 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DGRASSE4__5158520_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DMNDSPG7__5160040_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DMNDSPG7__5160050_6 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DUNCAN_2__5114530_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2( 511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 511452 TO DUNCAN-4 511453 TO DUNC2-1 511410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELGINJT2__5114860_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCTY_2__5114580_7 | 3 Phase fault on ELKCTY-2 (511459) 69 kV Bus a. Apply fault at the ELKCTY-2( 511459) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-2 511459 TO ELKCTY-4 511458 TO ELKC4-1 511493 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELKCTY_4__5114900_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ELRENO_2__5148190_7 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_04_DOVERSW4__5208810_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_04_IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_04_SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_CHISHOLM6__5115530_7 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_CIMARON4__5149010_7 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_05_VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_06_DIANA__4__5088320_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_06_PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_06_SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FLETCH_4__5209110_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FPLWIND4__5157870_7 | 3 Phase fault on FPLWIND4 (515786) 138 kV Bus a. Apply fault at the FPLWIND4( 515786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FPLWIND4 515786 TO FPLWND11 515787 TO FLPWND21 515790 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSUPLY4__5209190_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4( 520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 520920 TO FTSUPLY2 520919 TO FTSUPTERTB 521182 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRACMNT4__5158000_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRNDFLD4__5209260_7 | 3 Phase fault on GRNDFLD4 (521106) 138 kV Bus a. Apply fault at the GRNDFLD4( 521106) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFLD4 521106 TO GRANFLD2 520926 TO GRNDTERT 521184 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GROVE__4__5104110_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4( 510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 510402 TO GROVE 5 510411 TO GROVE1-1 510368 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HOB_JCT2__5114630_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2( 511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 511464 TO HOB-JCT4 511463 TO HOBJT1-1 511417 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUGO___7__5205600_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IMO____2__5147900_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2( 514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 514721 TO IMO 4 514790 TO IMO 1 515788 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_4__5148090_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KEENAN_1__5153940_7 | 3 Phase fault on KEENAN 1 (515393) 34.5 kV Bus a. Apply fault at the KEENAN 1( 515393) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEENAN 1 515393 TO KEENAN 4 515394 TO KEENAN T 515392 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_BRK1_5__5126340_7 | 3 Phase fault on KERR BRK1 5 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5( 512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 512770 TO KERR GR3 512634 TO KERR1 1 512846 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KERR_BRK4_5__5126340_7 | 3 Phase fault on KERR BRK4 5 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5( 512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 512771 TO KERR GR3 512634 TO KERR2 1 512847 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KINGWD_7__5160170_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL11 516017 TO KNGWDT11 516020 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | KINGWD_7__5160180_6 | 3 Phase fault on KINGWD 7 (516019) 345 kV Bus a. Apply fault at the KINGWD 7( 516019) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGWD 7 516019 TO KNGWDL21 516018 TO KNGWDT21 516021 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LAKEP2WT__5121100_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT( 512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 512111 TO LAKEP4WT 512110 TO LP2TERT 512112 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_2__5114670_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES_4__5114680_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LONGWD_4__5088090_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LSSOUTH2__5082970_7 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MANDEVILTP4__5043630_7 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARAUTO2__5085570_7 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MARIETA4__5209870_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MOORLND4__5209950_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MORWODS4__5210000_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4( 521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 521001 TO MORWODS2 521000 TO MRWDTERT 521172 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NE_ENID2__5147690_7 | 3 Phase fault on NE ENID2 (514732) 69 kV Bus a. Apply fault at the NE ENID2( 514732) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID2 514732 TO NE ENID4 514769 TO NE ENID1 515741 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NEO184_5__5475430_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5( 547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 547471 TO NEO184 2 547543 TO NEO184B1 547709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NNBOSTN2__5080690_7 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NOL435_5__5476100_7 | 3 Phase fault on NOL435 5 (547496) 161 kV Bus a. Apply fault at the NOL435 5( 547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 547496 TO NOL435 2 547610 TO NOL435 1 547720 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORMHLL7__5160970_6 | 3 Phase fault on NORMHLL7 (516096) 345 kV Bus a. Apply fault at the NORMHLL7( 516096) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORMHLL7 516096 TO NORMHLL4 516097 TO NORMHL21 516099 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NORTWST4__5148800_7 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK4__5080720_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OKAY___2__5074280_7 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OKEENE_4__5210150_7 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PATTERS2__5074310_7 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_4__5085630_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT2__5104190_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2( 510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 510400 TO PRY-JCT4 510419 TO PRYJT2-1 510369 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT4__5104070_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4( 510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 510419 TO PRY-JCT3 510407 TO PRYJT1-1 510371 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDDIRT7__5158780_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT11 515878 TO RDDRTT11 515884 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | REDDIRT7__5158790_6 | 3 Phase fault on REDDIRT7 (515877) 345 kV Bus a. Apply fault at the REDDIRT7( 515877) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDDIRT7 515877 TO RDDIRT21 515879 TO RDDRTT21 515885 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RENFROW4__5155430_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RKY_RDG4__5119620_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-2CB 511962 TO RKYRDG2-1 511555 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RKY_RDG4__5119630_7 | 3 Phase fault on RKY_RDG4 (511554) 138 kV Bus a. Apply fault at the RKY_RDG4( 511554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKY_RDG4 511554 TO RKYRDGW1-1CB 511963 TO RKYRDG1-1 511556 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROCKYPT2__5151640_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSHSPR7__5119650_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSELL4__5210420_7 | 3 Phase fault on RUSSELL4 (521043) 138 kV Bus a. Apply fault at the RUSSELL4( 521043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL4 521043 TO RUSSELL2 521042 TO RSLTERT 521175 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SEMINOL4__5150450_7 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SETEXAR2__5080780_7 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SFOREMAN__4__5040300_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SKELTON7__5159910_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7( 515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 515990 TO SKELTL11 515991 TO SKELTT11 515992 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SLEEPBR4__5211410_7 | 3 Phase fault on SLEEPBR4 (520922) 138 kV Bus a. Apply fault at the SLEEPBR4( 520922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLEEPBR4 520922 TO SLP BR CL1 521141 TO SLP BR TERT 521151 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_2__5114350_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2( 511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 511475 TO SNYDER-4 511435 TO SNYDRTER 511419 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4__5210510_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4( 521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 521052 TO SNYDER 2 521051 TO SNYDTERT 521176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SO4TH__2__5147310_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SOONER_4__5148030_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUGARHL2__5080800_7 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNDANC4__5160240_7 | 3 Phase fault on SUNDANC4 (516025) 138 kV Bus a. Apply fault at the SUNDANC4( 516025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDANC4 516025 TO SUNDCL11 516024 TO SUNDCT11 516026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4__5151360_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD7__5151350_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SW_SHV_7__5077590_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_2__5114770_7 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SWS_4__5118490_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TALOGA_4__5210640_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | THISTLE7__5398040_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | THUNDER7__5158900_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | THUNDER7__5158910_6 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TLGAWND1__5153900_7 | 3 Phase fault on TLGAWND1 (515389) 34.5 kV Bus a. Apply fault at the TLGAWND1( 515389) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TLGAWND1 515389 TO TLGAWND4 515390 TO TLGAWNDT 515388 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TRAVERSE3__5873010_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___3__5074540_7 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___4__5074550_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VALIANT4__5109110_7 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VINTAJC2__5104170_7 | 3 Phase fault on VINTAJC2 (510418) 69 kV Bus a. Apply fault at the VINTAJC2( 510418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 510418 TO VINTAJC4 510417 TO VINJT1-1 510367 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WATLANT2__5080900_7 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WEKIWA_4__5097550_7 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WHITNEY2__5085750_7 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WILKES_4__5088410_7 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG4__5147150_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD4__5147820_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4( 514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 514785 TO WODWRD 2 514782 TO WOODWR21 515771 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV4__5153750_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE_All_34_P4_5_CTNWOOD4 | Single Phase Fault with Stuck Breaker on CTNWOOD4 (514827) 138.0 kV bus a.Apply single-phase fault on CTNWOOD4 (514827) 138.0 kV bus b.Run for 22.02 cycles and trip the following elements: b. 1. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 2. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 3. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 4. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 5. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 10.38 cycles and trip the following elements: b. 6. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.3 cycles and trip the following elements: b. 7. Close branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 3.96 cycles and trip the following elements: b. 8. Close branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 9. Close branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 1.74 cycles and trip the following elements: b. 10. Close branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.3 cycles and trip the following elements: b. 11. Close branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 9.3 cycles and trip the following elements: b. 12. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 1.08 cycles and trip the following elements: b. 13. Close branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 5.34 cycles and trip the following elements: b. 14. Open branch from MCELROY4 (515009) 138.0 kV bus to UNVRSTY4 (515181) 138.0 kV bus CKT 1 b.Run for 7.92 cycles and trip the following elements: b. 15. Open branch from KETCH (514834) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 16. Open branch from CRESENT4 (515377) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 3.48 cycles and trip the following elements: b. 17. Open branch from KINZE (515008) 138.0 kV bus to KINZEGR4 (512710) 138.0 kV bus CKT 1 b.Run for 0.6 cycles and trip the following elements: b. 18. Open branch from WOODRNG4 (514714) 138.0 kV bus to MARSHL (514733) 138.0 kV bus CKT 1 b.Run for 0.96 cycles and trip the following elements: b. 19. Close branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b.Run for 19.8 cycles and trip the following elements: b. 20. Open branch from ARCADIA4 (514907) 138.0 kV bus to CTNWOOD4 (514827) 138.0 kV bus CKT 1 b.Run for 37.8 cycles and trip the following elements: b. 21. Open branch from NORTWST4 (514879) 138.0 kV bus to KETCHTP4 (514828) 138.0 kV bus CKT 1 b. 22. Clear fault from CTNWOOD4 (514827) b. 23. Drop load from CTNWOOD4 (514827 ID 1) 138.0 kV bus b. 24. Drop load from PINE (514829 ID 1) 138.0 kV bus b. 25. Drop load from PINE (514829 ID 2) 138.0 kV bus b. 26. Drop load from FITZGRD4 (514830 ID 1) 138.0 kV bus b. 27. Drop load from WATRLOO4 (514831 ID 1) 138.0 kV bus b. 28. Drop load from UNVRSTY4 (515181 ID 1) 138.0 kV bus b. 29. Drop load from LBRTYLK4 (515373 ID 1) 138.0 kV bus b. 30. Drop load from MITCHSB4 (515466 ID 1) 138.0 kV bus b. 31. Drop load from WHITESB4 (515467 ID 1) 138.0 kV bus b. 32. Drop load from MARSHAL4 (521006 ID 1) 138.0 kV bus b. 33. Disconnect MARSHL (514733) 138.0 kV bus b. 34. Disconnect CTNWOOD4 (514827) 138.0 kV bus b. 35. Disconnect KETCHTP4 (514828) 138.0 kV bus b. 36. Disconnect PINE (514829) 138.0 kV bus b. 37. Disconnect FITZGRD4 (514830) 138.0 kV bus b. 38. Disconnect WATRLOO4 (514831) 138.0 kV bus b. 39. Disconnect KINZE (515008) 138.0 kV bus b. 40. Disconnect UNVRSTY4 (515181) 138.0 kV bus b. 41. Disconnect LBRTYLK4 (515373) 138.0 kV bus b. 42. Disconnect MITCHSB4 (515466) 138.0 kV bus b. 43. Disconnect WHITESB4 (515467) 138.0 kV bus b. 44. Disconnect MARSHAL4 (521006) 138.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-029 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_76_P4_TONECE5 | Single Phase Fault with Stuck Breaker on TONECE5 (512751) 161.0 kV bus a.Apply single-phase fault on TONECE5 (512751) 161.0 kV bus b.Run for 15.0 cycles and trip the following elements: b. 1. Open branch from SILMCTY5 (512643) 161.0 kV bus to TONECE5 (512751) 161.0 kV bus CKT 1 b. 2. Clear fault from TONECE5 (512751) b. 3. Disconnect TONNEC1 (512754) 13.2 kV bus b. 4. Drop load from SSLINC2 (512745 ID 1) 69.0 kV bus b. 5. Drop load from SSNORT2 (512746 ID 1) 69.0 kV bus b. 6. Disconnect ARKLIN2 (512728) 69.0 kV bus b. 7. Disconnect SSLINC2 (512745) 69.0 kV bus b. 8. Disconnect SSNORT2 (512746) 69.0 kV bus b. 9. Disconnect SSNEWN2 (512747) 69.0 kV bus b. 10. Disconnect TONECESTR2 (512756) 69.0 kV bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE_All_32_P4_3_VBI5 | Apply single-phase fault on and DISCONNECT 515339, near VBI 5 for 146 cycles with stuck breaker at VBI 5 ( 515339) 161 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE_All_33_P4_4_WODWRD2 | Apply single-phase fault on and DISCONNECT 514782, near WODWRD 2 (514872) 69 kV Bus for 274 cycles with stuck breaker at WODWRD 2 (514872) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4 | No | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | 112GORE4_511488 | Apply single-phase fault on: 112GORE4 138.0 KV 511488 TO COMANC-4 138.0 KV 511437 CKT 1, near 112GORE4 138 kV for 7 cycles with stuck breaker at 112GORE4 138 kV. Clear Fault after 10 cycles and trip: 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ALTUSJT4_511440 | Apply single-phase fault on: ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1, near ALTUSJT4 138 kV for 7 cycles with stuck breaker at ALTUSJT4 138 kV. Clear Fault after 10 cycles and trip: ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | BANN___4_508054 | Apply single-phase fault on: BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CACHEJ4_521190 | Apply single-phase fault on: CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1, near CACHEJ4 138 kV for 7 cycles with stuck breaker at CACHEJ4 138 kV. Clear Fault after 10 cycles and trip: CACHEJ4 138.0 KV 521190 TO MDCPRK4 138.0 KV 520404 CKT 1 LOAD 1 520404 MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 LOAD 1 521024 PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOCOR4_514778 | Apply single-phase fault on: CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1, near CLEOCOR4 138 kV for 7 cycles with stuck breaker at CLEOCOR4 138 kV. Clear Fault after 10 cycles and trip: CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CLEOPLT4_515562 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO CLEO PL4 138.0 KV 515553 CKT 1, near CLEOPLT4 138 kV for 7 cycles with stuck breaker at CLEOPLT4 138 kV. Clear Fault after 10 cycles and trip: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | COMMTAP4_511494 | Apply single-phase fault on: COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1, near COMMTAP4 138 kV for 7 cycles with stuck breaker at COMMTAP4 138 kV. Clear Fault after 10 cycles and trip: COMMTAP4 138.0 KV 511494 TO L.E.S.-4 138.0 KV 511467 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CROCKET7_509241 | Apply single-phase fault on: CROCKET7 345.0 KV 509241 TO 7GRIMES% 345.0 KV 334028 CKT 1, near CROCKET7 345 kV for 6 cycles with stuck breaker at CROCKET7 345 kV. Clear Fault after 10 cycles and trip: CROCKET7 345.0 KV 509241 TO TENRUSK7 345.0 KV 508585 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | DEWEY__4_514787 | Apply single-phase fault on: DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1, near DEWEY 4 138 kV for 7 cycles with stuck breaker at DEWEY 4 138 kV. Clear Fault after 10 cycles and trip: REDCLFT4 138.0 KV 515533 TO DEWEY 4 138.0 KV 514787 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | EXCLART4_510401 | Apply single-phase fault on: EXCLART4 138.0 KV 510401 TO 510373 CKT 1 510373 TO 510437 CKT 1 509752 TO 510437 CKT 1, near EXCLART4 138 kV for 7 cycles with stuck breaker at EXCLART4 138 kV. Clear Fault after 10 cycles and trip: EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 LOAD 1 510431 PRY_CRK4 138.0 KV 510431 TO MCARBDE4 138.0 KV 510366 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FRMNTAP4_514709_0 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near FRMNTAP4 138 kV for 7 cycles with stuck breaker at FRMNTAP4 138 kV. Clear Fault after 10 cycles and trip: FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 LOAD 1 514712 FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 LOAD 1 515641 PLNSMEN4 138.0 KV 515641 TO BRECKNR4 138.0 KV 514815 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSUPLY2_520919 | Apply single-phase fault on: FTSUPLY2 69.0 KV 520919 TO STOCKHOLM2 69.0 KV 520421 CKT 1 LOAD 1 520421 STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1, near FTSUPLY2 69 kV for 7 cycles with stuck breaker at FTSUPLY2 69 kV. Clear Fault after 10 cycles and trip: FTSUPLY2 69.0 KV 520919 TO FTSPLY 2 69.0 KV 520456 CKT 1 LOAD 1 520456 LOAD 2 520456 FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FTSUPLY4_520920 | Apply single-phase fault on: FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1, near FTSUPLY4 138 kV for 7 cycles with stuck breaker at FTSUPLY4 138 kV. Clear Fault after 10 cycles and trip: FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 LOAD 1 520957 IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G176_TAP_588779 | Apply single-phase fault on: G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1, near G17-036_TAP 138 kV for 7 cycles with stuck breaker at G17-036_TAP 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G18_092_PROX_763215 | Apply single-phase fault on: G18-092-PROX 345.0 KV 763215 TO CRAWFISH_DR 345.0 KV 560022 CKT 2, near G18-092-PROX 345 kV for 6 cycles with stuck breaker at G18-092-PROX 345 kV. Clear Fault after 10 cycles and trip: G18-092-PROX 345.0 KV 763215 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | G185_TAP_762467 | Apply single-phase fault on: G18-015-TAP 345.0 KV 762467 TO G17-151TAP 345.0 KV 762216 CKT 1, near G18-015-TAP 345 kV for 6 cycles with stuck breaker at G18-015-TAP 345 kV. Clear Fault after 10 cycles and trip: G18-015-TAP 345.0 KV 762467 TO L.E.S.-7 345.0 KV 511468 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GOTEBO_2_520925 | Apply single-phase fault on: GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1, near GOTEBO 2 69 kV for 7 cycles with stuck breaker at GOTEBO 2 69 kV. Clear Fault after 10 cycles and trip: STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 LOAD 1 521033 ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 LOAD 1 520955 WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 LOAD 1 520866 CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GRACMNT7_515800 | Apply single-phase fault on: GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1, near GRACMNT7 345 kV for 6 cycles with stuck breaker at GRACMNT7 345 kV. Clear Fault after 10 cycles and trip: GRACMNT7 345.0 KV 515800 TO MINCO 7 345.0 KV 514801 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | GROVE__4_510402 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near GROVE 4 138 kV for 7 cycles with stuck breaker at GROVE 4 138 kV. Clear Fault after 10 cycles and trip: GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HOB_JCT4_511463 | Apply single-phase fault on: HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1, near HOB-JCT4 138 kV for 7 cycles with stuck breaker at HOB-JCT4 138 kV. Clear Fault after 10 cycles and trip: HOB-JCT4 138.0 KV 511463 TO CL-AFTP4 138.0 KV 511446 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | HUNTERS7_515476 | Apply single-phase fault on: HUNTERS7 345.0 KV 515476 TO WOODRNG7 345.0 KV 514715 CKT 1, near HUNTERS7 345 kV for 6 cycles with stuck breaker at HUNTERS7 345 kV. Clear Fault after 10 cycles and trip: HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | IMO____4_514790 | Apply single-phase fault on: CLEOPLT4 138.0 KV 515562 TO MENOTAP4 138.0 KV 514789 CKT 1 LOAD 1 514789 MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1, near IMO 4 138 kV for 7 cycles with stuck breaker at IMO 4 138 kV. Clear Fault after 10 cycles and trip: IMO 4 138.0 KV 514790 TO GLENWD 4 138.0 KV 514734 CKT 1 LOAD 1 514734 GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | JOHNCO_7_514809 | Apply single-phase fault on: JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO 7 345 kV for 6 cycles with stuck breaker at JOHNCO 7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LEBROCK7_508572 | Apply single-phase fault on: LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1, near LEBROCK7 345 kV for 6 cycles with stuck breaker at LEBROCK7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES4_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LES7_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LWS_NTP4_511471 | Apply single-phase fault on: LWS-NTP4 138.0 KV 511471 TO LWS N4 138.0 KV 511430 CKT 1, near LWS-NTP4 138 kV for 7 cycles with stuck breaker at LWS-NTP4 138 kV. Clear Fault after 10 cycles and trip: LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | LYDIA__7_508298 | Apply single-phase fault on: LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1, near LYDIA 7 345 kV for 6 cycles with stuck breaker at LYDIA 7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MOORLND4_520999 | Apply single-phase fault on: MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1, near MOORLND4 138 kV for 7 cycles with stuck breaker at MOORLND4 138 kV. Clear Fault after 10 cycles and trip: MOORLND4 138.0 KV 520999 TO GLASMTN4 138.0 KV 514788 CKT 1 LOAD 1 514788 LOAD 2 514788 GLASMTN4 138.0 KV 514788 TO CLEOCOR4 138.0 KV 514778 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | MORWODS4_521001 | Apply single-phase fault on: MORWODS4 138.0 KV 521001 TO ELLIS 4 138.0 KV 511561 CKT 1 LOAD 1 511561 ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 LOAD 1 520459 CUSTER 4 138.0 KV 520459 TO 521116 CKT 1, near MORWODS4 138 kV for 7 cycles with stuck breaker at MORWODS4 138 kV. Clear Fault after 10 cycles and trip: MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NINMLTP4_521128 | Apply single-phase fault on: NINMLTP4 138.0 KV 521128 TO MORWODS4 138.0 KV 521001 CKT 1, near NINMLTP4 138 kV for 7 cycles with stuck breaker at NINMLTP4 138 kV. Clear Fault after 10 cycles and trip: NINMLTP4 138.0 KV 521128 TO BEARCAT4 138.0 KV 520500 CKT 1 LOAD 1 520500 BEARCAT4 138.0 KV 520500 TO ASPEN 4 138.0 KV 520462 CKT 1 LOAD 1 520462 ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWT_BNT4_508070 | Apply single-phase fault on: NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 10 cycles and trip: BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK4_508071 | Apply single-phase fault on: NWTXARK4 138.0 KV 508071 TO NASH 4 138.0 KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 10 cycles and trip: NWTXARK4 138.0 KV 508071 TO NWT-BNT4 138.0 KV 508070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | NWTXARK7_508072 | Apply single-phase fault on: NWTXARK7 345.0 KV 508072 TO TURK 7 345.0 KV 507455 CKT 1, near NWTXARK7 345 kV for 6 cycles with stuck breaker at NWTXARK7 345 kV. Clear Fault after 10 cycles and trip: NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | OKEENE_4_521016 | Apply single-phase fault on: OKEENE 4 138.0 KV 521016 TO CDRDLTP4 138.0 KV 520848 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 10 cycles and trip: OKEENE 4 138.0 KV 521016 TO WATNGSW4 138.0 KV 520536 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PINTAIL7_516010 | Apply single-phase fault on: PINTAIL7 345.0 KV 516010 TO WOODRNG7 345.0 KV 514715 CKT 1, near PINTAIL7 345 kV for 6 cycles with stuck breaker at PINTAIL7 345 kV. Clear Fault after 10 cycles and trip: PINTAIL7 345.0 KV 516010 TO SOONER 7 345.0 KV 514803 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PIRKEY_7_508563 | Apply single-phase fault on: PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1, near PIRKEY 7 345 kV for 6 cycles with stuck breaker at PIRKEY 7 345 kV. Clear Fault after 10 cycles and trip: LEBROCK7 345.0 KV 508572 TO PIRKEY 7 345.0 KV 508563 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT2_510400 | Apply single-phase fault on: PRY-JCT2 69.0 KV 510400 TO ADAIR--2 69.0 KV 510387 CKT 1 LOAD 1 510387 ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1, near PRY-JCT2 69 kV for 7 cycles with stuck breaker at PRY-JCT2 69 kV. Clear Fault after 10 cycles and trip: PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | PRY_JCT4_510419 | Apply single-phase fault on: PRY-JCT4 138.0 KV 510419 TO BIRDHOL4 138.0 KV 510398 CKT 1 LOAD 1 510398 BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 LOAD 1 510421 JAY 4 138.0 KV 510421 TO GROVE 4 138.0 KV 510402 CKT 1, near PRY-JCT4 138 kV for 7 cycles with stuck breaker at PRY-JCT4 138 kV. Clear Fault after 10 cycles and trip: PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | ROMNOSE4_514823 | Apply single-phase fault on: ROMNOSE4 138.0 KV 514823 TO SOUTHRD4 138.0 KV 514822 CKT 1 LOAD 1 514822 LOAD 2 514822 SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 LOAD 1 515964 CANTNLK4 138.0 KV 515964 TO DEWEY 4 138.0 KV 514787 CKT 1, near ROMNOSE4 138 kV for 7 cycles with stuck breaker at ROMNOSE4 138 kV. Clear Fault after 10 cycles and trip: ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | RUSSELL4_521043 | Apply single-phase fault on: RUSSELL4 138.0 KV 521043 TO 512110 CKT 1, near RUSSELL4 138 kV for 7 cycles with stuck breaker at RUSSELL4 138 kV. Clear Fault after 10 cycles and trip: RUSSELL4 138.0 KV 521043 TO ALTUSJT4 138.0 KV 511440 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_2_511475 | Apply single-phase fault on: SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1, near SNYDER-2 69 kV for 7 cycles with stuck breaker at SNYDER-2 69 kV. Clear Fault after 10 cycles and trip: SNYDER-2 69.0 KV 511475 TO TIPTE T2 69.0 KV 511472 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_2_521051 | Apply single-phase fault on: SNYDER 2 69.0 KV 521051 TO SNYDRSB2 69.0 KV 520541 CKT Z1 LOAD 1 520541 SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1, near SNYDER 2 69 kV for 7 cycles with stuck breaker at SNYDER 2 69 kV. Clear Fault after 10 cycles and trip: SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4_511435 | Apply single-phase fault on: SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1, near SNYDER-4 138 kV for 7 cycles with stuck breaker at SNYDER-4 138 kV. Clear Fault after 10 cycles and trip: SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SNYDER_4_521052 | Apply single-phase fault on: SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1, near SNYDER 4 138 kV for 7 cycles with stuck breaker at SNYDER 4 138 kV. Clear Fault after 10 cycles and trip: SNYDER 4 138.0 KV 521052 TO SNYDER-4 138.0 KV 511435 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD4_515135 | Apply single-phase fault on: SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 LOAD 1 515137 UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 LOAD 1 515372 CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1, near SUNNYSD4 138 kV for 7 cycles with stuck breaker at SUNNYSD4 138 kV. Clear Fault after 10 cycles and trip: SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | SUNNYSD7_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TALOGA_2_521064 | Apply single-phase fault on: TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 LOAD 1 521082 VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1, near TALOGA 2 69 kV for 7 cycles with stuck breaker at TALOGA 2 69 kV. Clear Fault after 10 cycles and trip: TALOGA 2 69.0 KV 521064 TO CANTON-2 69.0 KV 520843 CKT 1 LOAD 1 520843 LOAD 2 520843 CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TALOGA_4_521065 | Apply single-phase fault on: TALOGA 4 138.0 KV 521065 TO DEWEY 4 138.0 KV 514787 CKT 1, near TALOGA 4 138 kV for 7 cycles with stuck breaker at TALOGA 4 138 kV. Clear Fault after 10 cycles and trip: G20-010-TAP 138.0 KV 765215 TO TALOGA 4 138.0 KV 521065 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TERRYRD7_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | TURK___7_507455 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1, near TURK 7 345 kV for 6 cycles with stuck breaker at TURK 7 345 kV. Clear Fault after 10 cycles and trip: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | VALIANT7_510911 | Apply single-phase fault on: TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345 kV for 6 cycles with stuck breaker at VALIANT7 345 kV. Clear Fault after 10 cycles and trip: LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WAUKOTP4_514711 | Apply single-phase fault on: WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1, near WAUKOTP4 138 kV for 7 cycles with stuck breaker at WAUKOTP4 138 kV. Clear Fault after 10 cycles and trip: WAUKOTP4 138.0 KV 514711 TO WAUKOMI4 138.0 KV 514710 CKT 1 LOAD 1 514710 WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WELSH__7_508359 | Apply single-phase fault on: WELSH 7 345.0 KV 508359 TO LYDIA 7 345.0 KV 508298 CKT 1, near WELSH 7 345 kV for 6 cycles with stuck breaker at WELSH 7 345 kV. Clear Fault after 10 cycles and trip: WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WILKES_7_508841 | Apply single-phase fault on: WILKES 7 345.0 KV 508841 TO LONGWD 7 345.0 KV 508809 CKT 1 LOAD 1 508311, near WILKES 7 345 kV for 6 cycles with stuck breaker at WILKES 7 345 kV. Clear Fault after 10 cycles and trip: WILKES 7 345.0 KV 508841 TO NWTXARK7 345.0 KV 508072 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG4_514714 | Apply single-phase fault on: WOODRNG4 138.0 KV 514714 TO FRMNTAP4 138.0 KV 514709 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 10 cycles and trip: WOODRNG4 138.0 KV 514714 TO OTTER 4 138.0 KV 514708 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODRNG7_514715 | Apply single-phase fault on: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1, near WOODRNG7 345 kV for 6 cycles with stuck breaker at WOODRNG7 345 kV. Clear Fault after 10 cycles and trip: WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WOODWRD2_521096 | Apply single-phase fault on: WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1, near WOODWRD2 69 kV for 7 cycles with stuck breaker at WOODWRD2 69 kV. Clear Fault after 10 cycles and trip: WOODWRD2 69.0 KV 521096 TO WODWRD 2 69.0 KV 514782 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | WWRDEHV4_515376 | Apply single-phase fault on: WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1, near WWRDEHV4 138 kV for 7 cycles with stuck breaker at WWRDEHV4 138 kV. Clear Fault after 10 cycles and trip: WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_74_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 515853 CKT 1 and DISCONNECT LINE 520436 TO 515853 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_67_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6.0 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 Run fault at MOORLND4 (520999) 138 kV Bus for 9.0 cycles, clear fault and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_49_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515785 TO 520999 CKT 1 and Open DISCONNECT LINE 520999 to 520462 ckt 1 and DISCONNECT LINE 520462 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 520500 CKT 1 and DISCONNECT LINE 521128 TO 521001 CKT 1 and DISCONNECT LOAD 1 520462 and DISCONNECT LOAD 1 520492 and DISCONNECT LOAD 1 520500 and DISCONNECT 520462 and DISCONNECT 520492 and DISCONNECT 520500 and DISCONNECT 521128 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_48_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520999 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 520425 CKT 1 and DISCONNECT LINE 520848 TO 521016 CKT 1 and DISCONNECT LOAD 1 520425 and DISCONNECT LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520507 and DISCONNECT 520848 and DISCONNECT LINE 520920 TO 520957 CKT 1 and DISCONNECT LINE 520999 TO 520957 CKT 1 and DISCONNECT LOAD 1 520957 and DISCONNECT 520957 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_47_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 515853 TO 520999 CKT 1 and DISCONNECT LOAD 1 520553 and DISCONNECT 520553 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_46_P2_4_MOORLND4 | Apply single-phase fault at MOORLND4 (520999) 138 kV Bus for 6 cycles and DISCONNECT LINE 520996 TO 520999 CKT 1 and DISCONNECT LINE 520998 TO 520999 CKT 1 and DISCONNECT GENERATOR 1 520996 and DISCONNECT LOAD F1 520996 and DISCONNECT LOAD V1 520996 and DISCONNECT 520996 and DISCONNECT GENERATOR 1 520998 and DISCONNECT LOAD F1 520998 and DISCONNECT LOAD V1 520998 and DISCONNECT 520998 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_45_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 900000 CKT 1 and DISCONNECT GENERATOR 1 520947 and DISCONNECT LINE 520834 TO 900001 CKT 1 and DISCONNECT LINE 520947 TO 520948 CKT 1 and DISCONNECT LOAD F1 520947 and DISCONNECT LOAD V1 520947 and DISCONNECT 520947 and DISCONNECT LOAD 1 520419 and DISCONNECT LOAD 1 520466 and DISCONNECT LOAD 1 520834 and DISCONNECT LOAD 1 520946 and DISCONNECT LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_44_P2_4_HUGOPP4 | Apply single-phase fault at HUGO PP4 (520948) 138 kV Bus for 6 cycles and DISCONNECT LINE 520948 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520411 CKT 1 and DISCONNECT LINE 521036 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 520874 CKT 1 and DISCONNECT LINE 520968 TO 510887 CKT 1 and DISCONNECT LINE 505602 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 505600 CKT 1 and DISCONNECT LINE 521074 TO 520448 CKT 1 and DISCONNECT LINE 521074 TO 510887 CKT 1 and DISCONNECT LOAD 1 515370 and DISCONNECT LOAD 1 515568 and DISCONNECT LOAD 1 520463 and DISCONNECT LOAD 1 520483 and DISCONNECT LOAD 1 520497 and DISCONNECT LOAD 1 520918 and DISCONNECT LOAD 1 521077 and DISCONNECT LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and DISCONNECT LOAD 1 520411 and DISCONNECT LOAD 1 520874 and DISCONNECT LOAD 1 520968 and DISCONNECT LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_43_P2_3_PHAROAH4 | Apply single-phase fault at PHAROAH4 (521026) 138 kV Bus for 6 cycles and DISCONNECT LINE 300686 TO 521026 CKT 1 and DISCONNECT LINE 301553 TO 521026 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_42_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520924 CKT 1 and DISCONNECT LINE 521104 TO 520924 CKT 1 and DISCONNECT LOAD 1 520924 and DISCONNECT 520924 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_41_P2_3_CANADNS4 | Apply single-phase fault at CANADNS4 (520842) 138 kV Bus for 6 cycles and DISCONNECT 514947 and DISCONNECT LINE 520842 TO 520400 CKT 1 and DISCONNECT LINE 520975 TO 520400 CKT 1 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_40_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520975 CKT 1 and DISCONNECT LINE 520400 TO 520842 CKT 1 and DISCONNECT LOAD 1 520400 and DISCONNECT LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_39_P2_3_FRNKLNS4 | Apply single-phase fault at FRNKLNS4 (520917) 138 kV Bus for 6 cycles and DISCONNECT 514946 and DISCONNECT LINE 520917 TO 520913 CKT 1 and DISCONNECT LINE 521028 TO 520913 CKT 1 and DISCONNECT LOAD 1 520913 and DISCONNECT 520913 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_38_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 521089 TO 521017 CKT 1 and DISCONNECT LOAD 1 520468 and DISCONNECT LOAD 1 520503 and DISCONNECT LOAD 1 520856 and DISCONNECT LOAD 1 520950 and DISCONNECT LOAD 1 521010 and DISCONNECT LOAD 2 521010 and DISCONNECT LOAD 1 521017 and DISCONNECT LOAD 1 521050 and DISCONNECT LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_37_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 511477 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_36_P2_3_WASHITA4 | Apply single-phase fault at WASHITA4 (521089) 138 kV Bus for 6 cycles and DISCONNECT LINE 515802 TO 521089 CKT 1 and DISCONNECT LINE 515802 TO 521089 CKT 2 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_35_P2_3_ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus for 6 cycles and DISCONNECT GENERATOR 1 521101 and DISCONNECT GENERATOR 1 521102 and DISCONNECT GENERATOR 1 521110 and DISCONNECT GENERATOR 1 521111 and DISCONNECT GENERATOR 1 521112 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_WFEC_All_34_P2_2_PAOLI4 | Apply single-phase fault at PAOLI 4 (521023) 138 kV Bus for 6 cycles and DISCONNECT 521023 and DISCONNECT 521174 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_9_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6.0 cycles, clear fault and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 20.0 cycles and CLOSE LINE 514778 TO 515562 CKT 1 and CLOSE LINE 515562 TO 514789 CKT 1 and CLOSE LINE 514789 TO 514790 CKT 1 and CLOSE LINE 514778 TO 514788 CKT 1 and CLOSE LINE 514788 TO 520999 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_8_P2_2_MASSARD5 | Apply single-phase fault at MASSARD5 (515343) 161 kV Bus for 6 cycles and DISCONNECT LINE 515293 TO 515343 CKT 1 and DISCONNECT LINE 515311 TO 515343 CKT 1 and DISCONNECT LINE 515341 TO 515343 CKT 1 and DISCONNECT LINE 515343 TO 515523 CKT 1 and DISCONNECT 515735 and DISCONNECT LOAD 1 515343 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_7_P2_2_BRISTOW4 | Apply single-phase fault at BRISTOW4 (515035) 138 kV Bus for 6 cycles and DISCONNECT LINE 515035 TO 515048 CKT 1 and DISCONNECT LINE 515035 TO 515242 CKT 1 and DISCONNECT LINE 515035 TO 515249 CKT 1 and DISCONNECT LINE 515035 TO 515417 CKT 1 and DISCONNECT 515709 and DISCONNECT LOAD 1 515035 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_6_P2_2_MCCLAIN4 | Apply single-phase fault at MCCLAIN4 (514902) 138 kV Bus for 6 cycles and DISCONNECT LINE 514902 TO 514998 CKT 1 and DISCONNECT LINE 514902 TO 514999 CKT 1 and DISCONNECT GENERATOR 1 514998 and DISCONNECT LOAD S1 514998 and DISCONNECT 514998 and DISCONNECT GENERATOR 1 514999 and DISCONNECT LOAD S1 514999 and DISCONNECT 514999 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_12_P2_4_MUSKOGE5 | Apply single-phase fault at MUSKOGE5 (515222) 161 kV Bus for 6 cycles and DISCONNECT LINE 505558 TO 515222 CKT 1 and DISCONNECT LINE 515222 TO 515232 CKT 1 and DISCONNECT LINE 515222 TO 515640 CKT 1 and DISCONNECT LINE 515222 TO 516027 CKT 1 and DISCONNECT 515797 and DISCONNECT 515739 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_11_P2_3_BEEDISCONNECT LINE4 | Apply single-phase fault at BEELINE4 (515247) 138 kV Bus for 6 cycles and DISCONNECT 515705 and DISCONNECT LINE 515247 TO 515473 CKT 1 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_OKGE_All_10_P2_3_CLEOCOR4 | Apply single-phase fault at CLEOCOR4 (514778) 138 kV Bus for 6 cycles and DISCONNECT LINE 514778 TO 515562 CKT 1 and DISCONNECT LINE 515562 TO 514789 CKT 1 and DISCONNECT LINE 514789 TO 514790 CKT 1 and DISCONNECT LINE 514778 TO 514788 CKT 1 and DISCONNECT LINE 514788 TO 520999 CKT 1 and DISCONNECT LOAD 1 514788 and DISCONNECT LOAD 2 514788 and DISCONNECT LOAD 1 514789 and DISCONNECT LOAD 1 515553 and DISCONNECT 514788 and DISCONNECT 514789 and DISCONNECT 515553 and DISCONNECT 515562 | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Apply single-phase fault at ANADARK4 (520814) 138 kV Bus 6 cycles and DISCONNECT LINE 521031 TO 520814 CKT 1 and DISCONNECT BUS | P2 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__WFEC-All-33-P2_2-ANADARK4 | Single phase fault with stuck relay near ANADARK4 (520814) 138 kV Bus a. Apply Fault at theANADARK4 (520814) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 520814 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_98_P5_Claremore | Single phase fault with stuck relay near CLARMR 4 (512707) 138 kV Bus a. Apply Fault at theCLARMR 4 (512707) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 513124 TO 512707 CKT 1 b.2. DISCONNECT 513124 b.3. LINE 510396 TO 513124 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_97_P5_36th&Olympia | Single phase fault with stuck relay near 36&OLY-4 (509724) 138 kV Bus a. Apply Fault at the36&OLY-4 (509724) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509724 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_96_P5_SapulpaRd | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 509871 TO 509848 CKT 1 b.2. LOAD 1 509727 b.3. DISCONNECT 509727 b.4. DISCONNECT 509848 b.5. LINE 509848 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_95_P5_Carson | Single phase fault with stuck relay near CARSN-S4 (509756) 138 kV Bus a. Apply Fault at theCARSN-S4 (509756) 138 kV Bus b. Clear fault after 4 cycles and trip the faulted elements: b.1. LINE 509756 TO 509788 CKT 1 b.2. LOAD 1 509742 b.3. LOAD 1 509756 b.4. LOAD 1 509777 b.5. DISCONNECT 509742 b.6. DISCONNECT 509756 b.7. DISCONNECT 509777 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_94_P5_72nd&Elwood | Single phase fault with stuck relay near 72ELWOD4 (509888) 138 kV Bus a. Apply Fault at the72ELWOD4 (509888) 138 kV Bus b. Clear fault after 45 cycles and trip the faulted elements: b.1. LINE 509888 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_93_P5_Riverside | Single phase fault with stuck relay near R.S.S.-4 (509783) 138 kV Bus a. Apply Fault at theR.S.S.-4 (509783) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 509783 TO 509814 CKT 1 b.2. LOAD 1 509856 b.3. LOAD 1 509859 b.4. DISCONNECT 509814 b.5. DISCONNECT 509856 b.6. DISCONNECT 509859 b.7. LINE 509814 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_92_P5_36th&Lewis | Single phase fault with stuck relay near 36LEWIS4 (509800) 138 kV Bus a. Apply Fault at the36LEWIS4 (509800) 138 kV Bus b. Clear fault after 65 cycles and trip the faulted elements: b.1. LINE 509800 TO 509788 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-027 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2018-027
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_37_P5_NWHenderson | Single phase fault with stuck relay near NWHENDR4 (509076) 138 kV Bus a. Apply Fault at theNWHENDR4 (509076) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509076 TO 509077 CKT 1 b.2. LINE 509077 TO 509078 CKT 1 b.3. LOAD 1 509077 b.4. LOAD 1 509078 b.5. DISCONNECT 509077 b.6. DISCONNECT 509078 b.7. LINE 509078 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_36_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 24 cycles and trip the faulted elements: b.1. LINE 508544 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_35_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 36 cycles and trip the faulted elements: b.1. LINE 508570 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_34_P5_RockHill | Single phase fault with stuck relay near ROKHILL4 (509083) 138 kV Bus a. Apply Fault at theROKHILL4 (509083) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509083 TO 509087 CKT 1 b.2. LINE 509087 TO 509059 CKT 1 b.3. LOAD 1 509059 b.4. LOAD 1 509087 b.5. LOAD 2 509087 b.6. DISCONNECT 509059 b.7. DISCONNECT 509087 b.8. LINE 509059 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_33_P5_Pirkey | Single phase fault with stuck relay near PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at thePIRKEY 4 (508562) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508562 TO 509092 CKT 1 b.2. LINE 509092 TO 508596 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 508596 TO 508548 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_32_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508575 TO 508595 CKT 1 b.2. LOAD 1 508595 b.3. DISCONNECT 508595 b.4. LINE 508595 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_31_P5_KnoxLee | Single phase fault with stuck relay near KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at theKNOXLEE4 (508548) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 508548 TO 508596 CKT 1 b.2. LINE 508596 TO 509092 CKT 1 b.3. LOAD 1 509092 b.4. LOAD 1 509605 b.5. DISCONNECT 508596 b.6. DISCONNECT 509092 b.7. DISCONNECT 509605 b.8. LINE 509092 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_30_P5_Scottsville | Single phase fault with stuck relay near SCOTTSV4 (508567) 138 kV Bus a. Apply Fault at theSCOTTSV4 (508567) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508567 TO 508569 CKT 1 b.2. LINE 508569 TO 508566 CKT 1 b.3. LOAD 1 508569 b.4. LOAD 1 508577 b.5. LOAD 2 508577 b.6. DISCONNECT 508566 b.7. DISCONNECT 508569 b.8. DISCONNECT 508577 b.9. LINE 508566 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_29_P5_Marshall | Single phase fault with stuck relay near MARSHL-4 (508557) 138 kV Bus a. Apply Fault at theMARSHL-4 (508557) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508557 TO 508562 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_28_P5_STXEastman | Single phase fault with stuck relay near SOTXEST4 (508570) 138 kV Bus a. Apply Fault at theSOTXEST4 (508570) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508570 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_27_P5_Harrison | Single phase fault with stuck relay near HARRISN4 (508544) 138 kV Bus a. Apply Fault at theHARRISN4 (508544) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508544 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_26_P5_Whitney | Single phase fault with stuck relay near WHITNEY4 (508575) 138 kV Bus a. Apply Fault at theWHITNEY4 (508575) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 508575 TO 508582 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_25_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507738 TO 507742 CKT 1 b.2. LOAD 1 507742 b.3. DISCONNECT 507742 b.4. LINE 507742 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_24_P5_Longwood | Single phase fault with stuck relay near LONGWD 4 (508808) 138 kV Bus a. Apply Fault at theLONGWD 4 (508808) 138 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 508808 TO 507774 CKT 1 b.2. LINE 507774 TO 507749 CKT 1 b.3. LOAD 1 507749 b.4. LOAD 1 507774 b.5. DISCONNECT 507749 b.6. DISCONNECT 507774 b.7. LINE 507749 TO 507711 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_23_P5_FlintCreek | Single phase fault with stuck relay near FLINTCR5 (506934) 161 kV Bus a. Apply Fault at theFLINTCR5 (506934) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506934 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_22_P5_Lowell | Single phase fault with stuck relay near LOWELL 5 (506938) 161 kV Bus a. Apply Fault at theLOWELL 5 (506938) 161 kV Bus b. Clear fault after 21 cycles and trip the faulted elements: b.1. LINE 506938 TO 506991 CKT 1 b.2. LOAD 1 506991 b.3. DISCONNECT 506991 b.4. LINE 506991 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_21_P5_ChamberSprings | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506944 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_20_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 504010 CKT 1 b.2. LOAD A1 504010 b.3. DISCONNECT 504010 b.4. DISCONNECT 504011 b.5. DISCONNECT 504012 b.6. DISCONNECT 504013 b.7. DISCONNECT 504014 b.8. LINE 504010 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_19_P5_Dyess | Single phase fault with stuck relay near DYESS 5 (506927) 161 kV Bus a. Apply Fault at theDYESS 5 (506927) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506927 TO 506957 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_18_P5_Decatur | Single phase fault with stuck relay near DEC392 5 (547484) 161 kV Bus a. Apply Fault at theDEC392 5 (547484) 161 kV Bus b. Clear fault after 23 cycles and trip the faulted elements: b.1. LINE 547484 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_17_P5_Tontitown | Single phase fault with stuck relay near TONTITN5 (506957) 161 kV Bus a. Apply Fault at theTONTITN5 (506957) 161 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 506957 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_16_P5_Siloam | Single phase fault with stuck relay near SILOAM 5 (506948) 161 kV Bus a. Apply Fault at theSILOAM 5 (506948) 161 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 506948 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_15_P5_ChambersSpring | Single phase fault with stuck relay near CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at theCHAMSPR5 (506944) 161 kV Bus b. Clear fault after 25 cycles and trip the faulted elements: b.1. LINE 506944 TO 504202 CKT 1 b.2. LOAD A1 504202 b.3. DISCONNECT 504202 b.4. LINE 504202 TO 506934 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_12_P5_Linwood | Single phase fault with stuck relay near LINWOOD4 (507738) 138 kV Bus a. Apply Fault at theLINWOOD4 (507738) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 507742 TO 507711 CKT 1 b.2. LINE 507771 TO 507755 CKT 1 b.3. LOAD 1 507738 b.4. LOAD 1 507742 b.5. LOAD 1 507748 b.6. DISCONNECT 507738 b.7. DISCONNECT 507742 b.8. DISCONNECT 507748 b.9. DISCONNECT 507771 b.10. LINE 507748 TO 507759 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_110_P5_Henryetta138kV | Single phase fault with stuck relay near HENRYET4 (510892) 138 kV Bus a. Apply Fault at theHENRYET4 (510892) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 510892 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_109_P5_WeleetkaSWPA | Single phase fault with stuck relay near WELEETK4 (505592) 138 kV Bus a. Apply Fault at theWELEETK4 (505592) 138 kV Bus b. Clear fault after 33 cycles and trip the faulted elements: b.1. LINE 505592 TO 510902 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_108_P5_SapulpaRoad | Single phase fault with stuck relay near SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at theSAPLPRD4 (509871) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509871 TO 509759 CKT 1 b.2. LINE 509759 TO 509753 CKT 1 b.3. LOAD 1 509753 b.4. LOAD 1 509759 b.5. DISCONNECT 509753 b.6. DISCONNECT 509759 b.7. LINE 509753 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_107_P5_OG&Ebee | Single phase fault with stuck relay near BEELINE4 (515247) 138 kV Bus a. Apply Fault at theBEELINE4 (515247) 138 kV Bus b. Clear fault after 26 cycles and trip the faulted elements: b.1. LINE 515247 TO 515473 CKT 1 b.2. LOAD 1 515248 b.3. DISCONNECT 515248 b.4. DISCONNECT 515473 b.5. LINE 515473 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_106_P5_KimberlyClark.id | Single phase fault with stuck relay near KIMCLRK4 (509845) 138 kV Bus a. Apply Fault at theKIMCLRK4 (509845) 138 kV Bus b. Clear fault after 35 cycles and trip the faulted elements: b.1. LINE 509845 TO 509775 CKT 1 b.2. LOAD 1 509775 b.3. DISCONNECT 509775 b.4. LINE 509775 TO 509783 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_105_P5_96th&Yale | Single phase fault with stuck relay near 96YALE-4 (509847) 138 kV Bus a. Apply Fault at the96YALE-4 (509847) 138 kV Bus b. Clear fault after 27 cycles and trip the faulted elements: b.1. LINE 509847 TO 509858 CKT 1 b.2. LINE 509858 TO 509849 CKT 1 b.3. LINE 509849 TO 509783 CKT 1 b.4. LOAD 1 509738 b.5. LOAD 1 509810 b.6. LOAD 1 509857 b.7. DISCONNECT 509738 b.8. DISCONNECT 509810 b.9. DISCONNECT 509849 b.10. DISCONNECT 509857 b.11. DISCONNECT 509858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_104_P5_SouthHudson | Single phase fault with stuck relay near S.HUD.-4 (509833) 138 kV Bus a. Apply Fault at theS.HUD.-4 (509833) 138 kV Bus b. Clear fault after 55 cycles and trip the faulted elements: b.1. LINE 509833 TO 509764 CKT 1 b.2. LINE 509764 TO 509809 CKT 1 b.3. LINE 509809 TO 509813 CKT 1 b.4. LINE 509813 TO 509853 CKT 1 b.5. LINE 509853 TO 509783 CKT 1 b.6. LOAD 1 509729 b.7. LOAD 1 509730 b.8. LOAD 1 509731 b.9. LOAD 1 509732 b.10. DISCONNECT 509729 b.11. DISCONNECT 509730 b.12. DISCONNECT 509731 b.13. DISCONNECT 509732 b.14. DISCONNECT 509764 b.15. DISCONNECT 509809 b.16. DISCONNECT 509813 b.17. DISCONNECT 509853 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_103_P5_LES | Single phase fault with stuck relay near L.E.S.-2 (511466) 69 kV Bus a. Apply Fault at theL.E.S.-2 (511466) 69 kV Bus b. Clear fault after 41 cycles and trip the faulted elements: b.1. LINE 511466 TO 511436 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_102_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 72 cycles and trip the faulted elements: b.1. LINE 511467 TO 511494 CKT 1 b.2. LINE 511494 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-009 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points) for GEN-2020-009
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_101_P5_LES | Single phase fault with stuck relay near L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at theL.E.S.-4 (511467) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 511467 TO 511437 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT_AEPW_2022_100_P5_Washita | Single phase fault with stuck relay near WASHITA4 (521089) 138 kV Bus a. Apply Fault at theWASHITA4 (521089) 138 kV Bus b. Clear fault after 8 cycles and trip the faulted elements: b.1. LINE 521089 TO 511477 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE-All-38-P5_2-WINDFRM4 | Single phase fault with stuck relay near WINDFRM4 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 (515785) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 b.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 b.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 c. Run fault for 37.02 cycles and c.1. CLOSE LINE FROM BUS 515785 TO BUS 515786 CKT 1 c.2. CLOSE LINE FROM BUS 514785 TO BUS 515785 CKT 1 c.3. CLOSE LINE FROM BUS 515785 TO BUS 520999 CKT 1 d. Clear fault after 64.02 cycles and trip faulted elements d.1. LINE FROM BUS 515785 TO BUS 515786 CKT 1 d.2. LINE FROM BUS 514785 TO BUS 515785 CKT 1 d.3. LINE FROM BUS 515785 TO BUS 520999 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE-All-37-P5_2-TARBY5 | Single phase fault with stuck relay near TARBY5 (515264) 161 kV Bus a. Apply Fault at the TARBY5 (515264) 161 kV Bus b. Run fault for 24 cycles and trip faulted elements b.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 b.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 c. Run fault for 34 cycles and trip faulted elements c.1. LINE FROM BUS 515262 TO BUS 515264 CKT 1 d. Run fault for 34 cycles and d.1. CLOSE LINE FROM BUS 515259 TO BUS 515275 CKT 1 d.2. CLOSE LINE FROM BUS 515259 TO BUS 515260 CKT 1 e. Run fault for 59 cycles and trip faulted elements e.1. LINE FROM BUS 515259 TO BUS 515275 CKT 1 e.2. LINE FROM BUS 515259 TO BUS 515260 CKT 1 f. Run fault for 80 cycles and trip faulted elements f.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 g. Run fault for 90 cycles and g.1. CLOSE LINE FROM BUS 515282 TO BUS 515276 CKT 1 h. Run fault for 126 cycles and trip faulted elements h.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 i. Run fault for 136 cycles and i.1. CLOSE LINE FROM BUS 515263 TO BUS 515272 CKT 1 j. Run fault for 170 cycles and trip faulted elements j.1. LINE FROM BUS 515282 TO BUS 515276 CKT 1 k. Run fault for 185 cycles and trip faulted elements k.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 l. Run fault for 195 cycles and l.1. CLOSE LINE FROM BUS 515264 TO BUS 515265 CKT 1 m. Run fault for 262 cycles and trip faulted elements m.1. LINE FROM BUS 515263 TO BUS 515272 CKT 1 n. Clear fault after 380 cycles and trip faulted elements n.1. LINE FROM BUS 515264 TO BUS 515265 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__OKGE-All-36-P5_1-INGLEWD4 | Single phase fault with stuck relay near INGLEWD (515060) 138 kV Bus a. Apply Fault at the INGLEWD (515060) 138 kV Bus b. Run fault for 37.98 cycles and trip faulted elements b.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 c. Run fault for 19.98 cycles and trip faulted elements c.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 d. Run fault for 37.98 cycles and trip faulted elements d.1. LINE FROM BUS 515060 TO BUS 515059 CKT 1 e. Run fault for 56.46 cycles and trip faulted elements e.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 f. Run fault for 19.98 cycles and trip faulted elements f.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 g. Run fault for 97.80 cycles g.1. CLOSE LINE FROM BUS 515442 TO BUS 515046 CKT 1 h. Run fault for 16.62 cycles and trip faulted elements h.1. LINE FROM BUS 514941 TO BUS 515480 CKT 1 i. Run fault for 27.60 cycles and trip faulted elements i.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 j. Run fault for 6.60 cycles and trip faulted elements j.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 k. Run fault for 6.00 cycles and trip faulted elements k.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 l. Run fault for 7.38 cycles and trip faulted elements l.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 m. Run fault for 6.60 cycles m.1. CLOSE LINE FROM BUS 514973 TO BUS 514964 CKT 1 n. Run fault for 6.00 cycles n.1. CLOSE LINE FROM BUS 514993 TO BUS 514941 CKT 1 o. Run fault for 21.00 cycles and trip faulted elements o.1. LINE FROM BUS 515442 TO BUS 515046 CKT 1 p. Run fault for 30.6 cycles and trip faulted elements p.1. LINE FROM BUS 514973 TO BUS 514884 CKT 1 q. Run fault for 13.20 cycles and trip faulted elements q.1. LINE FROM BUS 514973 TO BUS 514964 CKT 1 r. Run fault for 12.00 cycles and trip faulted elements r.1. LINE FROM BUS 514993 TO BUS 514941 CKT 1 s. Run fault for 20.82 cycles and trip faulted elements s.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 t. Run fault for 19.98 cycles t.1. CLOSE LINE FROM BUS 514941 TO BUS 514906 CKT 1 u. Run fault for 57.42 cycles and trip faulted elements u.1. LINE FROM BUS 514927 TO BUS 514937 CKT 1 v. Clear fault after 60.00 cycles and trip the faulted elements v.1. LINE FROM BUS 514941 TO BUS 514906 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-91-P5-TulsaSoutheast | Single phase fault with stuck relay near Tulsa SouthEast (509811) 138 kV Bus a. Apply Fault at the Tulsa SouthEast (509811) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 509811 TO BUS 509831 CKT 1 b.2. LINE FROM BUS 509811 TO BUS 509833 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 509781 TO BUS 509718 CKT 1 d. Run fault for 4 cycles and trip faulted elements d.1. LINE FROM BUS 509763 TO BUS 509772 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509765 TO BUS 509855 CKT 1 f. Run fault for 4 cycles and trip faulted elements f.1. LINE FROM BUS 509785 TO BUS 509891 CKT 1 g. Clear fault after 9 cycles and trip the faulted elements g.1. LINE FROM BUS 509776 TO BUS 509800 CKT 1 g.2. LOAD 1 BUS 509716 g.3. LOAD 1 BUS 509717 g.4. LOAD 1 BUS 509728 g.5. LOAD 1 BUS 509733 g.6. LOAD 1 BUS 509734 g.7. LOAD 1 BUS 509735 g.8. LOAD 1 BUS 509744 g.9. LOAD 1 BUS 509760 g.10. LOAD 1 BUS 509761 g.11. LOAD 1 BUS 509774 g.12. LOAD 1 BUS 509779 g.13. LOAD 1 BUS 509780 g.14. LOAD 1 BUS 509797 g.15. LOAD 1 BUS 509808 g.16. LOAD 1 BUS 509811 g.17. LOAD 1 BUS 509824 g.18. LOAD 1 BUS 509826 g.19. LOAD 1 BUS 509827 g.20. LOAD 1 BUS 509829 g.21. LOAD 1 BUS 509861 g.22. LOAD 1 BUS 509886 g.23. DISCONNECT BUS 509716 g.24. DISCONNECT BUS 509717 g.25. DISCONNECT BUS 509718 g.26. DISCONNECT BUS 509728 g.27. DISCONNECT BUS 509733 g.28. DISCONNECT BUS 509734 g.29. DISCONNECT BUS 509735 g.30. DISCONNECT BUS 509744 g.31. DISCONNECT BUS 509760 g.32. DISCONNECT BUS 509761 g.33. DISCONNECT BUS 509762 g.34. DISCONNECT BUS 509763 g.35. DISCONNECT BUS 509765 g.36. DISCONNECT BUS 509771 g.37. DISCONNECT BUS 509774 g.38. DISCONNECT BUS 509776 g.39. DISCONNECT BUS 509779 g.40. DISCONNECT BUS 509780 g.41. DISCONNECT BUS 509785 g.42. DISCONNECT BUS 509797 g.43. DISCONNECT BUS 509808 g.44. DISCONNECT BUS 509811 g.45. DISCONNECT BUS 509820 g.46. DISCONNECT BUS 509824 g.47. DISCONNECT BUS 509826 g.48. DISCONNECT BUS 509827 g.49. DISCONNECT BUS 509828 g.50. DISCONNECT BUS 509829 g.51. DISCONNECT BUS 509830 g.52. DISCONNECT BUS 509861 g.53. DISCONNECT BUS 509873 g.54. DISCONNECT BUS 509886 g.55. LINE FROM BUS 509771 TO BUS 509790 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-90-P5-TulsaNorth | Single phase fault with stuck relay near Tulsa North (509817) 138 kV Bus a. Apply Fault at the Tulsa North (509817) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 509842 TO BUS 509784 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 509863 TO BUS 509801 CKT 1 c.2. LINE FROM BUS 509844 TO BUS 509860 CKT 1 c.3. DISCONNECT BUS 509894 d. Run fault for 5 cycles and trip faulted elements d.1. LINE FROM BUS 509839 TO BUS 509887 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 509851 TO BUS 509757 CKT 1 f. Run fault for 1 cycles and trip faulted elements f.1. LINE FROM BUS 509817 TO BUS 510396 CKT 1 g. Clear fault after 11 cycles and trip the faulted elements g.1. LINE FROM BUS 509884 TO BUS 510388 CKT 1 g.2. LOAD 1 BUS 509714 g.3.LOAD 1 BUS 509715 g.4. LOAD 1 BUS 509726 g.5. LOAD 1 BUS 509743 g.6. LOAD 1 BUS 509805 g.7. LOAD 1 BUS 509817 g.8. LOAD 1 BUS 509818 g.9. LOAD 1 BUS 509822 g.10. LOAD 1 BUS 509825 g.11. LOAD 1 BUS 509837 g.12. LOAD 1 BUS 509840 g.13. LOAD 1 BUS 509884 g.14. DISCONNECT BUS 509714 g.15. DISCONNECT BUS 509715 g.16 DISCONNECT BUS 509726 g.17. DISCONNECT BUS 509743 g.18. DISCONNECT BUS 509746 g.19. DISCONNECT BUS 509805 g.20. DISCONNECT BUS 509817 g.21. DISCONNECT BUS 509818 g.22. DISCONNECT BUS 509822 g.23. DISCONNECT BUS 509825 g.24. DISCONNECT BUS 509837 g.25. DISCONNECT BUS 509839 g.26. DISCONNECT BUS 509840 g.27. DISCONNECT BUS 509842 g.28. DISCONNECT BUS 509844 g.29. DISCONNECT BUS 509851 g.30. DISCONNECT BUS 509862 g.31. DISCONNECT BUS 509863 g.32. DISCONNECT BUS 509884 g.33. DISCONNECT BUS 509900 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-89-P5-Weleetka | Single phase fault with stuck relay near Weleetka (510902) 138 kV Bus a. Apply Fault at the Weleetka (510902) 138 kV Bus b. Run fault for 18 cycles and trip faulted elements b.1. LINE FROM BUS 510921 TO BUS 510908 CKT 1 c. Run fault for 6 cycles and trip faulted elements c.1. LINE FROM BUS 510877 TO BUS 510948 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 510902 TO BUS 505592 CKT 1 e. Run fault for 6 cycles and trip faulted elements e.1. LINE FROM BUS 510902 TO BUS 510892 CKT 1 f. Run fault for 24 cycles and trip faulted elements f.1. LINE FROM BUS 515078 TO BUS 510877 CKT 1 g. Clear fault after 5 cycles and trip faulted elements g.1. LINE FROM BUS 510923 TO BUS 510898 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-88-P5-TPS | Single phase fault with stuck relay near TPS (509788) 138 kV Bus a. Apply Fault at the TPS (509788) 138 kV Bus b. Run fault for 16 cycles and trip faulted elements b.1. LINE FROM BUS 509788 TO BUS 509724 CKT 1 c. Run fault for 15 cycles and trip faulted elements c.1. LINE FROM BUS 509788 TO BUS 509800 CKT 1 d. Run fault for 2 cycles and trip faulted elements d.1. LINE FROM BUS 509850 TO BUS 509783 CKT 1 d.2. LINE FROM BUS 509848 TO BUS 509871 CKT 1 e. Run fault for 2 cycles and trip faulted elements e.1. LINE FROM BUS 509788 TO BUS 509888 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 509814 TO BUS 509783 CKT 1 g. Clear fault after 195 cycles and trip faulted elements g.1. DISCONNECT BUS 509880 g.2. DROP GENERATOR 1 BUS 509890 g.3. DROP GENERATOR 1 BUS 511854 g.4. DROP GENERATOR 1 BUS 511858 g.5. DROP LOAD 1 BUS 509727 g.6. DROP LOAD 1 BUS 509742 g.7. DROP LOAD 1 BUS 509750 g.8. DROP LOAD 1 BUS 509751 g.9. DROP LOAD 1 BUS 509756 g.10. DROP LOAD 1 BUS 509777 g.11. DROP LOAD 1 BUS 509788 g.12. DROP LOAD 1 BUS 509789 g.13. DROP LOAD 1 BUS 509795 g.14. DROP LOAD 1 BUS 509846 g.15. DROP LOAD 1 BUS 509856 g.16. DROP LOAD 1 BUS 509859 g.17. DROP LOAD S1 BUS 511854 g.18. DROP LOAD S1 BUS 511858 g.19. DISCONNECT BUS 509727 g.20. DISCONNECT BUS 509742 g.21. DISCONNECT BUS 509750 g.22. DISCONNECT BUS 509751 g.23. DISCONNECT BUS 509756 g.24. DISCONNECT BUS 509777 g.25. DISCONNECT BUS 509795 g.26. DISCONNECT BUS 509814 g.27. DISCONNECT BUS 509846 g.28. DISCONNECT BUS 509848 g.29. DISCONNECT BUS 509850 g.30. DISCONNECT BUS 509856 g.31. DISCONNECT BUS 509859 g.32. DISCONNECT BUS 509890 g.33. DISCONNECT BUS 511854 g.34. DISCONNECT BUS 511858 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-87-P5-SWS | Single phase fault with stuck relay near SWS (511477) 138 kV Bus a. APPLY FAULT AT SWS 138.0 kv BUS 511477 IMPEDANCE 0.48 4.59 OHM b. RUN FOR 23.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 b.1 OPEN LINE FROM BUS 511477 TO BUS 520814 CKT 1 c. RUN FOR 1.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 c.1 OPEN LINE FROM BUS 511477 TO BUS 511483 CKT 1 d. RUN FOR 3.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 d.1 OPEN LINE FROM BUS 511502 TO BUS 511449 CKT 1 d.2 OPEN LINE FROM BUS 511445 TO BUS 511463 CKT 1 d.3 OPEN LINE FROM BUS 511423 TO BUS 511467 CKT 1 e. RUN FOR 4.0 CYCLES PRINT 0 PLOT 3 CRTPLT 0 e.1 OPEN LINE FROM BUS 511477 TO BUS 521089 CKT 1 f. Clear fault after 489.0 cycles and trip faulted elements f.1 OPEN LINE FROM BUS 511486 TO BUS 511467 CKT 1 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-86-P5-Oneta | Single phase fault with stuck relay near Oneta (509807) 345 kV Bus a. Apply Fault at the Oneta (509807) 345 kV Bus b. Run fault for 26 cycles and trip faulted elements b.1. LINE FROM BUS 509807 TO BUS 509836 CKT 1 b.2. LINE FROM BUS 509807 TO BUS 509836 CKT 2 b.3. INE FROM BUS 509807 TO BUS 509782 CKT 1 c. Run fault for 18 cycles and trip faulted elements c.1. LINE FROM BUS 509807 TO BUS 509745 CKT 1 d. Run fault for 1 cycles and trip faulted elements d.1. LINE FROM BUS 509807 TO BUS 510406 CKT 1 e. Clear fault after 35 cycles and trip faulted elements e.1. LINE FROM BUS 509806 TO BUS 509891 CKT 1 e.2. LINE FROM BUS 509806 TO BUS 509869 CKT 1 e.3. LINE FROM BUS 509806 TO BUS 509769 CKT 1 e.4. LINE FROM BUS 509806 TO BUS 509786 CKT 1 e.5. LINE FROM BUS 509806 TO BUS 509768 CKT 1 e.6. DROP GENERATOR 1 BUS 511938 e.7. DROP GENERATOR 1 BUS 511939 e.8. DROP GENERATOR 1 BUS 511940 e.9. DROP GENERATOR 1 BUS 511941 e.10. DROP GENERATOR 1 BUS 511942 e.11. DROP GENERATOR 1 BUS 511943 e.12. DROP LOAD 1 BUS 509806 e.13. DROP LOAD S1 BUS 511940 e.14. DROP LOAD S1 BUS 511943 e.15. DISCONNECT BUS 509806 e.16. DISCONNECT BUS 509807 e.17. DISCONNECT BUS 509836 e.18. DISCONNECT BUS 509868 e.19. DISCONNECT BUS 509874 e.20. DISCONNECT BUS 509881 e.21. DISCONNECT BUS 511938 e.22. DISCONNECT BUS 511939 e.23. DISCONNECT BUS 511940 e.24. DISCONNECT BUS 511941 e.25. DISCONNECT BUS 511942 e.26. DISCONNECT BUS 511943 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-85-P5-LES | Single phase fault with stuck relay near LES (511467) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 27 cycles and trip faulted elements b.1. LINE FROM BUS 511437 TO BUS 511494 CKT 1 b.2. LINE FROM BUS 511512 TO BUS 511439 CKT 1 b.3. LINE FROM BUS 511477 TO BUS 511563 CKT 1 c. Run fault for 12 cycles and trip faulted elements c.1. LINE FROM BUS 529304 TO BUS 511494 CKT 1 d. Run fault for 15 cycles and trip faulted elements d.1. DISCONNECT BUS 511415 e. Run fault for 1 cycles and trip faulted elements e.1. DISCONNECT BUS 511416 f. Run fault for 2 cycles and trip faulted elements f.1. LINE FROM BUS 511474 TO BUS 511467 CKT 1 g. Run fault for 6 cycles and trip faulted elements g.1. DISCONNECT BUS 511411 h. Run fault for 2 cycles and trip faulted elements h.1. LINE FROM BUS 511437 TO BUS 511467 CKT 1 i. Run fault for 7 cycles and trip faulted elements i.1. DISCONNECT BUS 511414 j. Run fault for 24 cycles and trip faulted elements j.1. INE FROM BUS 511467 TO BUS 511486 CKT 1 k. Clear fault after 15 cycles and trip faulted elements k.1. LINE FROM BUS 511477 TO BUS 511421 CKT 1 k.2. DROP LOAD 1 BUS 511422 k.3. DROP LOAD 1 BUS 511431 k.4. DROP LOAD 1 BUS 511467 k.5. DISCONNECT BUS 511422 k.6. DISCONNECT BUS 511423 k.7. DISCONNECT BUS 511431 k.8. DISCONNECT BUS 511439 k.9. DISCONNECT BUS 511494 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-14-P5-FtHumbug | Single phase fault with stuck relay near FtHumbug (507731) 138 kV Bus a. Apply Fault at the FtHumbug (507731) 138 kV Bus b. Run fault for 21 cycles and trip faulted elements b.1. LINE FROM BUS 507731 TO BUS 507711 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 507731 TO BUS 507763 CKT 1 d. Run fault for 33 cycles and trip faulted elements d.1. LINE FROM BUS 507730 TO BUS 507716 CKT 1 e. Run fault for 1 cycles and trip faulted elements e.1. LINE FROM BUS 507735 TO BUS 507755 CKT 1 f. Clear fault after 2 cycles and trip faulted elements f.1. LINE FROM BUS 507722 TO BUS 507717 CKT 1 f.2. DROP LOAD 1 BUS 507722 f.3. DROP LOAD 1 BUS 507730 f.4. DROP LOAD 1 BUS 507735 f.5. DROP LOAD 1 BUS 507746 f.6. DISCONNECT BUS 507722 f.7. DISCONNECT BUS 507730 f.8. DISCONNECT BUS 507731 f.9. DISCONNECT BUS 507735 f.10. DISCONNECT BUS 507746 f.11. DISCONNECT BUS 507753 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-13-P5-SugarHill | Single phase fault with stuck relay near SugarHill (508080) 138 kV Bus a. Apply Fault at the SugarHill (508080) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508080 TO BUS 507454 CKT 1 c. Run fault for 3 cycles and trip faulted elements c.1. LINE FROM BUS 508082 TO BUS 508085 CKT 1 d. Run fault for 7 cycles and trip faulted elements d.1. LINE FROM BUS 508080 TO BUS 508071 CKT 1 e. Run fault for 55 cycles and trip faulted elements e.1. LINE FROM BUS 508073 TO BUS 508053 CKT 1 f. Run fault for 18 cycles and trip faulted elements f.1. LINE FROM BUS 508081 TO BUS 508084 CKT 1 g. Clear fault after 56 cycles and trip faulted elements f.1. LINE FROM BUS 508051 TO BUS 507429 CKT 1 f.2. DROP LOAD A1 BUS 504109 f.3. DROP LOAD 1 BUS 508051 f.4. DROP LOAD 1 BUS 508073 f.5. DROP LOAD 1 BUS 508076 f.6. DROP LOAD 1 BUS 508080 f.7. DROP LOAD 1 BUS 508094 f.8. DISCONNECT BUS 504109 f.9. DISCONNECT BUS 508051 f.10. DISCONNECT BUS 508066 f.11. DISCONNECT BUS 508073 f.12. DISCONNECT BUS 508076 f.13. DISCONNECT BUS 508079 f.14. DISCONNECT BUS 508080 f.15. DISCONNECT BUS 508081 f.16. DISCONNECT BUS 508082 f.17. DISCONNECT BUS 508094 f.18 DISCONNECT BUS 508103 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | FAULT__AEPW-2022-11-P5-Lieberman | Single phase fault with stuck relay near Lieberman (508806) 138 kV Bus a. Apply Fault at the Lieberman (508806) 138 kV Bus b. Run fault for 23 cycles and trip faulted elements b.1. LINE FROM BUS 508806 TO BUS 507711 CKT 1 c. Run fault for 4 cycles and trip faulted elements c.1. LINE FROM BUS 508833 TO BUS 508835 CKT 1 c.2. LINE FROM BUS 507772 TO BUS 507751 CKT 1 d. Run fault for 3 cycles and trip faulted elements d.1. LINE FROM BUS 508806 TO BUS 508833 CKT 1 e. Run fault for 4 cycles and trip faulted elements e.1. LINE FROM BUS 508806 TO BUS 508808 CKT 1 f. Run fault for 26 cycles and trip faulted elements f.1. LINE FROM BUS 508812 TO BUS 508815 CKT 1 g. Clear fault after 67 cycles and trip faulted elements f.1. LINE FROM BUS 508805 TO BUS 508801 CKT 1 f.2. DROP GENERATOR 1 BUS 509401 f.3. DROP GENERATOR 1 BUS 509402 f.4. DROP LOAD 1 BUS 508805 f.5. DROP LOAD 1 BUS 508812 f.6. DROP LOAD 1 BUS 508833 f.7. DROP LOAD S1 BUS 509401 f.8. DROP LOAD S1 BUS 509402 f.9. DISCONNECT BUS 508805 f.10. DISCONNECT BUS 508806 f.11. DISCONNECT BUS 508812 f.12. DISCONNECT BUS 508820 f.13. DISCONNECT BUS 508821 f.14. DISCONNECT BUS 508822 f.15. DISCONNECT BUS 508833 f.16. DISCONNECT BUS 509401 f.17. DISCONNECT BUS 509402 | P5 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25S | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2020-001 CF | 25W | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_PHANTOM_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO PHANTOM 765.0 KV 528014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_PHANTOM_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO PHANTOM 765.0 KV 528014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_POTTERCO_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO POTTERCO 765.0 KV 523966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_POTTERCO_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO POTTERCO 765.0 KV 523966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse G20-067: 0.32023 G20-065: 0.50148 G20-060: 0.24854 | Multi - Border - Woodward 345 kV Tap Potter County 345/230 kV Transformer Ckt 2
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_POTTER_CO | 3 Phase fault on BECKHAM7 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 345.0 KV 516059 TO POTTERCO 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_POTTER_CO | 3 Phase fault on BECKHAM7 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 345.0 KV 516059 TO POTTERCO 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_9_527669 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS9 527669 TO CROSSROADS7 527656 TO CROSSROADS TR1 527668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_9_527669 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS9 527669 TO CROSSROADS7 527656 TO CROSSROADS TR1 527668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Collapse G20-067: 0.21415 G20-065: 0.16337 G20-060: 0.21541 | Multi - Border - Woodward 345 kV Tap
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Collapse G20-067: 0.21415 G20-065: 0.16337 G20-060: 0.21541 | Multi - Border - Woodward 345 kV Tap
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Collapse G20-067: 0.21415 G20-065: 0.16337 G20-060: 0.21541 | Multi - Border - Woodward 345 kV Tap
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage Collapse G20-067: 0.21415 G20-065: 0.16337 G20-060: 0.21541 | Multi - Border - Woodward 345 kV Tap
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM_9_528014 | 3 Phase fault PHANTOM 9 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9 (528014) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM9 528014 TO PHANTOM7 528015 TO PHANTOM TR4 528001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM_9_528014 | 3 Phase fault PHANTOM 9 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9 (528014) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM9 528014 TO PHANTOM7 528015 TO PHANTOM TR4 528001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__BECKHAM7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__BECKHAM7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__TOLK_______7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__TOLK_______7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_POTTERCO_9_523966 | 3 Phase fault POTTERCO 9 (523966) 765 kV Bus a. Apply fault at the POTTERCO 9 (523966) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTERCO9 523966 TO POTTERCO7 523961 TO POTTERCO TR3 523964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_POTTERCO_9_523966 | 3 Phase fault POTTERCO 9 (523966) 765 kV Bus a. Apply fault at the POTTERCO 9 (523966) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTERCO9 523966 TO POTTERCO7 523961 TO POTTERCO TR3 523964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | Yes | Yes | Yes | Yes | No | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__AMOCO_TP___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-CLAUENE 3 115.0 KV 526491 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 b.2. LG-LEVELAND3 115.0 KV 526484 TO LG-CLAUENE 3 115.0 KV 526491 CKT 1 b.3. LOAD 1 526491 b.4. AMOCO_TP 3 115.0 KV 526445 TO LG-LEVELAND3 115.0 KV 526484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__FLATLAND___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__G20_074_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345 kV for 6 cycles with stuck breaker at TERRYRD7 345 kV. Clear Fault after 10 cycles and trip: TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK6_230kV_525531 | Apply single-phase fault on: TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1, near TOLK 6 230 kV for 7 cycles with stuck breaker at TOLK 6 230 kV. Clear Fault after 10 cycles and trip: PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TOLK7_345kV_525549 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1, near TOLK 7 345 kV for 6 cycles with stuck breaker at TOLK 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TREASILD7__G20_075_TAP | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_091 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GEN_2016_095 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TREASILD7__GRACMNT7 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___2__LH_WIL&ELN_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO LH-WIL&ELN+2 69.0 KV 525853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___2__SP_NEWDEAL_2 | 3 Phase fault on TUCO_INT 2 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 2 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 69.0 KV 525826 TO SP-NEWDEAL 2 69.0 KV 525885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__CARLISLE___3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 b.2. LOAD 1 526076 b.3. STANTON_W 3 115.0 KV 526076 TO INDIANA 3 115.0 KV 526146 CKT 1 b.4. LOAD 1 526146 b.5. LOAD 2 526146 b.6. SP-ERSKINE 3 115.0 KV 526109 TO INDIANA 3 115.0 KV 526146 CKT 1 b.7. LOAD 1 526146 b.8. LOAD 2 526146 b.9. SP-ERSKINE 3 115.0 KV 526109 TO CARLISLE 3 115.0 KV 526160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17_151_TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G17_151_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17_151_TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT___7__G20_067_TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT6_230kV_525830 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near TUCO_INT 6 230 kV for 7 cycles with stuck breaker at TUCO_INT 6 230 kV. Clear Fault after 10 cycles and trip: SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO BORDER7 345.0 KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TUCO_INT7_345kV_525832 | Apply single-phase fault on: TUCO_INT 7 345.0 KV 525832 TO G20-067-TAP 345.0 KV 764945 CKT 1, near TUCO_INT 7 345 kV for 6 cycles with stuck breaker at TUCO_INT 7 345 kV. Clear Fault after 10 cycles and trip: TUCO_INT 7 345.0 KV 525832 TO BORDER7 345.0 KV 515458 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_TULIA_TP___3__KRESS_INT__3 | 3 Phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 115.0 KV 525179 TO KRESS_INT 3 115.0 KV 525192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFCRK4__CHEEKTP4 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__3__SP_WOLF_TP_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUMA_INT 3 115.0 KV 526475 TO WOLFFORTH 3 115.0 KV 526524 CKT 1 b.2. YUMA_INT 3 115.0 KV 526475 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__3__TERRY_CNTY_3 | 3 Phase fault on WOLFFORTH 3 (526524) 115 kV Bus a. Apply fault at the WOLFFORTH 3 (526524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 3 115.0 KV 526524 TO TERRY_CNTY 3 115.0 KV 526736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WOLFFORTH__6__526524_0 | 3 Phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6( 526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 526525 TO WOLFFORTH 3 526524 TO WOLFRTH_TR11 526522 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4( 515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BECKHAM7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__BOBCAT_7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16_003_TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16_003_TAP 345.0 KV 560071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__GEN_2019_012 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_XTO_MAHONEY6__GEN_2017_239 | 3 Phase fault on XTO_MAHONEY6 (527011) 230 kV Bus a. Apply fault at the XTO_MAHONEY6 (527011) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_MAHONEY6 230.0 KV 527011 TO GEN-2017-239 230.0 KV 761355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__ARCO_TP____3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO ARCO_TP 3 115.0 KV 527041 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__SEAGRAVES__3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 115.0 KV 526934 TO LG-PLSHILL 3 115.0 KV 527194 CKT 1 b.2. LOAD 1 527194 b.3. LG-PLSHILL 3 115.0 KV 527194 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____3__TERRY_CNTY_3 | 3 Phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 b.2. TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_____6__SUNDOWN____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 b.2. SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_059_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__G20_067_TAP | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345__GEN_2019_011 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO GEN-2019-011 345.0 KV 763516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM_345kV_526936 | Apply single-phase fault on: YOAKUM_345 345.0 KV 526936 TO G20-067-TAP 345.0 KV 764945 CKT 1, near YOAKUM_345 345 kV for 6 cycles with stuck breaker at YOAKUM_345 345 kV. Clear Fault after 10 cycles and trip: YOAKUM_345 345.0 KV 526936 TO G20-059-TAP 345.0 KV 764866 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM3_115kV_526934 | Apply single-phase fault on: PRENTICE 3 115.0 KV 526792 TO YOAKUM 3 115.0 KV 526934 CKT 1 TERRY_CNTY 3 115.0 KV 526736 TO PRENTICE 3 115.0 KV 526792 CKT 1, near YOAKUM 3 115 kV for 7 cycles with stuck breaker at YOAKUM 3 115 kV. Clear Fault after 10 cycles and trip: PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near YOAKUM 6 230 kV for 7 cycles with stuck breaker at YOAKUM 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25S | Transfer | GROUP_05_FAULT_ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 CF | 25W | Transfer | GROUP_05_FAULT_ZIA________3__DCP_ZIA_TP_3 | 3 Phase fault on ZIA 3 (528420) 115 kV Bus a. Apply fault at the ZIA 3 (528420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_112GORE4__LAIRGST4 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_PHANTOM_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO PHANTOM 765.0 KV 528014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_PHANTOM_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO PHANTOM 765.0 KV 528014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_POTTERCO_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO POTTERCO 765.0 KV 523966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_765_CROSSROADS_9_POTTERCO_9 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS 765.0 KV 527669 TO POTTERCO 765.0 KV 523966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ACCO_______2__CLUTTER____2 | 3 Phase fault on ACCO 2 (526249) 69 kV Bus a. Apply fault at the ACCO 2 (526249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACCO 2 69.0 KV 526249 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__LP_WHEELOCK3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LP-WHEELOCK3 115.0 KV 526236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__LUBBCK_STH_3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO LUBBCK_STH 3 115.0 KV 526268 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ALLEN______3__SP_QUAKER__3 | 3 Phase fault on ALLEN 3 (526213) 115 kV Bus a. Apply fault at the ALLEN 3 (526213) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 3 115.0 KV 526213 TO SP-QUAKER 3 115.0 KV 526243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__CORTEZ_____3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLRED_SUB 3 115.0 KV 527024 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 b.2. APACHE_ROB 3 115.0 KV 527022 TO ALLRED_SUB 3 115.0 KV 527024 CKT 1 b.3. LOAD 1 527024 b.4. CORTEZ 3 115.0 KV 527021 TO APACHE_ROB 3 115.0 KV 527022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ALRDCRTZ_TP3__SHELLC3_TP_3 | 3 Phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALRDCRTZ_TP3 115.0 KV 527030 TO XTO_CORNEL+3 115.0 KV 527033 CKT 1 b.2. LOAD 1 527033 b.3. XTO_CORNEL+3 115.0 KV 527033 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__524414_0 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6( 524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 524415 TO AMA_SOUTH 3 524414 TO AMA_SO_TR1 1 524410 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_AMERADA____3__SEMINOLE___3 | 3 Phase fault on AMERADA 3 (527242) 115 kV Bus a. Apply fault at the AMERADA 3 (527242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMERADA 3 115.0 KV 527242 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_AMOCO_TP___3__AMOCO_CRYO_3 | 3 Phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_TP 3 115.0 KV 526445 TO AMOCO_CRYO 3 115.0 KV 526452 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANADARK4__GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANADARK4__POCASET4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 345 kV Bus a. Apply fault at the ANDREWS 6( 528604) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-065: PTDF = 0.05538 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARCO_TP____3__ARCO_TP____3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNETT 3 115.0 KV 527018 TO ARCO_TP 3 115.0 KV 527041 CKT 1 b.2. BENNETT 3 115.0 KV 527018 TO ODC_TP 3 115.0 KV 527051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARCO_TP____3__OXY_WILRD1_3 | 3 Phase fault on ARCO_TP 3 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO_TP 3 115.0 KV 527041 TO OXY_WILRD1 3 115.0 KV 527047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARTESIA____3__EAGLE_CREEK3 | 3 Phase fault on ARTESIA 3 (527707) 115 kV Bus a. Apply fault at the ARTESIA 3 (527707) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTESIA 3 115.0 KV 527707 TO EAGLE_CREEK3 115.0 KV 527711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARTSA_CC_TP3__ATOKA______3 | 3 Phase fault on ARTSA_CC_TP3 (527777) 115 kV Bus a. Apply fault at the ARTSA_CC_TP3 (527777) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTSA_CC_TP3 115.0 KV 527777 TO ATOKA 3 115.0 KV 527786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ARTVLTP4__LWS_NTP4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 b.2. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ATOKA______3__527785_0 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3( 527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 527786 TO ATOKA 2 527785 TO ATOKA_TR1 1 527784 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ATOKA______3__CV_IRISHHL_3 | 3 Phase fault on ATOKA 3 (527786) 115 kV Bus a. Apply fault at the ATOKA 3 (527786) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA 3 115.0 KV 527786 TO CV-IRISHHL+3 115.0 KV 528116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_345kV_516059 | Apply single-phase fault on: BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1, near BECKHAM7 345 kV for 6 cycles with stuck breaker at BECKHAM7 345 kV. Clear Fault after 10 cycles and trip: WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BECKHAM7_POTTER_CO | 3 Phase fault on BECKHAM7 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 345.0 KV 516059 TO POTTERCO 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BLANCO_____3__CROSBY_____3 | 3 Phase fault on BLANCO 3 (525803) 115 kV Bus a. Apply fault at the BLANCO 3 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 115.0 KV 525803 TO CROSBY 3 115.0 KV 525926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BLUECLDCOL_6__BLUECLDPOI_6 | 3 Phase fault on BLUECLDCOL 6 (525584) 230 kV Bus a. Apply fault at the BLUECLDCOL 6 (525584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDCOL 6 230.0 KV 525584 TO BLUECLDPOI 6 230.0 KV 525585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BLUECLDPOI_6__NEEDMORE___6 | 3 Phase fault on BLUECLDPOI 6 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 230.0 KV 525585 TO NEEDMORE 6 230.0 KV 525586 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__BECKHAM7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.18912 GEN-2020-065: PTDF = 0.1237 GEN-2020-067: PTDF = 0.18737 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BORDER_____7__TUCO_INT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.18912 GEN-2020-065: PTDF = 0.1237 GEN-2020-067: PTDF = 0.18737 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BRU_SUB____6__OXYBRU_____6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO OXYBRU 6 230.0 KV 527010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BRU_SUB____6__XTO_MAHONEY6 | 3 Phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BRU_SUB6_230kV_527009 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1, near BRU_SUB 6 230 kV for 7 cycles with stuck breaker at BRU_SUB 6 230 kV. Clear Fault after 10 cycles and trip: BRU_SUB 6 230.0 KV 527009 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CALLAHAN___3__FLOYD_CNTY_3 | 3 Phase fault on CALLAHAN 3 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 115.0 KV 525763 TO FLOYD_CNTY 3 115.0 KV 525780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CANNON_TP__3__CANNONAFB__3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANNON_TP 3 115.0 KV 524790 TO CANNONAFB 3 115.0 KV 524794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CANNON_TP__3__FE_CLVS_INT3 | 3 Phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_CLOVIS 3 115.0 KV 524784 TO CANNON_TP 3 115.0 KV 524790 CKT 1 b.2. W_CLOVIS 3 115.0 KV 524784 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CAPITAN____3__ROSWLL_INT_3 | 3 Phase fault on CAPITAN 3 (527541) 115 kV Bus a. Apply fault at the CAPITAN 3 (527541) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAPITAN 3 115.0 KV 527541 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARDINAL___3__LIVSTNRIDGE3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.3. LOAD 1 527955 b.4. LOAD 1* 527955 b.5. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARDINAL___3__S_JAL______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 b.2. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__526159_0 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3( 526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 526160 TO CARLISLE 2 526159 TO CRLSLE_TR2 1 526158 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__LP_DOUD_TP_3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO LP-DOUD_TP 3 115.0 KV 526162 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___3__MURPHY_____3 | 3 Phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 115.0 KV 526160 TO MURPHY 3 115.0 KV 526192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARLSBAD___3__PECOS______3 | 3 Phase fault on CARLSBAD 3 (528160) 115 kV Bus a. Apply fault at the CARLSBAD 3 (528160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLSBAD 3 115.0 KV 528160 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__BETHEL_COL13 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO BETHEL_COL13 115.0 KV 524757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__NEWHART____3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 115.0 KV 524746 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CASTRO_CNTY3__TIERABLANCA3 | 3 Phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#21 3 115.0 KV 524734 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 b.2. TIERABLANCA3 115.0 KV 524630 TO DS-#21 3 115.0 KV 524734 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAN_TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__PRICE_TAP__3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO PRICE_TAP 3 115.0 KV 527509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__SAMSON_____3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO SAMSON 3 115.0 KV 527546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY3__URTON______3 | 3 Phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY3 115.0 KV 527482 TO URTON 3 115.0 KV 527501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHEEKTP4__CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHINA_DRAW7_345kV_528223 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near CHINA_DRAW 7 345 kV for 6 cycles with stuck breaker at CHINA_DRAW 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__BECKHAM7 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CHVS_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on CHVS_SLRCOL3 (527470) 115 kV Bus a. Apply fault at the CHVS_SLRCOL3 (527470) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHVS_SLRCOL3 115.0 KV 527470 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COCHRAN____3__526360_0 | 3 Phase fault on COCHRAN 3 (526361) 115 kV Bus a. Apply fault at the COCHRAN 3( 526361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COCHRAN 3 526361 TO COCHRAN 2 526360 TO COCHRAN_TR21 526359 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMANC_2__L_DISTP2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L-DISTP2 69.0 KV 511524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CORNVIL2__511449_0 | 3 Phase fault on CORNVIL2 (511450) 69 kV Bus a. Apply fault at the CORNVIL2( 511450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORNVIL2 511450 TO CORNVIL4 511449 TO CORNV2-1 511418 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COX________3__CALLAHAN___3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO CALLAHAN 3 115.0 KV 525763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_COX________3__HALE_CNTY__3 | 3 Phase fault on COX 3 (525326) 115 kV Bus a. Apply fault at the COX 3 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 115.0 KV 525326 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSBY_____2__LH_CROSBY__2 | 3 Phase fault on CROSBY 2 (525925) 69 kV Bus a. Apply fault at the CROSBY 2 (525925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 2 69.0 KV 525925 TO LH-CROSBY +2 69.0 KV 525936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSBY_____3__525925_0 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3( 525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 525926 TO CROSBY 2 525925 TO CROSBY_TR2 1 525924 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSBY_____3__LUBBCK_EST_3 | 3 Phase fault on CROSBY 3 (525926) 115 kV Bus a. Apply fault at the CROSBY 3 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__HOBBS_INT__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_7__SAGA_SDCOL_7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 b.2. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SCOL 7 345.0 KV 527610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS_9_527669 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS9 527669 TO CROSSROADS7 527656 TO CROSSROADS TR1 527668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS_9_527669 | 3 Phase fault CROSSROADS 9 (527669) 765 kV Bus a. Apply fault at the CROSSROADS 9 (527669) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSSROADS9 527669 TO CROSSROADS7 527656 TO CROSSROADS TR1 527668 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CROSSROADS7_345kV_527656 | Apply single-phase fault on: CROSSROADS 7 345.0 KV 527656 TO HOBBS_INT 7 345.0 KV 527896 CKT 1, near CROSSROADS 7 345 kV for 6 cycles with stuck breaker at CROSSROADS 7 345 kV. Clear Fault after 10 cycles and trip: TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM3_115kV_527864 | Apply single-phase fault on: CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 10 cycles and trip: CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAM6_230kV_527867 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near CUNNIGHM_S 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_S 6 230 kV. Clear Fault after 10 cycles and trip: CUNNIGHM_N 6 230.0 KV 527865 TO CUNNIGHM_S 6 230.0 KV 527867 CKT *1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUNNINHAMN6_230kV_527865 | Apply single-phase fault on: CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1, near CUNNIGHM_N 6 230 kV for 7 cycles with stuck breaker at CUNNIGHM_N 6 230 kV. Clear Fault after 10 cycles and trip: EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CURRY______3__524821_0 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3( 524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 524822 TO CURRY 2 524821 TO CURRY_TR2 1 524820 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CURRY______3__BAILEYCO___3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CURRY______3__PLSNT_HILL_3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E_CLOVIS 3 115.0 KV 524773 TO CURRY 3 115.0 KV 524822 CKT 1 b.2. LOAD 1 524822 b.3. PLSNT_HILL 3 115.0 KV 524768 TO E_CLOVIS 3 115.0 KV 524773 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CURRY______3__ROOSEVELT__3 | 3 Phase fault on CURRY 3 (524822) 115 kV Bus a. Apply fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURRY 3 115.0 KV 524822 TO ROOSEVELT 3 115.0 KV 524908 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CV_8_MILE__3__CV_TURKYTRK3 | 3 Phase fault on CV-8_MILE 3 (527809) 115 kV Bus a. Apply fault at the CV-8_MILE 3 (527809) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-8_MILE 3 115.0 KV 527809 TO CV-TURKYTRK3 115.0 KV 527822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_CV_AZMESA__3__PECOS______3 | 3 Phase fault on CV-AZMESA 3 (528070) 115 kV Bus a. Apply fault at the CV-AZMESA 3 (528070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CV-AZMESA 3 115.0 KV 528070 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DEAFSMITH__6__G17_146_TAP | 3 Phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 230.0 KV 524623 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DENVER_S___3__527125_0 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3( 527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 527136 TO DENVER_CTY 2 527125 TO DNVER_S_TR21 527123 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DENVER_S___3__MUSTANG____3 | 3 Phase fault on DENVER_S 3 (527136) 115 kV Bus a. Apply fault at the DENVER_S 3 (527136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_S 3 115.0 KV 527136 TO MUSTANG 3 115.0 KV 527146 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DFSMTH_EST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_EST 3 (524619) 115 kV Bus a. Apply fault at the DFSMTH_EST 3 (524619) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_EST 3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DFSMTH_WST_3__TIERABLANCA3 | 3 Phase fault on DFSMTH_WST 3 (524622) 115 kV Bus a. Apply fault at the DFSMTH_WST 3 (524622) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DFSMTH_WST 3 115.0 KV 524622 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DIAMONDBACK3__FLATLAND___3 | 3 Phase fault on DIAMONDBACK3 (527212) 115 kV Bus a. Apply fault at the DIAMONDBACK3 (527212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIAMONDBACK3 115.0 KV 527212 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS__15&_19_2__CASTRO_CNTY2 | 3 Phase fault on DS-#15&#19+2 (524721) 69 kV Bus a. Apply fault at the DS-#15&#19+2 (524721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#15&#19+2 69.0 KV 524721 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS__20_____3__CURRY______3 | 3 Phase fault on DS-#20 3 (524669) 115 kV Bus a. Apply fault at the DS-#20 3 (524669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#20 3 115.0 KV 524669 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS__22_____3__CASTRO_CNTY3 | 3 Phase fault on DS-#22 3 (524694) 115 kV Bus a. Apply fault at the DS-#22 3 (524694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#22 3 115.0 KV 524694 TO CASTRO_CNTY3 115.0 KV 524746 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS__25_____3__TIERABLANCA3 | 3 Phase fault on DS-#25+ 3 (524575) 115 kV Bus a. Apply fault at the DS-#25+ 3 (524575) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#25+ 3 115.0 KV 524575 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS__3______2__CASTRO_CNTY2 | 3 Phase fault on DS-#3 2 (524688) 69 kV Bus a. Apply fault at the DS-#3 2 (524688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-#3 2 69.0 KV 524688 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DS_CASTRO__2__CASTRO_CNTY2 | 3 Phase fault on DS-CASTRO 2 (524728) 69 kV Bus a. Apply fault at the DS-CASTRO 2 (524728) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DS-CASTRO 2 69.0 KV 524728 TO CASTRO_CNTY2 69.0 KV 524745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_DUNCAN_4__OMDUNCN4 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__527710_0 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3( 527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 527711 TO EAGLE_CREEK2 527710 TO EGCREEK_TR11 527709 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__7_RIVERS___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO 7-RIVERS 3 115.0 KV 528094 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__ARTSA_CC_TP3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO ARTSA_CC_TP3 115.0 KV 527777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_2TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_2TP 3 115.0 KV 527715 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EAGLE_CREEK3__NAVAJO_5TP_3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO NAVAJO_5TP 3 115.0 KV 527736 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-065: PTDF = 0.05053 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_CNTY7_345kV_527802 | Apply single-phase fault on: EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1, near EDDY_CNTY 7 345 kV for 6 cycles with stuck breaker at EDDY_CNTY 7 345 kV. Clear Fault after 10 cycles and trip: CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_NTH___3__ROSWLL_INT_3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 b.2. ROSWLL_INT 3 115.0 KV 527564 TO TWEEDY 3 115.0 KV 527597 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_STH___3__ATOKA______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 b.2. LOAD 1 527821 b.3. ATOKA 3 115.0 KV 527786 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__CORNVIL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CYRIL--2 69.0 KV 511451 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. CORNVIL2 69.0 KV 511450 TO CYRIL--2 69.0 KV 511451 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ELGINJT2__FT_SILL2 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2 (511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PO.HILL2 69.0 KV 511473 TO ELGINJT2 69.0 KV 511487 CKT 1 b.2. LOAD 1 511487 b.3. FT.SILL2 69.0 KV 511461 TO PO.HILL2 69.0 KV 511473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ELGINJT4__S_W_S__4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 b.2. LOAD 1 511563 b.3. LOAD 2 511563 b.4. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FE_CLVS_INT3__A12_02&13_05 | 3 Phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FE-CLVS_INT3 115.0 KV 524808 TO A12-02&13-05 115.0 KV 583280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLATLAND___3__GEN_2017_187 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO GEN-2017-187 115.0 KV 761796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLATLAND___3__SULPHUR____3 | 3 Phase fault on FLATLAND 3 (527257) 115 kV Bus a. Apply fault at the FLATLAND 3 (527257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATLAND 3 115.0 KV 527257 TO SULPHUR 3 115.0 KV 527262 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-187 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2017-187 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__525779_0 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3( 525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 525780 TO FLOYD_CNTY 2 525779 TO FLOYD_TR2 1 525778 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__BLANCO_____3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G20_067_TAP__GEN_2020_068 | 3 Phase fault on G20-067-TAP (764945) 345 kV Bus a. Apply fault at the G20-067-TAP (764945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-067-TAP 345.0 KV 764945 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G20_068_SS1__GEN_2020_068 | 3 Phase fault on G20-068-SS1 (764948) 345 kV Bus a. Apply fault at the G20-068-SS1 (764948) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS1 345.0 KV 764948 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G20_068_SS2__GEN_2020_068 | 3 Phase fault on G20-068-SS2 (764949) 345 kV Bus a. Apply fault at the G20-068-SS2 (764949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-068-SS2 345.0 KV 764949 TO GEN-2020-068 345.0 KV 764950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_G20_075_TAP__GEN_2020_087 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GAINES_PLNT7__SIDEWINDER_7 | 3 Phase fault on GAINES_PLNT7 (527000) 345 kV Bus a. Apply fault at the GAINES_PLNT7 (527000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GAINES_PLNT7 345.0 KV 527000 TO SIDEWINDER 7 345.0 KV 527020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_009__G20_009_TAP | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__764845_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM1 764845 TO GSU_1_LV 10003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__764850_0 | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059( 764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 764840 TO G20-059-XFM2 764850 TO GSU_2_LV 20003 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_059__G20_059_TAP | 3 Phase fault on GEN-2020-059 (764840) 345 kV Bus a. Apply fault at the GEN-2020-059 (764840) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-059 345.0 KV 764840 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_067__G20_067_TAP | 3 Phase fault on GEN-2020-067 (764935) 345 kV Bus a. Apply fault at the GEN-2020-067 (764935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-067 345.0 KV 764935 TO G20-067-TAP 345.0 KV 764945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GEN_2020_074__G20_074_TAP | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__3__GRAHAM_____3 | 3 Phase fault on GRASSLAND 3 (526676) 115 kV Bus a. Apply fault at the GRASSLAND 3 (526676) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 3 115.0 KV 526676 TO GRAHAM 3 115.0 KV 526694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__526676_0 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6( 526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 526677 TO GRASSLAND 3 526676 TO GRASLND_TR11 526674 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_GRASSLAND__6__CIRRUS_WND_6 | 3 Phase fault on GRASSLAND 6 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 230.0 KV 526677 TO CIRRUS_WND 6 230.0 KV 526679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__525453_0 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3( 525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 525454 TO HALE_CNTY 2 525453 TO HALE_TR2 1 525452 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__PLANT_X____3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525931_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL11 525931 TO HALE_WD_TR11 525930 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525981_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL21 525981 TO HALE_WD_TR21 525980 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALE_WNDCL16__525990_0 | 3 Phase fault on HALE_WNDCL16 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16( 525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 525957 TO HALEWD_COL31 525990 TO HALE_WD_TR31 525989 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HALECENTER_2__TUCO_INT___2 | 3 Phase fault on HALECENTER 2 (525738) 69 kV Bus a. Apply fault at the HALECENTER 2 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 69.0 KV 525738 TO TUCO_INT 2 69.0 KV 525826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HART_INDUST3__LAMTON_____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO LAMTON 3 115.0 KV 525414 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HART_INDUST3__NEWHART____3 | 3 Phase fault on HART_INDUST3 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 115.0 KV 525124 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HEREFORD___3__TIERABLANCA3 | 3 Phase fault on HEREFORD 3 (524606) 115 kV Bus a. Apply fault at the HEREFORD 3 (524606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEREFORD 3 115.0 KV 524606 TO TIERABLANCA3 115.0 KV 524630 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-008 trips on voltage protection settings. LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for GEN-2020-008 and LANO GSU prevents trips. There are no stability constraints when these generators trip offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-008 trips on voltage protection settings. LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU and GEN-2020-008 prevents trips. There are no stability constraints when these generator trips offline or when the protection settings are disabled to prevent them from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.18109 GEN-2020-065: PTDF = 0.23043 GEN-2020-067: PTDF = 0.18896 LANO GSU trips on voltage protection settings. | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.08731 GEN-2020-065: PTDF = 0.19942 GEN-2020-067: PTDF = 0.2634 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.08731 GEN-2020-065: PTDF = 0.19942 GEN-2020-067: PTDF = 0.2634 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__G20_059_TAP | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO G20-059-TAP 345.0 KV 764866 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.08731 GEN-2020-065: PTDF = 0.19942 GEN-2020-067: PTDF = 0.2634 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-065: PTDF = 0.09402 GEN-2020-067: PTDF = 0.05426 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT__7__RDRUNNER___7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT3_115kV_527891 | Apply single-phase fault on: HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT6_230kV_527894 | Apply single-phase fault on: CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1, near HOBBS_INT 6 230 kV for 7 cycles with stuck breaker at HOBBS_INT 6 230 kV. Clear Fault after 10 cycles and trip: INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOBBS_INT7_345kV_527896 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near HOBBS_INT 7 345 kV for 6 cycles with stuck breaker at HOBBS_INT 7 345 kV. Clear Fault after 10 cycles and trip: SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOCKLEY____3__526019_0 | 3 Phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply fault at the HOCKLEY 3( 526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOCKLEY 3 526020 TO HOCKLEY 2 526019 TO HOCKLEY_TR21 526018 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HOCKLEY3_115kV_526020 | Apply single-phase fault on: LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1, near HOCKLEY 3 115 kV for 7 cycles with stuck breaker at HOCKLEY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__A16_008SUB | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO A16-008SUB 115.0 KV 588460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__ALRDCRTZ_TP3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__527027_0 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6( 527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 527028 TO INK_BASIN 3 527027 TO INKBASN_TR 1 527026 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_INK_BASIN3_115kV_527027 | Apply single-phase fault on: INK_BASIN 3 115.0 KV 527027 TO ALRDCRTZ_TP3 115.0 KV 527030 CKT 1, near INK_BASIN 3 115 kV for 7 cycles with stuck breaker at INK_BASIN 3 115 kV. Clear Fault after 10 cycles and trip: INK_BASIN 3 115.0 KV 527027 TO LEWAITS 3 115.0 KV 528325 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_IVORY______2__LUBBCK_STH_2 | 3 Phase fault on IVORY 2 (526205) 69 kV Bus a. Apply fault at the IVORY 2 (526205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY 2 69.0 KV 526205 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_IVORY_TP___2__LUBBCK_STH_2 | 3 Phase fault on IVORY_TP 2 (526256) 69 kV Bus a. Apply fault at the IVORY_TP 2 (526256) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IVORY_TP 2 69.0 KV 526256 TO LUBBCK_STH 2 69.0 KV 526267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_JONES6_115kV_526337 | Apply single-phase fault on: TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1, near JONES 6 230 kV for 7 cycles with stuck breaker at JONES 6 230 kV. Clear Fault after 10 cycles and trip: LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.05804 GEN-2020-065: PTDF = 0.12765 GEN-2020-067: PTDF = 0.0809 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-065: PTDF = 0.9242 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KIOWA7_345kV_527965 | Apply single-phase fault on: HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1, near KIOWA 7 345 kV for 6 cycles with stuck breaker at KIOWA 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KISER______3__COX________3 | 3 Phase fault on KISER 3 (525272) 115 kV Bus a. Apply fault at the KISER 3 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 115.0 KV 525272 TO COX 3 115.0 KV 525326 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__HALE_CNTY__3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__KRS_RURL_TP3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO KRS_RURL_TP3 115.0 KV 525226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__NEWHART____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO NEWHART 3 115.0 KV 525460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_KRESS_INT__3__SWISHER____3 | 3 Phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 115.0 KV 525192 TO SWISHER 3 115.0 KV 525212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__FT_SILL2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 b.2. LOAD 1 511469 b.3. FT.SILL2 69.0 KV 511461 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__2__LAW__WC2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 b.2. LOAD 1 511470 b.3. LGORE-S2 69.0 KV 511470 TO LAW WC2 69.0 KV 511503 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_009_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__G20_075_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_L_E_S__7__GEN_2018_115 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__SUDANRURAL_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 b.2. AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 b.3. LOAD 1 525613 b.4. LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 b.5. LOAD 1 525606 b.6. SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__2__W_ANTON_TP_2 | 3 Phase fault on LAMB_CNTY 2 (525635) 69 kV Bus a. Apply fault at the LAMB_CNTY 2 (525635) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 2 69.0 KV 525635 TO LC-LTTLFLD+2 69.0 KV 525650 CKT 1 b.2. LOAD 1 525650 b.3. LC-LTTLFLD+2 69.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__3__HOCKLEY____3 | 3 Phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__525636_0 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6( 525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 525637 TO LAMB_CNTY 3 525636 TO LAMB_TR3 1 525633 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY__6__GEN_2020_017 | 3 Phase fault on LAMB_CNTY 6 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 230.0 KV 525637 TO GEN-2020-017 230.0 KV 764825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY_69kV_525635 | Apply single-phase fault on: LAMB_CNTY 2 69.0 KV 525635 TO LC LTTLFLD 69.0 KV 525650 CKT 1 LC LTTLFLD 230.0 KV 525650 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1, near LAMB_CNTY 2 69 kV for 7 cycles with stuck breaker at LAMB_CNTY 2 69 kV. Clear Fault after 10 cycles and trip: W_LITTLFLD 2 69.0 KV 525613 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 AMHERST 2 69.0 KV 525606 TO W_LITTLFLD 2 69.0 KV 525613 CKT 1 LOAD 1 525613 LC-SANDHLL+2 69.0 KV 525599 TO AMHERST 2 69.0 KV 525606 CKT 1 LOAD 1 525606 SUDANRURAL 2 69.0 KV 525592 TO LC-SANDHLL+2 69.0 KV 525599 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMB_CNTY3_115kV_525636 | Apply single-phase fault on: PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1, near LAMB_CNTY 3 115 kV for 7 cycles with stuck breaker at LAMB_CNTY 3 115 kV. Clear Fault after 10 cycles and trip: LAMB_CNTY 3 115.0 KV 525636 TO HOCKLEY 3 115.0 KV 526020 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LAMTON_____3__HALE_CNTY__3 | 3 Phase fault on LAMTON 3 (525414) 115 kV Bus a. Apply fault at the LAMTON 3 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 115.0 KV 525414 TO HALE_CNTY 3 115.0 KV 525454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LC_BECK____2__SUDANRURAL_2 | 3 Phase fault on LC-BECK +2 (525045) 69 kV Bus a. Apply fault at the LC-BECK +2 (525045) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-BECK +2 69.0 KV 525045 TO SUDANRURAL 2 69.0 KV 525592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_PLNSINT_2__LE_PLNSGOAB2 | 3 Phase fault on LE-PLNSINT 2 (528626) 69 kV Bus a. Apply fault at the LE-PLNSINT 2 (528626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-PLNSINT 2 69.0 KV 528626 TO LE-PLNSGOAB2 69.0 KV 528709 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_FORT_SW_2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-FORT_SW 2 69.0 KV 528714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___2__LE_TP51____2 | 3 Phase fault on LE-WAITS 2 (528617) 69 kV Bus a. Apply fault at the LE-WAITS 2 (528617) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 2 69.0 KV 528617 TO LE-TP51 2 69.0 KV 528759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LEHMAN_TP__3__LEHMAN_____3 | 3 Phase fault on LEHMAN_TP 3 (526350) 115 kV Bus a. Apply fault at the LEHMAN_TP 3 (526350) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEHMAN_TP 3 115.0 KV 526350 TO LEHMAN 3 115.0 KV 526352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LES4_138kV_511467 | Apply single-phase fault on: L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 LOAD 1 511474 SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 10 cycles and trip: L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LES7_345kV_511468 | Apply single-phase fault on: L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 10 cycles and trip: L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LG_DOCWEBR_2__TERRY_CNTY_2 | 3 Phase fault on LG-DOCWEBR 2 (526506) 69 kV Bus a. Apply fault at the LG-DOCWEBR 2 (526506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-DOCWEBR 2 69.0 KV 526506 TO TERRY_CNTY 2 69.0 KV 526735 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LG_WELLMAN_2__SEAGRAVES__2 | 3 Phase fault on LG-WELLMAN 2 (526993) 69 kV Bus a. Apply fault at the LG-WELLMAN 2 (526993) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-WELLMAN 2 69.0 KV 526993 TO SEAGRAVES 2 69.0 KV 527201 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LG_YEAR4__112GORE4 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LOST_DRAW__3__COCHRAN____3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO COCHRAN 3 115.0 KV 526361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LOST_DRAW__3__LEHMAN_TP__3 | 3 Phase fault on LOST_DRAW 3 (526012) 115 kV Bus a. Apply fault at the LOST_DRAW 3 (526012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOST_DRAW 3 115.0 KV 526012 TO LEHMAN_TP 3 115.0 KV 526350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LP_DOUD_TP_3__SP_WOLF_TP_3 | 3 Phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LP-DOUD_TP 3 115.0 KV 526162 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LRNZ_MPT___3__BLANCO_____3 | 3 Phase fault on LRNZ_MPT 3 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 115.0 KV 525801 TO BLANCO 3 115.0 KV 525803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 764866 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764866 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 764945 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 560022 TO 525832 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 560022 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 560022 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__LAMB_CNTY__2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO LAMB_CNTY 2 69.0 KV 525635 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LTFLD_S&CTY2__W_ANTON_TP_2 | 3 Phase fault on LTFLD_S&CTY2 (525620) 69 kV Bus a. Apply fault at the LTFLD_S&CTY2 (525620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTFLD_S&CTY2 69.0 KV 525620 TO W_ANTON_TP 2 69.0 KV 525657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__CLUTTER____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO CLUTTER 2 69.0 KV 526310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SLATON_____2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 2 69.0 KV 526297 TO SLATON 2 69.0 KV 526562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_2__SW_6786_S__2 | 3 Phase fault on LUBBCK_EST 2 (526297) 69 kV Bus a. Apply fault at the LUBBCK_EST 2 (526297) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANTERS 2 69.0 KV 526284 TO LUBBCK_EST 2 69.0 KV 526297 CKT 1 b.2. SW_6786_S 2 69.0 KV 526087 TO PLANTERS 2 69.0 KV 526284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_3__526297_0 | 3 Phase fault on LUBBCK_EST 3 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3( 526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 526298 TO LUBBCK_EST 2 526297 TO LBB_EST TR31 526296 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__526298_0 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6( 526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 526299 TO LUBBCK_EST 3 526298 TO LBB_EST TR11 526294 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__GEN_2020_060 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO GEN-2020-060 230.0 KV 764875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__526267_0 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3( 526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 526268 TO LUBBCK_STH 2 526267 TO LBB_STH TR21 526266 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LUBBCK_EST_3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_3__LYNN_CNTY__3 | 3 Phase fault on LUBBCK_STH 3 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 115.0 KV 526268 TO WOODROW 3 115.0 KV 526602 CKT 1 b.2. LOAD 1 526602 b.3. WOODROW 3 115.0 KV 526602 TO LYNN_CNTY 3 115.0 KV 526656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__526268_0 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6( 526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 526269 TO LUBBCK_STH 3 526268 TO LBB_STH TR11 526265 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBCK_STH_6__WOLFFORTH__6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LUBBUCK_EST_115kV_526298 | Apply single-phase fault on: TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1, near LUBBCK_EST 3 115 kV for 7 cycles with stuck breaker at LUBBCK_EST 3 115 kV. Clear Fault after 10 cycles and trip: CROSBY 3 115.0 KV 525926 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LWS___N4__LWS_NTP4 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LWS_NTP4__112GORE4 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LWSTAP_4__112GORE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 b.2. LOAD 1 511512 b.3. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__526655_0 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3( 526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 526656 TO LYNN_CNTY 2 526655 TO LYNN_TR2 1 526654 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_LYNN_CNTY__3__GRASSLAND__3 | 3 Phase fault on LYNN_CNTY 3 (526656) 115 kV Bus a. Apply fault at the LYNN_CNTY 3 (526656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYNN_CNTY 3 115.0 KV 526656 TO GRASSLAND 3 115.0 KV 526676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on voltage protection settings. | Disabling voltage protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-004 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MAPCO______3__JOHNSON_DRW3 | 3 Phase fault on MAPCO 3 (527360) 115 kV Bus a. Apply fault at the MAPCO 3 (527360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__MILLEN_TPW_3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN 3 115.0 KV 528435 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 b.2. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN 3 115.0 KV 528435 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPE_3__TAYLOR_____3 | 3 Phase fault on MILLEN_TPE 3 (528436) 115 kV Bus a. Apply fault at the MILLEN_TPE 3 (528436) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MINCO__7__NORMHLL7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MULESHVALLY3__MULSHVLY_TP3 | 3 Phase fault on MULESHVALLY3 (525018) 115 kV Bus a. Apply fault at the MULESHVALLY3 (525018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULESHVALLY3 115.0 KV 525018 TO MULSHVLY_TP3 115.0 KV 525019 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__BAILEYCO___3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO BAILEYCO 3 115.0 KV 525028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MULSHVLY_TP3__PLANT_X____3 | 3 Phase fault on MULSHVLY_TP3 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 115.0 KV 525019 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____3__SEAGRAVES__3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEAGRAVES 3 115.0 KV 527202 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____3__SEMINOLE___3 | 3 Phase fault on MUSTANG 3 (527146) 115 kV Bus a. Apply fault at the MUSTANG 3 (527146) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 3 115.0 KV 527146 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__527146_0 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6( 527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 527149 TO MUSTANG 3 527146 TO MUSTANG_TR11 527143 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__SEMINOLE___6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG____6__XTO_MAHONEY6 | 3 Phase fault on MUSTANG 6 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 230.0 KV 526784 TO MUSTANG 6 230.0 KV 527149 CKT 1 b.2. AMOCOWASSON6 230.0 KV 526784 TO XTO_MAHONEY6 230.0 KV 527011 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_MUSTANG6_230kV_527149 | Apply single-phase fault on: YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1, near MUSTANG 6 230 kV for 7 cycles with stuck breaker at MUSTANG 6 230 kV. Clear Fault after 10 cycles and trip: MUSTANG 6 230.0 KV 527149 TO SEMINOLE 6 230.0 KV 527276 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_CANAL____3__PECOS______3 | 3 Phase fault on N_CANAL 3 (528137) 115 kV Bus a. Apply fault at the N_CANAL 3 (528137) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CANAL 3 115.0 KV 528137 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__FE_CLVS_INT3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO FE-CLVS_INT3 115.0 KV 524808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_CLOVIS_TP3__N_CLOVIS___3 | 3 Phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_CLOVIS_TP3 115.0 KV 524776 TO N_CLOVIS 3 115.0 KV 524777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_N_LOVING7_345kV_528185 | Apply single-phase fault on: N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1, near N_LOVING 7 345 kV for 6 cycles with stuck breaker at N_LOVING 7 345 kV. Clear Fault after 10 cycles and trip: KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH__3__DRINKARD_TP3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 b.2. LOAD 1 528603 b.3. LOAD 5* 528603 b.4. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NA_ENRICH3_115kV_528603 | Apply single-phase fault on: ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1, near NA_ENRICH 3 115 kV for 7 cycles with stuck breaker at NA_ENRICH 3 115 kV. Clear Fault after 10 cycles and trip: NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 LOAD 1 528605 CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NE_HEREFORD3__TIERABLANCA3 | 3 Phase fault on NE_HEREFORD3 (524567) 115 kV Bus a. Apply fault at the NE_HEREFORD3 (524567) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE_HEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__525460_0 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6( 525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 525461 TO NEWHART 3 525460 TO NEWHART_TR11 525459 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__GEN_2018_089 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO GEN-2018-089 230.0 KV 763186 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NEWHART____6__PLANT_X____6 | 3 Phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 230.0 KV 525461 TO PLANT_X 6 230.0 KV 525481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-089 trips on frequency protection settings. | Disabling frequency protection settings for GEN-2018-089 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NICHOLS____6__AMA_SOUTH__6 | 3 Phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 230.0 KV 524044 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__CURRY______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO CURRY 3 115.0 KV 524822 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__NORRIS_____3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO NORRIS 3 115.0 KV 524801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NORRIS_TP__3__OASIS______3 | 3 Phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 b.2. LOAD 1 524863 b.3. FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NORTON_____3__FE_TUCMCARI3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO FE-TUCMCARI3 115.0 KV 524509 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_NORTON_____3__PLSNT_HILL_3 | 3 Phase fault on NORTON 3 (524502) 115 kV Bus a. Apply fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 3 115.0 KV 524502 TO PLSNT_HILL 3 115.0 KV 524768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__G20_009_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Unstable oscillations GEN-2020-060: PTDF = 0.21541 GEN-2020-065: PTDF = 0.16337 GEN-2020-067: PTDF = 0.21415 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______3__CANNON_TP__3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERIMETER 3 115.0 KV 524797 TO OASIS 3 115.0 KV 524874 CKT 1 b.2. CANNON_TP 3 115.0 KV 524790 TO PERIMETER 3 115.0 KV 524797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______3__PORTALES___3 | 3 Phase fault on OASIS 3 (524874) 115 kV Bus a. Apply fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______6__524874_0 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6( 524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 524875 TO OASIS 3 524874 TO OASIS_TR1 1 524872 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______6__GEN_2020_062 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO GEN-2020-062 230.0 KV 764890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______6__ROOSEVELT__6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS______6__SN_JUAN_TAP6 | 3 Phase fault on OASIS 6 (524875) 230 kV Bus a. Apply fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 230.0 KV 524875 TO SN_JUAN_TAP6 230.0 KV 524885 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS3_115kV_524874 | Apply single-phase fault on: OASIS 3 115.0 KV 524874 TO PORTALES 3 115.0 KV 524924 CKT 1, near OASIS 3 115 kV for 7 cycles with stuck breaker at OASIS 3 115 kV. Clear Fault after 10 cycles and trip: NORRIS_TP 3 115.0 KV 524764 TO FE-CHZPLT 3 115.0 KV 524863 CKT 1 LOAD 1 524863 FE-CHZPLT 3 115.0 KV 524863 TO OASIS 3 115.0 KV 524874 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OASIS6_230kV_524875 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near OASIS 6 230 kV for 7 cycles with stuck breaker at OASIS 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OCOTILLO___3__PECOS______3 | 3 Phase fault on OCOTILLO 3 (528132) 115 kV Bus a. Apply fault at the OCOTILLO 3 (528132) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCOTILLO 3 115.0 KV 528132 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ODC_TP_____3__ODC________3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO ODC 3 115.0 KV 527056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ODC_TP_____3__SHELL_CO2__3 | 3 Phase fault on ODC_TP 3 (527051) 115 kV Bus a. Apply fault at the ODC_TP 3 (527051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODC_TP 3 115.0 KV 527051 TO SHELL_CO2 3 115.0 KV 527062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ONEY___4__WASHITA4 | 3 Phase fault on ONEY 4 (521017) 138 kV Bus a. Apply fault at the ONEY 4 (521017) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PECOS______3__HOPI_SUB___3 | 3 Phase fault on PECOS 3 (528178) 115 kV Bus a. Apply fault at the PECOS 3 (528178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 3 115.0 KV 528178 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM____3__CHINA_DRAW_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 b.2. LOAD 1 528228 b.3. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM____3__MALAGABEND_3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.05856 GEN-2020-065: PTDF = 0.12341 GEN-2020-067: PTDF = 0.08036 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.05856 GEN-2020-065: PTDF = 0.12341 GEN-2020-067: PTDF = 0.08036 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-060: PTDF = 0.0595 GEN-2020-065: PTDF = 0.17715 GEN-2020-067: PTDF = 0.0899 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM_9_528014 | 3 Phase fault PHANTOM 9 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9 (528014) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM9 528014 TO PHANTOM7 528015 TO PHANTOM TR4 528001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM_9_528014 | 3 Phase fault PHANTOM 9 (528014) 765 kV Bus a. Apply fault at the PHANTOM 9 (528014) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM9 528014 TO PHANTOM7 528015 TO PHANTOM TR4 528001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PHANTOM7_345kV_528015 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near PHANTOM 7 345 kV for 6 cycles with stuck breaker at PHANTOM 7 345 kV. Clear Fault after 10 cycles and trip: PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLAINS_INT_3__LEHMAN_TP__3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 b.2. LOAD 1 526944 b.3. LEHMAN_TP 3 115.0 KV 526350 TO LG-PLAINS 3 115.0 KV 526944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLAINS_INT_3__YOAKUM_____3 | 3 Phase fault on PLAINS_INT 3 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 115.0 KV 526928 TO YOAKUM 3 115.0 KV 526934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLAINVW_TP_2__HALE_CNTY__2 | 3 Phase fault on PLAINVW_TP 2 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 2 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 69.0 KV 525291 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____3__CASTRO_CNTY3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 b.2. LOAD 1 525480 b.3. BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 b.4. LOAD 1 525056 b.5. CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____3__LAMB_CNTY__3 | 3 Phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 115.0 KV 525480 TO LAMB_CNTY 3 115.0 KV 525636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__525480_0 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6( 525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 525481 TO PLANT_X 3 525480 TO PLANTX_TR1 1 525479 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__G17_146_TAP | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO G17-146-TAP 230.0 KV 760498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__SUNDOWN____6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO SUNDOWN 6 230.0 KV 526435 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLANT_X3_115kV_525480 | Apply single-phase fault on: BC-EARTH 3 115.0 KV 525056 TO PLANT_X 3 115.0 KV 525480 CKT 1 LOAD 1 525480 BC-KELLEY +3 115.0 KV 525050 TO BC-EARTH 3 115.0 KV 525056 CKT 1 LOAD 1 525056 CASTRO_CNTY3 115.0 KV 524746 TO BC-KELLEY +3 115.0 KV 525050 CKT 1, near PLANT_X 3 115 kV for 7 cycles with stuck breaker at PLANT_X 3 115 kV. Clear Fault after 10 cycles and trip: RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__CURRY______3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO FE-HOLLAND 3 115.0 KV 524831 CKT 1 b.2. LOAD 1 524831 b.3. FE-HOLLAND 3 115.0 KV 524831 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 b.4. LOAD 1 524838 b.5. CURRY 3 115.0 KV 524822 TO FE-CLOVIS2+3 115.0 KV 524838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_3__N_CLOVIS_TP3 | 3 Phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__524768_0 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6( 524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 524770 TO PLSNT_HILL 3 524768 TO PLSNHIL_TR11 524767 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__OASIS______6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO OASIS 6 230.0 KV 524875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PLSNT_HILL_6__ROOSEVELT__6 | 3 Phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PORTALES___2__PORTALES_1_2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO PORTALES#1 2 69.0 KV 524941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PORTALES___2__ZODIAC_____2 | 3 Phase fault on PORTALES 2 (524923) 69 kV Bus a. Apply fault at the PORTALES 2 (524923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 2 69.0 KV 524923 TO ZODIAC 2 69.0 KV 524934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PORTALES___3__524923_0 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3( 524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 524924 TO PORTALES 2 524923 TO PORTLES_TR21 524922 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_PORTALES___3__KILGORE____3 | 3 Phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PORTALES 3 115.0 KV 524924 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.2. LOAD 1 524977 b.3. S_PORTALES 3 115.0 KV 524963 TO GREYHOUND 3 115.0 KV 524977 CKT 1 b.4. LOAD 1 524977 b.5. KILGORE 3 115.0 KV 524935 TO S_PORTALES 3 115.0 KV 524963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__BECKHAM7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__BECKHAM7 | 3 Phase fault POTTER_CO 7(523961)345 kV Bus a. Apply fault at the POTTER_CO 7(523961)345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trips. There are no stability constraints when this generators trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTER_CO7_345kV_523961 | Apply single-phase fault on: POTTER_CO 7 345.0 KV 523961 TO BECKHAM7 345.0 KV 516059 CKT 1, near POTTER_CO 7 345 kV for 6 cycles with stuck breaker at POTTER_CO 7 345 kV. Clear Fault after 10 cycles and trip: HITCHLAND7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_POTTERCO_9_523966 | 3 Phase fault POTTERCO 9 (523966) 765 kV Bus a. Apply fault at the POTTERCO 9 (523966) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTERCO9 523966 TO POTTERCO7 523961 TO POTTERCO TR3 523964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_POTTERCO_9_523966 | 3 Phase fault POTTERCO 9 (523966) 765 kV Bus a. Apply fault at the POTTERCO 9 (523966) 765 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTERCO9 523966 TO POTTERCO7 523961 TO POTTERCO TR3 523964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RANDALL____6__AMA_SOUTH__6 | 3 Phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 230.0 KV 524365 TO AMA_SOUTH 6 230.0 KV 524415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | LANO GSU trips on voltage protection settings. | Disabling voltage protection settings for LANO GSU prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER3_115kV_528025 | Apply single-phase fault on: RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 10 cycles and trip: RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RDRUNNER7_345kV_528027 | Apply single-phase fault on: PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 10 cycles and trip: HOBBS_INT 7 345.0 KV 527896 TO RDRUNNER 7 345.0 KV 528027 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__LAMTON_____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-S_OLTON+3 115.0 KV 525440 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 b.2. LAMTON 3 115.0 KV 525414 TO LC-S_OLTON+3 115.0 KV 525440 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RKYFORD_TP_3__PLANT_X____3 | 3 Phase fault on RKYFORD_TP 3 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 115.0 KV 525446 TO PLANT_X 3 115.0 KV 525480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROCKYFORD__3__RKYFORD_TP_3 | 3 Phase fault on ROCKYFORD 3 (525393) 115 kV Bus a. Apply fault at the ROCKYFORD 3 (525393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYFORD 3 115.0 KV 525393 TO RKYFORD_TP 3 115.0 KV 525446 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__3__PORTALES___3 | 3 Phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 3 115.0 KV 524908 TO PORTALES 3 115.0 KV 524924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__524908_0 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6( 524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 524909 TO ROOSEVELT 3 524908 TO ROSEVLT_TR11 524907 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__GEN_2019_003 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO GEN-2019-003 230.0 KV 763483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS 6 230.0 KV 524875 TO ROOSEVELT 6 230.0 KV 524909 CKT 1, near ROOSEVELT 6 230 kV for 7 cycles with stuck breaker at ROOSEVELT 6 230 kV. Clear Fault after 10 cycles and trip: PLSNT_HILL 6 230.0 KV 524770 TO ROOSEVELT 6 230.0 KV 524909 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROSWLL_INT_3__527563_0 | 3 Phase fault on ROSWLL_INT 3 (527564) 115 kV Bus a. Apply fault at the ROSWLL_INT 3( 527564) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSWLL_INT 3 527564 TO ROSWLL_INT 2 527563 TO ROSWELL_TR21 527562 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_ROZ________3__SEMINOLE___3 | 3 Phase fault on ROZ 3 (527238) 115 kV Bus a. Apply fault at the ROZ 3 (527238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROZ 3 115.0 KV 527238 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RR_SVC_HV__3__RDRUNNER___3 | 3 Phase fault on RR_SVC_HV 3 (528024) 115 kV Bus a. Apply fault at the RR_SVC_HV 3 (528024) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RR_SVC_HV 3 115.0 KV 528024 TO RDRUNNER 3 115.0 KV 528025 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_CC_E_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_CC_E 7 345.0 KV 527655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL1_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL1 7 345.0 KV 527666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RSVLT_CC_W_7__RSVLT_COL2_7 | 3 Phase fault on RSVLT_CC_W 7 (527654) 345 kV Bus a. Apply fault at the RSVLT_CC_W 7 (527654) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_W 7 345.0 KV 527654 TO RSVLT_COL2 7 345.0 KV 527667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RSWL_SLRCOL3__CHAVES_CNTY3 | 3 Phase fault on RSWL_SLRCOL3 (527455) 115 kV Bus a. Apply fault at the RSWL_SLRCOL3 (527455) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSWL_SLRCOL3 115.0 KV 527455 TO CHAVES_CNTY3 115.0 KV 527482 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_PLAINVEW_2__HALE_CNTY__2 | 3 Phase fault on S_PLAINVEW 2 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 2 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 69.0 KV 525298 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SAGA_SDCOL_7__SAGA_SMEAS_7 | 3 Phase fault on SAGA_SDCOL 7 (527599) 345 kV Bus a. Apply fault at the SAGA_SDCOL 7 (527599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SDCOL 7 345.0 KV 527599 TO SAGA_SMEAS 7 345.0 KV 527600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SAMSON_____3__ROSWLL_INT_3 | 3 Phase fault on SAMSON 3 (527546) 115 kV Bus a. Apply fault at the SAMSON 3 (527546) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAMSON 3 115.0 KV 527546 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__DENVER_S___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SAN_ANDS_TP3__SEMINOLE___3 | 3 Phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAN_ANDS_TP3 115.0 KV 527105 TO SEMINOLE 3 115.0 KV 527275 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__OXYPERMIAN_3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__2__LG_MC&SMNL_2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO LG-MC&SMNL+2 69.0 KV 527223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__2__MOSS_______2 | 3 Phase fault on SEAGRAVES 2 (527201) 69 kV Bus a. Apply fault at the SEAGRAVES 2 (527201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 2 69.0 KV 527201 TO MOSS 2 69.0 KV 527217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__3__527201_0 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3( 527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 527202 TO SEAGRAVES 2 527201 TO SEAGRAV_TR11 527200 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEAGRAVES__3__FLATLAND___3 | 3 Phase fault on SEAGRAVES 3 (527202) 115 kV Bus a. Apply fault at the SEAGRAVES 3 (527202) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAGRAVES 3 115.0 KV 527202 TO FLATLAND 3 115.0 KV 527257 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___3__DOSS_______3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO DOSS 3 115.0 KV 527340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___3__GAINES_____3 | 3 Phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 3 115.0 KV 527275 TO GAINES 3 115.0 KV 527322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEMINOLE___6__527275_0 | 3 Phase fault on SEMINOLE 6 (527276) 230 kV Bus a. Apply fault at the SEMINOLE 6( 527276) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOLE 6 527276 TO SEMINOLE 3 527275 TO SEMINLE_TR21 527274 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SHELL_C2___3__DENVER_S___3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO DENVER_S 3 115.0 KV 527136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SHELL_C2___3__SHELLC3_TP_3 | 3 Phase fault on SHELL_C2 3 (527036) 115 kV Bus a. Apply fault at the SHELL_C2 3 (527036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_C2 3 115.0 KV 527036 TO SHELLC3_TP 3 115.0 KV 527068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SHELL_CO2__3__EL_PASO____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO EL_PASO 3 115.0 KV 527080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SHELL_CO2__3__MUSTANG____3 | 3 Phase fault on SHELL_CO2 3 (527062) 115 kV Bus a. Apply fault at the SHELL_CO2 3 (527062) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELL_CO2 3 115.0 KV 527062 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SHELLC3_TP_3__SHELLC3____3 | 3 Phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELLC3_TP 3 115.0 KV 527068 TO SHELLC3 3 115.0 KV 527074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__ANDREWS____6 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO ANDREWS 6 345.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Unstable oscillations GEN-2020-065: PTDF = 0.29928 | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse The following CQ units were found to contribute to the issue: GEN-2020-065: PTDF = 0.93193 | Build New Andrews to Road Runner 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SIDEWINDER_7__HOBBS_INT__7 | 3 Phase fault on SIDEWINDER 7 (527020) 345 kV Bus a. Apply fault at the SIDEWINDER 7 (527020) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIDEWINDER 7 345.0 KV 527020 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Voltage Collapse The following CQ units were found to contribute to the issue: GEN-2020-065: PTDF = 0.91393 | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SLATON_____2__SP_SLATON__2 | 3 Phase fault on SLATON 2 (526562) 69 kV Bus a. Apply fault at the SLATON 2 (526562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLATON 2 69.0 KV 526562 TO SP-SLATON 2 69.0 KV 526569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SN_JUAN_TAP6__SN_JUAN_WND6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO SN_JUAN_WND6 230.0 KV 524889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SOUTH_LOVNG3__MALAGABEND_3 | 3 Phase fault on SOUTH_LOVNG3 (528192) 115 kV Bus a. Apply fault at the SOUTH_LOVNG3 (528192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_ABERNTHY2__TUCO_INT2__2 | 3 Phase fault on SP-ABERNTHY2 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY2 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 69.0 KV 525731 TO TUCO_INT2 2 69.0 KV 525816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_ACUFF___2__CROSBY_____2 | 3 Phase fault on SP-ACUFF +2 (525906) 69 kV Bus a. Apply fault at the SP-ACUFF +2 (525906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ACUFF +2 69.0 KV 525906 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_CROSBY__2__CROSBY_____2 | 3 Phase fault on SP-CROSBY 2 (525915) 69 kV Bus a. Apply fault at the SP-CROSBY 2 (525915) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-CROSBY 2 69.0 KV 525915 TO CROSBY 2 69.0 KV 525925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_HALFWAY_2__HALE_CNTY__2 | 3 Phase fault on SP-HALFWAY+2 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+2 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 69.0 KV 525432 TO HALE_CNTY 2 69.0 KV 525453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_UPLAND__SP_WOLF_TP_3 | 3 Phase fault on SP-UPLAND (526198) 115 kV Bus a. Apply fault at the SP-UPLAND (526198) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-UPLAND 115.0 KV 526198 TO SP-WOLF_TP 3 115.0 KV 526481 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SP_WOLF_TP_3__SP_WOLFORTH3 | 3 Phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-WOLF_TP 3 115.0 KV 526481 TO SP-WOLFORTH3 115.0 KV 526483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_STANTON_E__2__SW_6786_S__2 | 3 Phase fault on STANTON_E 2 (526075) 69 kV Bus a. Apply fault at the STANTON_E 2 (526075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_E 2 69.0 KV 526075 TO SW_6786_S 2 69.0 KV 526087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__AMOCO_TP___3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 3 115.0 KV 526434 TO AMOCO_TP 3 115.0 KV 526445 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__COCHRAN____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PACIFIC 3 115.0 KV 526424 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. COCHRAN 3 115.0 KV 526361 TO PACIFIC 3 115.0 KV 526424 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____3__HOCKLEY____3 | 3 Phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC-OPDYKE 3 115.0 KV 526036 TO SUNDOWN 3 115.0 KV 526434 CKT 1 b.2. HOCKLEY 3 115.0 KV 526020 TO LC-OPDYKE 3 115.0 KV 526036 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__526434_0 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6( 526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 526435 TO SUNDOWN 3 526434 TO SUNDOWN_TR11 526432 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN____6__WOLFFORTH__6 | 3 Phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNDOWN6_230kV_526435 | Apply single-phase fault on: SUNDOWN 6 230.0 KV 526435 TO WOLFFORTH 6 230.0 KV 526525 CKT 1, near SUNDOWN 6 230 kV for 7 cycles with stuck breaker at SUNDOWN 6 230 kV. Clear Fault after 10 cycles and trip: AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 SUNDOWN 6 230.0 KV 526435 TO AMOCO_SS 6 230.0 KV 526460 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7__G20_074_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1, near SUNNYSD7 345 kV for 6 cycles with stuck breaker at SUNNYSD7 345 kV. Clear Fault after 10 cycles and trip: JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW_6786_N__2__SW_6786_S__2 | 3 Phase fault on SW_6786_N 2 (526086) 69 kV Bus a. Apply fault at the SW_6786_N 2 (526086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_6786_N 2 69.0 KV 526086 TO SW_6786_S 2 69.0 KV 526087 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW4J795_E__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_E 3 (527533) 115 kV Bus a. Apply fault at the SW4J795_E 3 (527533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_E 3 115.0 KV 527533 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SW4J795_W__3__ROSWLL_INT_3 | 3 Phase fault on SW4J795_W 3 (527534) 115 kV Bus a. Apply fault at the SW4J795_W 3 (527534) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW4J795_W 3 115.0 KV 527534 TO ROSWLL_INT 3 115.0 KV 527564 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__E_SANGER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_2__LG_BROWNFLD2 | 3 Phase fault on TERRY_CNTY 2 (526735) 69 kV Bus a. Apply fault at the TERRY_CNTY 2 (526735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 2 69.0 KV 526735 TO LG-BROWNFLD2 69.0 KV 526747 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25S | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | DISIS-2020-001 | 25W | Transfer | GROUP_05_FAULT_TERRY_CNTY_3__526735_0 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3( 526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 526736 TO TERRY_CNTY 2 526735 TO TERRY_TR2 1 526734 CKT 2 Three winding Transformer | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes